## Checklist
New Resource Implementation Checklist v47
|  | Full Network Model Schedule Webpage |  |  | Review the NRI Guide and Checklist on the NRI webpage before starting the process | NRI Webpage
|  | Existing WEIM projects please follow the process at this link: |  |  | Modeling-Submission-Checklist
|  | PDR and RDRR projects please follow process at this link: |  |  | Demand Response Resource Participating Guide
Project Type
File name guideline for submittal attachments: ISO Project Code: ISOPN Document Title: DT Version Number: VerX (X = Number) Example: ISOPN DT VerX Example: 19GEN123 DSL Ver1 | ISO Reference Document | Hyperlink to document | Bucket Deadline | Days before initial synchronization date - Deliverables must be ACCEPTED by the CAISO by this date. Days listed are calendar days unless otherwise noted. | Additional Information | Wind QF | Wind/Wind Repower | Existing QF | Solar | Conventional | Dynamic (Existing) | Dynamic New Construction | Non-Generation Resource (Hybrid resources have the ability to charge and discharge from the grid) | Storage (Does not have the ability to charge from the grid) | Custom LAP (CLAP) | Pseudo Tie (Existing) | Pseudo Tie New Construction | Distributed Energy Resource Aggregated Provider | Existing Resource Converting to Scheduling Coordinator Metered Entity (SCME) | Meter Replacement | RIG Reconfiguration (Includes Reconfigurations, Replacements, IP changes and breakouts) | Max_Gen (Pmax) Increase or Decrease | Load
Project Details Form Document Title: ProjectDetailsForm |  | Project Details Form | X | At least 10-20 days prior to the Bucket 1 and 2 "Customer Model Document Submission Deadline" | Submitting this online form will assign the project an internal CAISO Project code. All documentation must reference this code in the required file naming convention. Project Details Forms are needed to gather specific details about your project and to determine in which Full Network Model (FNM) build your project can be included. Note: If your proposed project requires more than one market resource ID you will need to create one project per resource ID. For example, if the project is a large solar resource requiring two market resource IDs, two Project Details Forms will be required. | Upload through RIMS UI | Upload through RIMS UI | Upload through RIMS UI | Upload through RIMS UI | Upload through RIMS UI | Upload through RIMS UI ----------------- *After Coordination Meeting | Upload through RIMS UI ----------------- *After Coordination Meeting | Upload through RIMS UI | Upload through RIMS UI | Upload through RIMS UI | Upload through RIMS UI ----------------- *After Coordination Meeting | Upload through RIMS UI ----------------- *After Coordination Meeting | Email submission to NRI@caiso.com ----------------- Resources that are 10MW or greater OR Participating in AS: At least 10-20 days prior to the Bucket 1 and 2 "Customer Model Document Submission Deadline" ----------------- Resources that are less than 10 MW and/or NOT participating in AS: Submit no later than 40 calendar days for resources that are 10MW or greater OR participating in AS. | Email submission to NRI@caiso.com ----------------- Submit no later than 40 calendar days | Upload through RIMS UI | Upload through RIMS UI | Upload through RIMS UI Project Type of “Conventional” | Upload through RIMS UI
Single Line - IFC Electrical Drawings Document Title: SLD (See Guideline Above) | BPM for Direct Telemetry | Single Line Drawing Requirements can be found under Metering Documentation Guidelines | 1 | Accepted by the "Customer Model Document Submission Deadline" date for the model build you would like be in. | Issued For Construction (IFC) Drawings should comply with Section 18 of BPM for Direct Telemetry and BPM for Metering for CAISO review. | Required | Required | Required | Required | Required | Required | Required | Required | Required | N/A | Required | Required | Required | Required ----------------- 35 calendar days prior | Required if moving the meter from its current location | N/A | N/A | Required
SCME PE Stamp Attestation Letter Document Title: Attestation |  |  | 1 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | If a Scheduling Coordinator Metered Entity does not have a Local Regulatory Authority, or if their Local Regulatory Authority does not have any Metering standards set, then Scheduling Coordinator Metered Entities are required to meet California ISO Metering standards. CAISO requires Single Line drawings that are either “Issued for construction” or “As- Built”. All the “Issued for Construction” drawings are required to be stamped by a Professional Engineer (PE). In the absence of the Professional Engineer stamp, CAISO accepts an attestation letter. Stamp Attestation letter must be from the Electrical Engineer and it should state that the Single Line Drawing is the exact physical and electrical representation of the resource. | If Applicable: Participating as SCME | If Applicable: Participating as SCME | If Applicable: Participating as SCME | If Applicable: Participating as SCME | If Applicable: Participating as SCME | If Applicable: Participating as SCME | If Applicable: Participating as SCME | If Applicable: Participating as SCME | If Applicable: Participating as SCME | N/A | If Applicable: Participating as SCME | If Applicable: Participating as SCME | N/A | If Applicable: Participating as SCME --------------- 35 calendar days prior | N/A | N/A | N/A | N/A
Executed Two-Party Generator Interconnection Agreement (SGIA or LGIA) with Participating Transmission Owner (PTO) Document Title: IA |  |  | 1 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | If the resource is distribution-connected, then the agreement will not include CAISO as a signatory, but a copy of this agreement will need to be submitted to NRI. Please also provide a copy of the facility study report with the agreement. If the resource has a 3-party agreement with CAISO, this requirement does not apply. *DYNAMICS- Interconnection Agreement to Host BA | Required | Required | Required | Required | Required | Interconnection Agreement to Host BA | Interconnection Agreement to Host BA | Required | Participating as SCME | Required | Interconnection Agreement with Native BA | Interconnection Agreement with Native BA | DERPA Concurrence Letter required in addition the Interconnection Agreement must be submitted. | N/A | N/A | N/A | Required | Required
Network Application Information Document Title: NetAppInfo (See Guideline Above) | New Resource Implementation Guide | NetAppInfo Template | 1 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | This simple Word document should identify the specific bay or bank the project will connect to at the CAISO controlled substation. If the resource is connecting to a new PTO substation, the substation name needs to be specified. Please see the NRI guide for detailed requirements. | Required | Required | Required | Required | Required | Required | Required | Required | Required | N/A | Required | Required | N/A | N/A | N/A | N/A | Required | Required
3 Line - IFC Electrical Drawing Document Title: 3LD (See Guideline Above) | BPM for Metering | Three Line Drawing Requirements can be found under Metering Documentation Guidelines | 1 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | Metering system 3-line diagram | Required (NA if participating as SCME) | Required (NA if participating as SCME) | Required (NA if participating as SCME) | Required (NA if participating as SCME) | Required (NA if participating as SCME) | N/A | N/A | Required (NA if participating as SCME) | Required (NA if participating as SCME) | N/A | Required (NA if participating as SCME) | Required (NA if participating as SCME) | N/A | N/A | Required if moving the meter from its current location | N/A | N/A | Required
Communication Block Diagram Document Title: CommBlock (See Guideline Above) | BPM for Direct Telemetry |  | 1 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | Communication Block Diagram for both metering and telemetry. | Required | Required | Required | Required | Required | N/A | N/A | Required | Required | N/A | Required | Required | For Telemetry Only** | N/A | N/A | N/A | N/A | Required
Site Information Sheet Document Title: SiteInfo | Tariff Appendix Q | Solar Site Information/Wind Site Information form can be found under Bucket 1 of the NRI website | 1 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | Site Information Form must be completely filled out before uploaded to RIMS. For plant location, the Eligible Intermittent Resource must use latitude and Longitude expressed in degrees/decimals using WGS84 geodetic datum only. Supplemental information may be required if the information provided on the information sheet is insufficient to generate a forecast. NOTE: If the Resource will be sharing meteorological data with another resource, then contracts between the host plant and the shared plant will be required (See NRI Guide for more information) | Required | Required | Required for Wind or Solar | Required | N/A | Required for Wind or Solar | Required for Wind or Solar | Required if including wind or solar | Required if including wind or solar | N/A | Required for Wind or Solar | Required for Wind or Solar | N/A | N/A | N/A | N/A | Required for wind or solar and changing physical facility that would alter the original Site info sheet | N/A
Topographical Map Document Title: TopoMap (See Guideline Above) | Tariff Appendix Q |  | 1 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | The topographical map is submitted for renewable resources only. This is a topographical plot plan map that depicts all the boundaries of the site and the topology of the land for forecasting purposes. The map must identify all meteorological stations and turbine/panel location by latitude and longitude and should be in degrees/decimals using WGS84 geodetic datum only. See the Tariff Appendix Q for more information about this requirement. For wind resources the purpose of this document is for our engineers to utilize the locations of turbines and the topology of the land to determine the designated turbines that will be used for forecasting purposes. A wind resource will need to illustrate the location and height for each wind turbine within a wind park. | Required | Required | Required for Wind or Solar | Required | N/A | Required for Wind or Solar | Required for Wind or Solar | Required if including wind or solar | Required if including wind or solar | N/A | Required for Wind or Solar | Required for Wind or Solar | N/A | N/A | N/A | N/A | Required for wind or solar | N/A
RIG Details: AT&T IP or ISP static address Document Title: RIGDetails (See Guideline Above) | BPM for Direct Telemetry | Remote Intelligent Gateway Details | 1 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | Critical Path Item (Do this early!) If obtaining the AT&T ECN IP Static Addressing or ISP Static Addressing may take 3 months or more in some cases. For the AT&T service contact Jennifer Ravazza at (925) 451-0017, jm7929@att.com or Magdi Omar at (201) 851-2077 or mo2747@att.com. ISP services can be obtained in many ways and most resource owner may already have a provider established. Once the IP addressing is received, please upload to RIMS User Interface using the proper form and filename. | Required | Required | Required | Required | Required | N/A | N/A | Required | Required | N/A | Required | Required | For Telemetry Only** | N/A | N/A | Required | N/A | For Telemetry Only **
Generator Dynamic Model file Document Title: DYNGEN |  |  | 1 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | Interconnection Customer must submit a dynamic data modeling (*.dyd) file used on GE-PSLF software. ISO reviews the correct dynamic modeling is used. The format tool is from the GE-PSLF “PSLF MODELS LIST BY TYPE” User’s Manual. | Required | Required | Required | Required | Required | N/A | N/A | Required for BESS or Hybrid only | Required | N/A | Required | Required | N/A | N/A | N/A | N/A | N/A | Required
Generator Positive Sequence Load Flow Data Document Title: PSLF or EPCL |  |  | 1 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | Interconnection Customer must submit PSLF data to the CAISO for modeling of a particular project. EPC may be provided in place of a PLSF. Additionally, the ISO does not accept PSSE files in place of a PSLF. | Required | Required | Required | Required | Required | Required | Required | Required for BESS or Hybrid only | Required | N/A | Required | Required | N/A | N/A | N/A | N/A | N/A | Required
Resource owner receives the Real Time Database spreadsheet of required telemetry points** | BPM for Direct Telemetry |  | 1 | N/A | CAISO EDAS will initiate the first draft after the receipt and approval of all required documentation. | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | ICCP data point starting tag EMS approval required | ICCP data point starting tag EMS approval required | For Telemetry Only ** | For Telemetry Only ** | N/A | Either ICCP or Real Time Device Required | Either ICCP or Real Time Device Required | For Telemetry Only ** | N/A | N/A | N/A | N/A | For Telemetry Only **
Initiate CAISO Regulatory Contract(s) by submitting Information Request Sheet(s) to RegulatoryContracts@caiso.com | Regulatory Contracts |  | 2 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | Follow the link provided. Under Contracts and Agreements --> Pro forma agreement and associated documentation --> Pro forma agreements choose the appropriate Information Request Sheet(s) to complete. Questions related to the types of contracts appropriate for a project should be directed to RegulatoryContracts@caiso.com. | Required | Required | Required | Required | Required | Required | Required | Required | Required | N/A | Required | Required | Required | Required --------------- 35 calendar days prior | Modify schedule 1 of Meter Service Agreement (MSA) | N/A | Modify the PGA | Required
ISO Meter Configuration Worksheet (ISOME) Document Title: MeterConfig [MeterDeviceID] (See Guideline Above) ------------------------------------------ ISO Meter Configuration Worksheet (SCME) Document Title: SQMD MeterConfig 0000000 (See Guideline Above) | BPM for Metering | Meter Configuration Worksheet --------------------------- SQMD plan template; SQMD plan template for additional metering devices. | 2 | By the "Customer Model Document Submission Deadline" for the model build you would like be in. | The purpose of the ISO Meter Configuration Worksheet is to set-up the meter configuration in MV90 and communicate with the meter. Please note that the Site Owner is responsible for the accuracy of the information on this form. ----------------------------------------------------------------------------- The purpose of the SQMD plan template is to verify the physical metering standards and resource algorithms. Please note that the Site Owner is responsible for the accuracy of the information on this form. | Required | Required | Required | Required | Required | N/A | N/A | Required | Required | N/A | Required | Required | Required ---------------- 35 calendar days prior | Required ---------------- 35 calendar days prior | Required | N/A | N/A | Required
Generator Resource Data Template (GRDT) - Final Version and Supporting Docs Document Title: FinalGRDT (See Guideline Above) Document Title: FinalGRDT Supporting Docs (See Guideline Above) |  | Generator Resource Data Template | 3 | 30 | Follow the link provided. Listed under Bucket 3 under Resource entity management- GRDT is a list of resource specific templates. A Scheduling Coordinator should review the final version of the GRDT on behalf of the legal entity. Please upload to RIMS User Interface. | Required if changing SC | Required | Required if changing SC | Required | Required | Required | Required | Required | Required | N/A | Required | Required | Required | Required - Submit to SCRequests@caiso.com - For WEIM resources more specifics can be found on the modeling submission checklist in the RC Portal | N/A | N/A | Required **If Scheduling Coordinator is not changing then the SC must update the Pmax via the MF UI once sync approval has been provided** | Required
Generator Resource Data Template (GRDT) Explanation Document Title: GRDT Explanation (See Guideline Above) |  |  | 3 | 30 | The final GRDT should be accompanied with a supporting explanation that include details about how the resource’s design capabilities were calculated. The CAISO may request additional supporting materials, such as test results, manufacturer recommendations, historical data, resource operating procedures, engineering studies, etc., with citations to specific page numbers or section numbers to allow the ISO to validate that the values reflect the design capabilities of the resource. | Required if changing SC | Required | Required if changing SC | Required | Required | Required | Required | Required | Required | N/A | Required | Required | Required | N/A | N/A | N/A | N/A | Required
Regulatory Contracts Executed |  |  | 3 | 30 | Regulatory contracts must be fully executed by the Bucket 4 deadline. The NRI team cannot proceed with creating the Scheduling Coordinator (SC) Association without these agreements executed. *If an Aggregate Capability Constraint (ACC) is required the interconnection customer must initiate the request with regulatory contracts. | Required | Required | Required | Required | Required | Applicable Contracts Executed | Applicable Contracts Executed | Required | Required | N/A | Applicable Contracts Executed | Applicable Contracts Executed | Applicable Contracts Executed | Applicable Contracts Executed ---------------- 10 calendar days prior | Modify schedule 1 of Meter Service Agreement (MSA) | N/A | Modify the PGA | Required
Initiate a Qualified Reporting Entity Service Agreement (QRESA) |  | http://www.caiso.com/participate/Pages/Generation/Default.aspx | 3 | 30 | For renewable resources to receive Renewable Energy Credits (RECs), the Generator Owner must enlist the services of a Qualified Reporting Entity (QRE) to submit meter data to WECC on their behalf. If the Generator Owner chooses the ISO to act as their QRE, they must first have a QRE service agreement (QRESA) in place with the ISO. Please note, the ISO can only submit meter data for production occurring on or after the effective date of the QRESA. To initiate a Qualified Reporting Entity Service Agreement (QRESA) submit a Qualified Reporting Entity Service Request Form to EDAS@caiso.com. The ISO will review the request form for accuracy against the resource Meter Service Agreement (MSAISOME). The MSAISOME must therefore have been executed prior to submittal of the QRE request form. | Required if Gen Owner chooses ISO to act as QRE | Required if Gen Owner chooses ISO to act as QRE | N/A | Required if Gen Owner chooses ISO to act as QRE | N/A | N/A | N/A | N/A | N/A | N/A | Required if Gen Owner chooses ISO to act as QRE (for wind or solar pseudo) | Required if Gen Owner chooses ISO to act as QRE (for wind or solar pseudo) | N/A | N/A | N/A | N/A | N/A | N/A
Participating Intermittent Resource (PIR) Documentation Document Title - Letter of Intent: PIRPLOI (See Guideline Above) Document Title- CECPreCert (See Guideline Above) | BPM for Market Operations | Form of Letter of Intent (LOI) to become a Participant | 3 | 30 | Participation in PIRP requires the following documentation: Form Letter of Intent and the CEC Pre-Certification for Renewable Portfolio. PIR Certification will require a minimum evaluation period consisting of 60 days with high quality data beginning three business days after the project has achieved COD and been setup in CAISO systems as an EIR. Projects that have a phased implementation schedule in their Generator Interconnection Agreement must be pre-approved by the CAISO to begin the PIR evaluation prior to 100 percent of the resource being commercial. A request for PIR Certification must be submitted by the generator owner and accepted by the CAISO during the planning stage (prior to project design or contract execution) in order for the PIR Certification evaluation to occur prior to 100% of project capacity achieving COD. The CAISO will review and approve such requests on a case-by-case basis and will require the phasing proposal 1) to align with the interconnections studies and analysis conducted and 2) to be reflected in applicable interconnection documents. For the CEC Pre-Certification please visit the following website: http://www.energy.ca.gov/renewables/index.html | Required if participating in PIR | Required if participating in PIR | N/A | Required if participating in PIR | N/A | Required if participating in PIR for Wind or Solar | Required if participating in PIR for Wind or Solar | N/A | N/A | N/A | Required if participating in PIR for Wind or Solar | Required if participating in PIR for Wind or Solar | N/A | N/A | N/A | N/A | N/A | N/A
Control and Protection Documentation Document Title: ControlProtection (See Guideline Above) |  |  | 3 | 30 | Control & Protection for high voltage bus, generators and generator step up transformers; one-line showing relaying/metering, CT/PT; a complete list of relay settings, including selected CT and PT ratios, frequency set points if used; and a copy of relay Certified Test Reports after relay settings have been accepted. Inverter based generation: In addition to the above requirements, all Generators using inverters (e.g. solar PV, wind turbines, etc.) must submit documentation that the inverters have been programmed with protection codes (if used) to be in compliance with the most recent version of NERC Standard PRC-024 | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater
Control Protection Inverter Document Title: ControlProtectionInverter (See Guideline Above) | http://www.caiso.com/planning/Pages/GeneratorInterconnection/InterconnectionRequest/Default.aspx | http://www.caiso.com/PublishedDocuments/GeneratingFacilityData-AttachmentAtoAppendix1.xlsm | 3 | 30 | Inverter based generation: In addition to the above requirements, all Generators using inverters (e.g. solar PV, wind turbines, etc.) must submit documentation that the inverters have been programmed with protection codes (if used) that are in compliance with the most recent version of NERC Standard PRC-024. If off nominal frequency protection is used, it must be in compliance with the Western Variance in the most recent version of NERC Standard PRC-024. When submitting the Inverter Report use the Generating Facility Data - Attachment A to Appendix 1 template located on the ISO Interconnection request page. | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater
Control and Protection Inverter Report Document Title: ControlProtection InverterReport (See Guideline Above) |  |  | 3 | 30 | In addition to the above requirements, all Generators and storage facilities using inverters (e.g. solar PV, wind turbines, etc.) must submit documentation that the inverters have been programmed with protection codes (if used), and LGIA requirements to be in compliance with the most recent version of NERC Standard PRC-024 and FERC recommendations. | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Grid connected, 10 MW or greater
New Scheduling Coordinator Selection Letter Document Title: SCSelection (See Guideline Above) |  |  | 3 | 30 | Effective date of assignment must match that in the SC Acceptance letter. SC Association will not be made effective until all other requirements (metering, telemetry, contracts) are fulfilled. The association process takes 5-11 business days to complete. | Required if changing SC or New Resource ID | Required | Required if changing SC or New Resource ID | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required - Submit to SCRequests@caiso.com - For WEIM resources more specifics can be found on the modeling submission checklist in the RC Portal | N/A | N/A | Required (if changing SC) | Required
New Scheduling Coordinator Acceptance Letter Document Title: SCAcceptance (See Guideline Above) |  |  | 3 | 30 | Effective date of assignment must match that in the SC Selection letter. SC Association will not be made effective until all other requirements (metering, telemetry, contracts) are fulfilled. The association process takes 5-11 business days to complete | Required if changing SC or New Resource ID | Required | Required if changing SC or New Resource ID | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required | Required - Submit to SCRequests@caiso.com - For WEIM resources more specifics can be found on the modeling submission checklist in the RC Portal | N/A | N/A | Required (if changing SC) | Required
Update NRI Project with Scheduling Coordinator's contact information fully completed via RIMS User Interface. |  |  | 3 | 30 | Complete the Scheduling Coordinator (SC) Information section on page 2. Make sure to have "SC Contact Information" in the subject line. | Required | Required | Required | Required | Required | Required | Required | Required | Required | N/A | Required | Required | N/A | N/A | N/A | N/A | Required | Required
Balancing Authority Extreme Weather Template |  | Balancing Authority Extreme Weather Template | 3 | 30 | The Extreme Weather template is available for entities that are Generator Owners for physical, NERC-registered, BES generation to submit their generator's cold weather attributes. Generator Owners shall have their Scheduling Coordinator provide the requested data via CIDI ticket once the resource SC association is effective. Data can be provided using the Balancing Authority Extreme Weather Template posted on the CAISO website under Market & Operations > Network and Resource and Modeling > Resource Data Submission section. Please ensure submissions include the resource ID in the template for processing. These data changes must be submitted before approval of commercial operation for new resources and as soon as practicable for existing resources. The California ISO’s operating procedures are available on the Operating Procedures webpage, including 3140, TOP-003 TOP – BA Data Request and Specification Guidelines, and 3140A, TOP-003 TOP – BA Data Request and Specifications for Data Provision. Please submit a CIDI ticket if you have any questions or concerns. | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | N/A | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | Required for entities that are Generator Owners for physical, NERC-registered, BES generation | N/A | N/A | N/A | N/A | N/A | N/A
Control Room Info - 24/7 contact information Document Title: 24HourContact (See Guideline Above) |  | Remote Intelligent Gateway Site Contact Information | 3 | 30 | The primary contact should be available 24/7 and have access to or be able to obtain real-time information on the output or status of the resource(s) being monitored by the real-time device. If there is a telemetry failure, this contact may be required to report specified changes in the output of the resource(s) until the problem is resolved. Additional contacts desired would have the ability to troubleshoot real-time related issues or coordinate real-time related work (e.g. SCADA specialist, plant manager). | Required | Required | Required | Required | For Telemetry Only ** | Required | Required | Required | Required | N/A | Required | Required | For Telemetry Only** | N/A | N/A | N/A | N/A | For Telemetry Only **
Device Certificate Request Form for Real Time Devices |  | Device Certificate Request Form | 3 | 30 | Email to ServiceDesk@caiso.com with the Certificate Signing Request (CSR) file. Allow 10 business days to complete the request. | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | N/A | N/A | For Telemetry Only ** | For Telemetry Only ** | N/A | Required if Pseudo Tie resource and using a Real Time Device | Required if Pseudo Tie resource and using a Real Time Device | For Telemetry Only ** | N/A | N/A | N/A | N/A | For Telemetry Only **
Email EDAS@caiso.com a notification from the resource owner witnessed and approved of the Real Time Device and Metering pretesting in accordance to the BPM for Telemetry. Email Subject Line example: 14GEN1234 RIG Pretesting Notification | BPM for Direct Telemetry |  | 3 | 30 | This should be completed prior to scheduling any telemetry testing with ISO. The electrical contractor & telemetry engineering company should perform the pretesting. | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | N/A | N/A | For Telemetry Only ** | For Telemetry Only ** | N/A | Required if Pseudo Tie resource and using a Real Time Device | Required if Pseudo Tie resource and using a Real Time Device | For Telemetry Only ** | N/A | N/A | N/A | For Telemetry Only ** | For Telemetry Only **
Submit a request through the EDAS Fieldwork Request Tool to schedule CAISO point-to-point and/or meter testing | BPM for Direct Telemetry | EDAS Fieldwork Request Tool | 3 | At LEAST 30 days before synchronization/QF conversion | Scheduling is done by the telemetry engineering firm after the basic health check of the database points is completed internally. Provide a minimum of 30 business days lead time on scheduling testing. | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | For Telemetry Only ** | N/A | N/A | For Telemetry Only ** | For Telemetry Only ** | N/A | Required if Pseudo Tie resource and using a Real Time Device | Required if Pseudo Tie resource and using a Real Time Device | For Telemetry Only ** | N/A | N/A | N/A | For Telemetry Only ** | For Telemetry Only **
CPS Subscriber Agreement for Remote Intelligent Gateways Document Title: CPSAgreement (See Guideline Above) | BPM for Direct Telemetry | CPS Subscriber Agreement for Remote Intelligent Gateways | 3 | 30 | This document describes the obligations of the Subscriber to the CAISO (the Certification Authority). | Required | Required | For Telemetry Only ** | Required | For Telemetry Only ** | N/A | N/A | For Telemetry Only ** | For Telemetry Only ** | N/A | Required if Pseudo Tie resource and using a Real Time Device | Required if Pseudo Tie resource and using a Real Time Device | For Telemetry Only ** | N/A | N/A | N/A | N/A | For Telemetry Only **
External Network Guidelines Document Title: ECNAgreement (See Guideline Above) | BPM for Direct Telemetry | Network Connectivity Security Requirements and Agreement | 3 | 30 | Please read and understand the External Network Guidelines. Must be signed before meter and telemetry is tested with the CAISO. | Required | Required | Required | Required | Required | Required if providing direct telemetry or electing to be a CAISO metered entity | Required if providing direct telemetry or electing to be a CAISO metered entity | Required | Required | Required if providing direct telemetry or electing to be a CAISO metered entity | Required if Pseudo Tie resource and using a Real Time Device | Required if Pseudo Tie resource and using a Real Time Device | For Telemetry Only ** | N/A | N/A | N/A | N/A | Required if providing direct telemetry or electing to be a CAISO metered entity
Metering and Telemetry testing completed | BPM for Direct Telemetry |  | 4 | 10 | The telemetry and metering end-to-end testing must be completed. This will include a preliminary validation of the meter data. A final validation of metering and telemetry data will be completed after synchronization using live data. | Required | Required | Required | Required | Required | N/A | N/A | Required | Required | N/A | Required if Pseudo Tie resource and using a Real Time Device | Required if Pseudo Tie resource and using a Real Time Device | For Telemetry Only ** | N/A | Required | Required | Required | Required
Interconnection Approval Letter from PTO for Initial Synchronization Document Title: PTO Sync Approval (See Guideline Above) |  |  | 4 | 10 | Letter of approval from the respective PTO notifying the ISO that all required transmission facilities have been completed and tested. | N/A | Required | N/A | Required | Required | N/A | N/A | Required | Required | N/A | N/A | N/A | NA | N/A | N/A | N/A | Required | Required
Submit request for initial sync/ Request for QF conversion/ Project Completion |  |  | 4 | 10 | The interconnection customer submits the request through RIMS for initial synchronization, QF conversion or Project Completion of your Dynamic or Pseudo Tie Project. This request serves as a indicator for the all business units to complete the final check of all requirements and submit the project package for approval. For DERP projects please submit an email request for project completion. Please see NRI guide for email subject line requirements. | Required | Required | Required | Required | Required | Required | Required | Required | Required | N/A | Required | Required | Required Email Request to NRI@caiso.com | N/A | N/A | N/A | N/A | Required
Test Energy Schedule | Resource Trial Operations and Test Energy Process |  | 4 | 10 | Please refer to the CAISO operating procedure 5320 Resource Trial Operations and Test Energy Process. | N/A | Required | N/A | Required | Required | Required | Required | Required | Required | N/A | Required | Required | N/A | N/A | N/A | N/A | N/A | Required
CAISO initial synchronization approval email to commence Trial Operations |  |  | 5 | 1 day prior to sync | All of the above requirements must be met prior to the approval of the resource to ISO System Operations. The resource owner will receive an email notification that the resource is approved. | N/A | Required | N/A | Required | Required | N/A | Required | Required | Required | N/A | N/A | Required | N/A | N/A | N/A | N/A | Required **If Scheduling Coordinator is not changing then the SC must update the Pmax via the MF UI once sync approval has been provided** | Required
24 Hour Notice of Initial Synchronization by phone to CAISO Outage Management | Resource Trial Operations and Test Energy Process |  | 5 | 1 day prior to sync | Scheduling Coordinator to contact ISO Outage Management, see specifics in Procedure 5320 | N/A | Required | N/A | Required | Required | Required | Required | Required | Required | N/A | Required | Required | N/A | N/A | N/A | N/A | N/A | For Telemetry Only **
Final Control and Protection Report Document Title: FinalControlProtection Report (See Guideline Above) |  |  | 5 | 1 day prior to sync | This documentation is only required for Interconnection Customers connecting directly to the CAISO control grid or when a generator has gone through the CAISO Application and Study queue process. Please Note: Only submit the Certified Test Reports associated with the relay settings submitted in Bucket 3. | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Grid connected, 10 MW or greater | Grid connected, 10 MW or greater
Call CAISO Immediately before synchronization for approval |  |  | 5 | Immediately prior to sync | Scheduling Coordinator to contact ISO Real-Time Generation Desk or Transmission Desk as needed for initial and all subsequent synchronizations. | N/A | Required | N/A | Required | Required | Required | Required | Required | Required | N/A | Required | Required | N/A | N/A | N/A | N/A | N/A | Required
Final Metering Package, including: | BPM for Metering | Metering Documentation | 5 | Must be ISO accepted 5 business days before COD/QF Conversion | It is the generation owner's responsibility to ensure that CAISO receives the complete set of metering documentation. The final metering package includes the completed CAISO metering certification form(s), metering calculations worksheet, compensation calculations to the POR, and the meter programs. CAISO must approve the installation/documentation prior to initial synchronization. | Required | Required | Required | Required | Required | N/A | N/A | Required | Required | N/A | Required | Required | N/A | N/A | Required | N/A | Required | Required
CAISO Meter Site Verification Sheet Document Title: MSVS [Meter Device ID] (See Guideline Above) | [14 empty] | N/A |  |  | N/A
Point of Receipt Meter Calculation Document (If applicable) Document Title: PORCalc [Meter Device ID] (See Guideline Above) | [5 empty] | Required for direct connection to ISO control grid | Required for direct connection to ISO control grid | Required for direct connection to ISO control grid | Required for direct connection to ISO control grid | Required for direct connection to ISO control grid | N/A | N/A | Required for direct connection to ISO control grid | Required for direct connection to ISO control grid | N/A | N/A | N/A | N/A | N/A | Required for direct connection to ISO control grid | N/A | N/A | Required
Distribution Compensation Factor Supporting Documentation Document Title: DCF (See Guideline Above) | BPM for Metering |  | 5 | 30 | If a CAISO Metered Entity is connected to a Utility Distribution Company’s (UDC)/Distribution Provider Distribution System, an approved Distribution Compensation Factor (DCF) must be determined and must be programmed into the meter to reflect the point of delivery at the CAISO Controlled Grid. WDAT or any letter of agreement of DCF from appropriate UDC/Distribution Company/ Interconnection entity must be submitted to NRI prior to programming the ISO Meter with a DCF. | Distribution Resources Only if Applicable | Distribution Resources Only if Applicable | Distribution Resources Only if Applicable | Distribution Resources Only if Applicable | Distribution Resources Only if Applicable | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Distribution Resources Only if Applicable, required if ISO has no record | N/A | N/A | Required
Meter Certificate of Compliance Issued by ISO | BPM for Direct Telemetry |  | 6 |  | Once all bucket items are completed and COD notification has been provided the CAISO will begin the Certificate of Compliance. The CAISO must issue a signed Certificate of Compliance once the metering and telemetry is validated and with live generation data and all documentation has been accepted. This certificate must be issued prior to completion of commercial operations. | Required | Required | Required | Required | Required | N/A | N/A | Required | Required | N/A | Required | Required | N/A | N/A | Required | N/A | N/A | Required
DERP Distribution Owner Final Approval Letter Document Title: DO Final Approval (See Guideline Above) |  |  | 6 |  | Distribution Owner Final Approval Letter - See NRI Guide for further details. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Required | N/A | N/A | N/A | N/A | N/A
COD (commercial operation date) Approval Letter from PTO Document Title: PTO COD Approval (See Guideline Above) |  |  | 6 | 5 business days before COD | This approval may be covered by the interconnection approval letter. Some transmission owners require two letters. | N/A | Required | N/A | Required | Required | N/A | Required | Required | Required | N/A | N/A | Required | NA | N/A | N/A | N/A | Required | Required
Submit request for COD or COM for Commercial Operations approval from CAISO |  |  | 6 | 5 business days before COD | This requests begins the CAISO internal approval process so that the resource may commence commercial operations in five business days or more from the date the request is received. | N/A | Required | N/A | Required | Required | Required (Dynamic Button) | Required | Required | Required | Required | Required (Pseudo Button) | Required | N/A | N/A | N/A | N/A | Required | Required
COM or COD Letter from Generator Owner declaring Commercial Operations | New Resource Implementation Guide | Commercial Operation template letters. See Bucket 6 of NRI Guide. | 6 | Upload to RIMS upon receiving Notification of Commercial Operations email from NRI | This letter notifies the CAISO that the resource has completed all start up testing and is available for commercial operations. * For incremental increases, please see the NRI Guide - Bucket 6 "Increasing Commercial Energy" | N/A | Required | N/A | Required | Required | N/A | Required | Required | Required | N/A | N/A | Required | N/A | N/A | N/A | N/A | Required | Required
Eligible Intermittent Resources Protocol (EIRP) | Appendix Q - Eligible Intermittent Resources Protocol (EIRP) | - | - | After achieving COD | Once a EIR resource has achieved COD, ‘in order for the CAISO to forecast Energy, an Eligible Intermittent Resource must provide the CAISO with MW production data and meteorological data’ the resource will need to complete a ‘minimum of thirty (30) consecutive days and be of sufficient quality as determined by a CAISO to produce a state of the art forecast.’ Please review Appendix Q for detail process. By following the below guidelines can assist resources through the process from stage 2 to stage 3, such errors can increase the number of days to reach the ‘minimum of thirty (30) consecutive days’ as specified in the tariff. 1. Locked/Repeating generation or MET data causes issues when creating a forecast. a. Please check your telemetry data that your resource is sending to the ISO. Is the data showing repeated values (zero or non-zero)? Is it increasing or decreasing in a linear manner? Is the weather and telemetry data within reasonable range (generation below Pmax, non-negative, realistic wind speed values, etc.) you’d expect given current weather conditions? Specifically, check the following points for any of the above: i. Telemetry data: UPMW (point of delivery) telemetry, UGMW (gross) telemetry (if applicable) ii. Meteorological data: Back panel temperature, Irradiance (solar resources), Wind speed and direction (wind resources) 2. Not consistently following the SUPP dispatches. 3. OMS Availability does not link up with actual generation production. a. We’ve noticed a resource frequently changes the reported availability but those values will not always sync up with the reported generation. At times the generation may actually exceed the reported availability | Required | Required | N/A | Required | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Net Qualifying Capacity (NQC) Request Form & Standard Capacity Product Grandfathering Document Title: NQCForm (See Guideline Above) | NQC Request Form |  | - | After achieving COD | Scheduling Coordinators for resources that plan to sell Resource Adequacy capacity must submit an NQC Request Form in order for the ISO to validate and establish NQC for the new resource. A resource will not be eligible to participate in the Resource Adequacy program until (a) it achieves COM/COD, (b) it submits this form to request NQC, and (c) the ISO performs its internal validation and establishes NQC on the resource. Scheduling Coordinator should submit this form through CIRA. | Optional | Optional | Optional | Optional | Optional | N/A | N/A | Optional | Optional | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
**NOTE**
For participating in ISO market's see the relative BPM's and/or Tariff appendices as needed for further instruction on participation.
Telemetry is required for resources 10 MW or greater and for resources 1 MW or greater that are an eligible intermittent resource (EIR) or an Ancillary Services (AS) market resource.

## Change Log
NRI Update Log
Date | Version | Update
2021-10-07 | 36 | Removed requirement for PTO Sync and COD Letter for Dynamic Projects
2021-11-05 | 37 | Addition of Column U - Pmax Increase/Decrease Projects; Meter Config for RIG projects updated to N/A
2022-03-14 | 38 | DERP PTO COD letter marked as NA since the requirement is covered under DERP Distribution Owner Final Approval Letter; DERP SLD is marked as Required
2022-04-15 | 39 | All EIM references updated to WEIM.
2022-04-20 | 40 | Updated ECN contact information.
2022-05-18 | 41 | Updated 22A to include the zeros required for SQMD Meter Config submission; Updated column 'Max_Gen (Pmax) Increase or Decrease' to require MSVS and not require Meter config
2022-10-18 | 42 | A23 - Updated the file name for the new bucket item " GRDT Explanation"; Column M - New Project Type of "Dynamic New Construction"; Column R - New Project Type of "Pseudo New Construction"
2023-02-21 | 43 | Updated Column W(Max_Gen Pmax Increase or Decrease) requirements. Control Protection- Required; Control Protection Inverter- Required; Final Control Protection- Required; SC Letters- Required if changing SCs
2023-06-02 | 44 | MaxGen Projects: If the SC is not changing the SC must update the Pmax at the time of Sync via the MF UI. DERA Projects: IA must be submitted along with the concurrence letter requirment. Telemetry timeline reflected. Added Load project type column with requirements. Regulatory Constracts Requirment note reagarding ACC - If an Aggregate Capability Constraint (ACC) is required the interconnection customer must initiate the request with regulatory contracts.
2023-09-28 | 45 | Corrections to line 31 and 32 for project types to list "Required" instead of "Required if changing SC".
2023-10-16 | 46 | Addition of Balancing Authority Extreme Weather Template Requirment.
2023-10-25 | 47 | Moved DCF requirement from Bucket 3 to Bucket 5 to align with RIMS