## Cost Details
All costs are $x1,000
2017 PG&E Final Generator Interconnection Unit Cost Guide |  |  |  | "Voltages" | 60/70 kV | 115 kV | 138 kV | 230 kV | 500 kV | Notes/Comments:
Revised as of: 01/01/2017
Equipment Categories |  |  |  | Units
New Substation Equipment
|  | Complete loop-in Substation, equipped with one line position to |  |  | 12500 | 13000 |  | 15000 |  | Includes all necessary equipment, including operating buses, one double-breaker line position on a breaker-and-a-half (BAAH) configuration for gen-tie, one three-breaker line position on a BAAH configuration to loop each existing transmission line, substation MPAC or control building, and associated protective relays. Also includes base costs of site preparation, ground grid, fencing, driveway and access road (up to .5 mi.) outside substation. Assumes nominal costs for PG&E to support the IC with land acquistion, land rights, licensing, permits, or environmental mitigations; independent permitting by PG&E is not included.
terminate a single gen-tie and loop in and out one existing PG&E T line.
1 complete Bay and 1 Partial Bay - 5 CBs
|  | Complete loop-in Substation, equipped with one line position to |  |  | N/A | 17000 |  | 20000
terminate a single gen-tie and loop in and out two existing PG&E T lines.
2 complete Bays and 1 Partial Bay - 8 CBs
New Substation Equipment
Transformer Banks:
|  |  | 500/230 kV 4-1 Phase (375 MVA each) | per unit |  |  |  | 41000 |  | Includes cost for Breaker and Protection for 2-500 kV
|  |  | 500/230 kV 3-1 Phase (375 MVA each) | per unit |  |  |  | 37000 |  | Breakers and 3-230 kV Breakers connected in BAAH
configuration. Assumed space is available in the
substation.
|  |  | 230/115 kV 1-3 Phase, 420 MVA | per unit |  |  |  | 11000 |  | Cost includes the Bank, its Protection relays and
|  |  | 230/60 or 70kV 4-1 Phase (4X 60 MVA) | per unit |  |  |  | 14000 |  | associated structures. Does not include cost for any high
|  |  | 230/60 or 70kV 1-3 Phase (200 MVA) | per unit |  |  |  | 10000 |  | or low side Breakers.
Assumed space is available in the substation.
|  |  | 115/60 or 70kV 4-1 Phase (4X 30) | per unit |  | 10500
|  |  | 115/60 or 70kV 1-3 Phase (200 MVA) | per unit |  | 8500
|  |  | (Add additional options) | per unit | N/A | N/A |  | N/A
|  | Line Positions to terminate gen-ties and GSU transformer positions | [7 empty] | Includes cost of related disconnect switches
|  |  | Single Breaker (add third breaker to breaker and a half) | per unit | 1300 | 1400 |  | 1600 |  | and protection equipment for the Breaker
|  |  | Breaker and a half (2CB) | per unit | 3000 | 3200 |  | 3800 |  | position. Assumed space is available in the
|  |  | Breaker and a half (3CB) | per unit | 4000 | 4300 |  | 5100 |  | Substation and control building for the Breaker and
|  |  | Double Breaker (2CB, double bus) | per unit |  |  |  | 3800 |  | its associated Protection Package.
|  | Double Operating Bus Sections - 2 new buses, spanning 2 positions |  | per unit |  | 500 |  | 650 |  | Cost for Bus and structures only. Includes base costs to interface with existing bus.
|  | Double Operating Bus Sections - 2 bus extensions, spanning 2 positions |  | per unit |  | 400 |  | 500 |  | Cost for Bus and structures only. Assumes existing bus can be extended (ie. standard steel).
|  | Sectionalizing Breaker |  | per unit | 1400 | 1800 |  | 2000 |  | Assumed that space is available in the Bus line up and
line reconfiguration or line swapping is not required.
Includes Breaker Protection and Bus Differential schemes.
|  | Shunt Capacitors |  | per step | N/A | 3000 |  | 4500 |  | Includes cost of switching CB per step. Does not include
cost of common breaker for the entire Bank or all the
steps together.
Assumed space is available in the substation.
| Miscellaneous Equipment (see comments) | [8 empty] | These items are rarely required for high-voltage
|  | Bus Tie (1CB) |  | lump sum | [5 empty] | substations. If required, would be estimated as
|  | Shunt Reactors |  | lump sum | [5 empty] | a lump sum in the study.
|  | Series Capacitors |  | lump sum
|  | Static VAR Compensator (SVC) |  | lump sum
|  | Adding second CT wires for breaker replacement |  | lump sum
| Gas Insulated Substation (in lieu of open air construction) |  |  | lump sum | [5 empty] | Not typical, would be estimated as a
lump sum, if GIS is required
Replacement Substation Equipment
|  | Circuit Breakers (with TRV Caps) |  | per unit | N/A | N/A |  | N/A
|  | Circuit Breakers (without TRV caps) |  | per unit | 400 | 450 |  | 650 |  | Only for CB replacement. Excludes Switches, Protection Packages, Bus work or property improvements
|  | Disconnect switches |  | per unit | 150 | 200 |  | 350 |  | 1 set of Breaker Disconnect switches. Assumed structure
and foundation replacement not required.
|  | Line protection relays (other end of line) |  | per terminal | 550 | 650 |  | 650 |  | Assumed switchboard space is available in
|  | Wave Trap - 1 phase only |  | per unit |  | 150 |  | 200 |  | the Control Building for the new relays.
|  | Wave Trap removal |  | per unit |  | 40 |  | 50
New Protection Equipment
|  | New SPS |  | lump sum | [5 empty] | Costs vary widely, will be lump sum
|  | SPS Relays |  | lump sum | [5 empty] | Costs vary widely, will be lump sum
|  | Additional set of bushing current transformers (3) at existing CBs |  | lump sum | [5 empty] | Will be provided on per project basis.
|  | DTT transmitter per PG&E's terminal |  | per unit | 300 | 300 |  | 300 |  | Does not include cost of lease line which is responsibility of the IC. Cost assumes no special Telecomm. requirements and no underground conduit work is required at the Substation for the lease line. Also assumed HVP shelf and other Telecomm equipment exists in the Control Building.
Information Technology (IT) Equipment
IT interface equipment
|  |  | 100' self-supporting comm. tower (3 legs) | per unit | 370 | 370 |  | 370 |  | Any towers over 120" will be lump sum estimates.
|  |  | 120' self-supporting comm. tower (4 legs) | per unit | 400 | 400 |  | 400
IT interface equipment - T/L
|  |  | Fiber optic cable on existing poles | per mile | 50 | 50 |  | 50 |  | Cost of Fiber and Hardware only. Does not include cost for installing the Fiber overhead or in underground conduits. Cost will be calculated on per project basis.
|  |  | Fiber optic cable on new poles | per mile | 50 | 50 |  | 50
| PG&E Meter at Gen Site |  |  |  | 25 | 25 |  | 25 |  | Cost includes pulling secondary wires and installing one electronic meter.
| PG&E RTU at Gen Site for EMS telemetry and RTSCADA |  |  |  | 170 | 170 |  | 170 |  | RTU costs include required work at the associated
PG&E operations center.
| PG&E Pre-parallel Inspection, Compliance Review for Gen Site |  |  |  | 200 | 200 |  | 200 |  | Costs based on a typical interconnection.
New HV Transmission Line
|  | Double Circuit, Strung on both sides, Lattice Tower |  | per mile | 2210 | 2210 | N/A | 2610 | N/A | Unit cost per mile shown is based on flat land/rural setting, engineering and construction costs only. Environmental, Permitting, and Right of way Acquisition costs are not included. Additional factors applied for hilly (1.2X), mountainous (1.3X), and forested (1.5X) terrain. Factors also apply for suburban (1.2X) or urban (1.5X) population density. Line length ≤4 miles (2X), line length 5 to 9 miles (1.5X - 1.1X), Line length ≥10 miles (1X). Costs for 60/70kV are same as for 115kV due to same 115kV standards used for new installation or design. 500kV estimates are not provided since PG&E did not build 500kV lines in recent years.
|  | Double Circuit, Strung on one side, Lattice Tower |  | per mile | 1725 | 1725 | N/A | 2050 | N/A
|  | Single Circuit, Lattice Tower |  | per mile | 1390 | 1390 | N/A | 1635 | N/A
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | per mile | 2470 | 2470 | N/A | 2935 | N/A
|  | Double Circuit, Strung on one side, Tubular Steel Pole |  | per mile | 2050 | 2050 | N/A | 2420 | N/A
|  | Single Circuit, Tubular Steel Pole |  | per mile | 1530 | 1530 |  | 1850 | N/A
|  | Wood poles |  | per mile | 595 | 595 | N/A | N/A | N/A
|  | Light Duty Steel poles |  | per mile | 620 | 620 | N/A | N/A | N/A | 230/500kV lines are built only on steel structures.
Removal of HV Transmission Line (complete tear down)
|  | Double Circuit |  | per mile | 420 | 420 | N/A | 650 | N/A
|  | Single Circuit |  | per mile | 255 | 255 | N/A | 450 | N/A
Reconductor/Upgrade Transmission Line
|  | Double Circuit, Strung on both sides, Lattice Tower |  | per mile | 1560 | 1560 | N/A | 1870 | N/A | Unit cost for reconductoring tubular steel poles assumes the removal of existing poles and installation of all new poles.
|  | Double Circuit, Strung on one side, Lattice Tower |  | per mile | 1170 | 1170 | N/A | 1400 | N/A | Unit cost for reconductoring wood poles and light duty steel poles assumes the removal of existing poles and wire, and installation of all new poles and wire.
|  | Single Circuit, Lattice Tower |  | per mile | 1170 | 1170 | N/A | 1400 | N/A | Unit cost per mile shown is based on flat land/rural setting, engineering and construction costs only. Environmental, Permitting, and Right of way Acquisition costs are not included. Additional factors applied for hilly (1.2X), mountainous (1.3X), and forested (1.5X) terrain. Factors also apply for suburban (1.2X) or urban (1.5X) population density. Line length ≤4 miles (2X), line length 5 to 9 miles (1.5X - 1.1X), Line length ≥10 miles (1X). Costs for 60/70kV are same as for 115kV due to same 115kV standards used for new installation or design. 500kV estimates are not provided since PG&E did not reconductor 500kV lines in recent years.
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | per mile | 2895 | 2895 | N/A | 3585 | N/A
|  | Double Circuit, Strung on one side, Tubular Steel Pole |  | per mile | 2461 | 2461 | N/A | 3070 | N/A
|  | Single Circuit, Tubular Steel Pole |  | per mile | 2090 | 2090 | N/A | 2300 | N/A
|  | Single Circuit, Wood Pole |  | per mile | 740 | 740 | N/A | N/A | N/A
|  | Single Circuit, Light Duty Steel Pole |  | per mile | 765 | 765 | N/A | N/A | N/A
Metering
|  | Upgrade of existing RTUs |  | lump sum
Lump Sum costs below are in addition to per-unit or lump-sum costs listed above:
| Engineering costs |  |  | lump sum
| Capitalized Licensing and Permitting Costs, including |  |  | lump sum
mitigation measures, FAA permits, etc.
Civil work: Site Preparation including site grading, ground grid,
| and walls/fencing/containment |  |  | lump sum
| General Facilities: station light & power, backup generator, |  |  | lump sum
station utilities (water, gas, etc. if manned substation)
| Substation Control (MEER) Buildings |  |  | lump sum
| Incremental cost for transmission line crossings (roads, |  |  | lump sum
streams, rail, highway, other T\L)
| Land cost for substations and T/L ROW |  |  | lump sum
| Incremental cost of soil/geotechnical mitigation measures |  |  | lump sum
| Incremental environmental monitoring and mitigations |  |  | lump sum
| Corporate Overheads (A&G, P&B, and AFUDC) |  |  | lump sum
| Income Tax Component of Contribution (ITCC) |  |  | lump sum
DRAFT

## Factors and Assumptions
2017 PG&E Final Generator Interconnection Unit Cost Guide
Factors for use in developing cost estimates in Phase I Generator Interconnection Studies
As of _____01/01/2017_____
Simplified example on how to apply factors:
[10 empty] | $ millions | Apply Factor | Delta
| Hypothetical baseline cost per mile for Double Circuit 220 kV line (strung one side) using Lattice Towers: | [8 empty] | 1
Known characteristics of proposed transmission line ROW at Phase I study:
|  | Will be constructed in mountainous terrain | [7 empty] | 1.5 | 1 x 1.5 = 1.5 | 0.5
Rural
|  | Line Length = 15 miles | [7 empty] | 1 | 1.0 x 1.0 = 1.0 | 0
|  |  | Total Delta (summation of applied factor) | [8 empty] | 0.5
|  |  | Estimated cost per mile | [8 empty] | 1
|  |  | Estimated cost per mile including applied factors ($ million/ mile) | [8 empty] | 1.5
|  | Factor Type: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | flat |  |  | hilly |  | mountain |  | forest
|  |  | Population density |  | rural |  | desert | suburban |  | urban/metro
|  |  | Line Length |  | ≥10 miles |  |  | 5 to 9 miles |  | ≤ 4 miles
|  | Factor Amounts: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | 1 |  |  | 1.3 |  | 1.5
|  |  | Population density |  |  | 1 |  |  | 1.2 |  | 1..5
|  |  | Line Length |  |  | 1 |  |  | 1.5 - 1.1 |  | 2
|  | Factor Type |  | Explanation of Factor issues and Factor multipliers
|  | Terrain |  | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex and costly.
|  | Population density |  | Population and land use affect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
|  | Line Length |  | Length of transmission lines affects the per mile cost. Shorter lines will have higher unit cost due to mobilization/de-mobilization, lack of economy of scale, stringing operations and other construction activities.
Other assumptions underlying unit cost guide:
| Assumption | [11 empty] | Explanation
All labor is straight time and based on a 5 day work week schedule. Overtime may be required due to clearances and work hour restrictions to meet project schedules.
| Contingency factor for New Transmission Line: 35%, Contingency for Reconductoring Transmission Line (assuming 25% tower modification and no foundation issue): 50%. Contingency factor for Substation Equipment and Installation: 0% (zero %) | [11 empty] | Accuracy of the cost estimate for budgeting pupose is based on level of detail engineering completed.
| Owner's Representative Fee for EPC construction: 10% of the total project cost | [11 empty] | Additional cost for PTO to manage,monitor and provide technical oversight of the project
Unit costs include costs to procure materials, installation, engineering, project management costs, home office costs, and contingency
Unit costs exclude allocated corporate overhead and AFUDC (will be added to total cost estimates)
Unit costs exclude generator's responsibility for Income Tax Component of Contribution (ITCC), (will be added to total cost estimates, if required)
Unit costs exclude environmental monitoring and mitigations
Transmission line cost per mile assumes conventional construction
Cost per mile of T\L requiring helicopter construction (or deconstruction) will have higher than published per-unit cost, the labor component of helicopter construction is incrementally higher, which is not included in the per-unit cost
The unit costs assume that operational clearances are available as required.
Installations at 500kV are rare for generation interconnection projects in PG&E's service area and good cost data is not available. PG&E will have to develop 500 kV cost on a case-by-case basis.
The estimated costs here do not include any applicable ITCC tax.
Cost estimates assume that the project site has regular soil conditions and is not located in an extra high seismic zone as identified in PG&E DCM 073102 nor in a locations consisting of the following conditions: liquefiable soils, expansive soils, unstable soils, susceptible to rupture, high ground water table (less than approximately 15 feet below finish grade), FEMA flood zone(s), excessive ground settlement due to subsidence or other geological factors, and hilly and/or rocky terrain requiring substantial grading effort.
Costs also assume that the site can be drained via customary storm water drainage infrastructure (i.e., without pump or lift stations) and not require on-site percolation basins. Costs assume including implementing Storm Water Pollution and Prevention (SWPP) and SPCC oil containment system(s).
Cost does not include any remedial work for impact on neighboring properties.
Costs assume that the on-site existing soil is adequate for engineered fill and can be reused on-site to achieve a balanced cut-fill earthwork volume. Costs do not assume removal of hazardous material or site remediation.
Costs assume that the site has nearby easy access to public roads and does not include any costs for access roads outside the substation.
Costs do not assume extensive permitting effort.
For installing Fiber Optic on existing poles the listed cost is only for the Fiber. It does not include splicing, stringing, relocation or replacement of poles, engineering or installation cost. Installation will be performed by Transmisson line Groups and they will estimate the cost on project basis.
For installing Fiber Optic on new poles the listed cost is only for the Fiber. It does not include splicing, stringing, banding equipment, specialized Fiber, additional staging efforts, material costs, engineering or installation costs. Installation will be performed by Transmission line Groups and they will estimate the cost on project basis.

## Escalation Rates & Factors
2017 PG&E Final Generator Interconnection Unit Cost Guide
OVERVIEW :
Current PTO Unit Cost Guide as posted on the CAISO website is in 2017 Constant Dollars.
PTO’s cost estimating is done in constant dollars and then escalated over the years during which the
project will be constructed, arriving at project costs in nominal dollars.
Current escalation rates used to arrive at costs in nominal dollars are from for total electric transmission plant from IHS Global Insight's Q3 2016 Power Planner forecast.
DEFINITIONS USED :
Project Cost in Constant Dollars represents the cost of the Project if all costs were paid for at a single point
in time.
Project Cost in Nominal Dollars represents the cost of the Project taking into account when actual dollars will be spent.
Mathematical formula: Cost in Nominal Dollars |  |  |  |  | = Cost in Constant Dollars x Escalation Factor
CURRENT PTO ESCALATION RATES *:
| 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
Escalation Rates |  | 2.262% | 2.308% | 2.32% | 2.332% | 2.376% | 2.411% | 2.323% | 2.38% | 2.082% | 2.082%
2017 Escalation Factors | 1 | 1.0226 | 1.0462 | 1.0705 | 1.0955 | 1.1215 | 1.1485 | 1.1752 | 1.2032 | 1.2282 | 1.2538

## Other Documentation
If in the process of developing estimates of the costs for upgrades for any specific generation project, a PTO has the ability to estimate transmission upgrade costs more accurately due to the existence of a similar transmission project that has recently been built (in other words, a comparable project), then the costs associated with the comparable projects may be used as a basis for that PTO estimation of costs for the specific project instead of using per-unit costs. A discussion of this option should be included in the PTO per-unit cost guide. Furthermore, when this option is used in a Phase II cost estimation process, the fact that this option has been used should be documented in the Phase II study results report along with any pertinent information regarding the comparable project whose costs were used. Because PG&E has no recent data/cost for 500 kV construction, the per mile cost is based on SCE per unit costs.