## TxCapabilityEstimates
Transmission capability estimates for use in the CPUC's IRP process - Revised 10/28/2021
Transmission Constraint | Affected Zones | Condition under which Constraint is Binding | Estimated FCDS Capability Based on On-peak Study Resource Output (MW)** |  | ADNU & Cost Estimate ($million) |  | Estimated EODS Capability Based on Off-peak Study Resource Output (MW)** |  | AOPNU & Cost Estimate ($million) |  | Wind/Solar Area Designation
|  |  | Existing System*** | Incremental due to ADNU | ADNU (Time to Construct) | Cost (Escalated to COD) | Existing System*** | Incremental due to AOPNU | AOPNU (Time to Construct) | Cost (Escalated to COD)
SCE Northern Study Area Constraints
South of Magunden Constraint | Non-CREZ – Big Creek | On-peak | 670 | 840 | Magunden 500kV upgrade (105 months) | 1197 | 1,024* | N/A | N/A | N/A | Solar
Antelope – Vincent Constraint | Tehachapi, Non-CREZ – Big Creek | On-peak | 4040 | 2700 | Antelope - Vincent 500kV line rating increase (18 months) | 15 | 5,171* | N/A | N/A | N/A | Solar
Windhub 500/230 kV Transformer Constraint | Tehachapi | On-peak, Off-peak | 1685 | 2395 | New 500/230kV substation connecting to Windhub 230kV and Vincent 500 kV (108 months) | 1126 | 1685 | 1385 | New 500/230kV substation connecting to Windhub 230kV and Vincent 500 kV (108 months) | 1126 | Solar
SCE Metro Study Area Constraints
Laguna Bell – Mesa Constraint | Non-CREZ – Ventura | On-peak | 0 | 3178 | Laguna Bell - Mesa line upgrade (27 months) | 15 | 2,708* | N/A | N/A | N/A | Solar
SCE Metro Area | Non-CREZ – SCE Metro | None | 4,083* | N/A | N/A | - | 4,083* | N/A | N/A | N/A | N/A
SCE North of Lugo (NOL) Study Area Constraints
Lugo 500/230 kV Transformer Constraint | Inyokern_North_Kramer, Victor, Pisgah | On-peak | 1576 | 980 | New Lugo 500/230kV No. 3 transformer (42 months) | 70 | 1,619* | N/A | N/A | N/A | Solar
Victor-Lugo Constraint | Inyokern_North_Kramer Victor | On-peak | 1156 | 430 | Reconductor Lugo - Victor 230kV lines (27 Months) | 226 | 1,311* | N/A | N/A | N/A | Solar
Kramer- Victor/Roadway -Victor Constraint | Inyokern_North_Kramer | On-peak, Off-peak | 826 | 430 | Loop in Kramer - Victor 115kV line into Roadway and reconductor Kramer to Lugo 230kV lines (81 months) | 108 | 1237.02 | 480 | Loop in Kramer - Victor 115kV line into Roadway and reconductor Kramer to Lugo 230kV lines (81 months) | 108 | Solar
SCE Eastern Study Area Constraints
Serrano – Alberhill – Valley 500 kV Constraint | Riverside_Palm_Springs, Arizona, Imperial | On-peak | 5700 | 3648 | Devers - Mira Loma - Mesa 500kV line (105 months) | 1480 | 11,800* | N/A | N/A | N/A | Solar
Devers – Red Bluff 500 kV Constraint | Riverside_Palm_Springs, Arizona | On-peak, Off-peak | 5400 | 3100 | New Devers - Red Bluff 500kV No. 3 line (105 months) | 1022 | 5820 | 1876 | New Devers - Red Bluff 500kV No. 3 line (105 months) | 1022 | Solar
Colorado River 500/230 kV Transformer Constraint | Riverside_Palm_Springs: Colorado River Substation 230 kV | On-peak | 1490 | 1000 | New Colorado River 500/230kV No. 3 transformer (42 months) | 74 | 1,739* | 1000 | New Colorado River 500/230kV No. 3 transformer (42 months) | 74 | Solar
SCE/GLW East of Pisgah (EOP) Study Area Constraints
Eldorado 500/230 kV Transformer #5 Constraint | Southern_Nevada, 'Eldorado/Mountain Pass (230kV) | On-peak | 3360 | 400 | New Eldorado 500/230 transformer (42 months) | 70 | 3,360* | N/A | N/A | N/A | Solar
GLW-VEA Area Constraint | Southern_Nevada | On-peak, Off-peak | 300 | 1000 | Pahrump - Sloan Canyon 230kV line rebuild and Innovation - Desert View 230kV line rebuild + other upgrades (60 months) | 175 | 269 | 1110 | Pahrump - Sloan Canyon 2nd 230kV line and Innovation - Northwest 2nd 230kV line + other upgrades (60 months) | 200 | Solar
Mohave/Eldorado 500 kV | Southern_Nevada | On-peak | 1,560* | N/A | N/A | - | 1,560* | N/A | N/A | N/A | Solar
SDG&E Study Area Constraints
East of Miguel Constraint | Arizona, Imperial, Baja, Riverside | On-peak, Off-peak | 731 | 1412 | New Imperial Valley - Serrano 500 kV line (120 months) | 3680 | 950 | 943 | New Imperial Valley - Serrano 500 kV line (120 months) | 3680 | Solar
Encina-San Luis Rey Constraint | Arizona, Imperial, Baja, Non-CREZ within San Diego | On-peak | 2901 | 3718 | New Encina - San Luis Rey 230 kV line (120 months) | 102 | 3,035* | N/A | N/A | N/A | Solar
Imperial Valley transformer Constraint | Imperial | On-peak | 1959 | 400 | Install a new Imperial Valley 500/230 kV Bank at new substation (105 months) | 214 | 1,959* | N/A | N/A | N/A | Solar
San Luis Rey-San Onofre Constraint | Arizona, Imperial, Non-CREZ within San Diego | On-peak | 1748 | 4269 | New San Luis Rey-San Onofre 230 kV line (120 months) | 237 | 3,281* | N/A | N/A | N/A | Solar
San Diego Internal Constraint | Imperial, Non-CREZ within San Diego | On-peak, Off-peak | 968 | 2067 | Internal San Diego Area reconductoring (18 months) | 89 | 290 | 274 | Internal San Diego Area reconductoring (18 months) | 89 | Solar
Silvergate-Bay Boulevard Constraint | Imperial, Baja, Non-CREZ within San Diego | On-peak | 1202 | 2119 | Silvergate - Bay Blvd 230kV 3-ohm Series Reactor (72 months) | 31 | 2,163* | N/A | N/A | N/A | Wind
San Diego Oceanside Constraint | Non-CREZ within San Diego | On-peak | 280 | 301 | Oceanside ADNU (60 months) | 133 | 280* | N/A | N/A | N/A | Solar
Orange County Area | Non-CREZ within San Diego | None | 450* | N/A | N/A | - | 450* | N/A | N/A | N/A | N/A
Transmission Constraint | Affected Zones | Condition under which Constraint is Binding | Estimated FCDS Capability Based on On-peak Study Resource Output (MW)** |  | ADNU & Cost Estimate ($million) |  | Estimated EODS Capability Based on Off-peak Study Resource Output (MW)** |  | AOPNU & Cost Estimate ($million) |  | Wind/Solar Area Designation
|  |  | Existing System*** | Incremental due to ADNU | ADNU (Time to Construct) | Cost (Escalated to COD) | Existing System*** | Incremental due to AOPNU | AOPNU (Time to Construct) | Cost (Escalated to COD)
PG&E North of Greater Bay Study Area Constraints
Rio Oso-SPI-Lincoln 115 kV Line | Rio Oso area within Sacramento River | On-peak | 41.96 | 54.3658 | Rio Oso (74 months) | 17.5 | 124* | N/A | N/A | N/A | WInd
Woodland-Davis 115 kV Lines | Davis Area within Sacramento River | On-peak | 63.5 | 35.6462 | Q653-Davis (60 months) | 11 | 64* | N/A | N/A | N/A | WInd
Cortina -Vaca-Dixon 230kV Line | Sacramento River& Round Mountain | On-peak | 454 | 2838.4655 | Delevan 500kV (144 months) | 3531 | 795* | N/A | N/A | N/A | Wind
Humboldt-Trinity 115 kV Line | Humboldt | On-peak | 20.52 | 57.3983 | Humboldt (98 months) | 158 | 63* | N/A | N/A | N/A | Wind
PG&E Greater Bay Study Area Constraints
Vierra-Tracy-Kasson 115 kV Line | Kasson Area within Sacramento River | On-peak | 149.21 | 125.33 | Vierra-Tracy-Kasson 230 kV (62 months) | 15 | 247* | N/A | N/A | N/A | WInd
Melones-Tulloch 115 kV Line | Melones area within Sacramento River | On-peak | 126.3 | 45.6888 | Melones-Tulloch 230 kV (64 months) | 18 | 239* | N/A | N/A | N/A | WInd
Contra Costa-Delta Switchyard 230kV Line | Solano & Round Mountain | On-peak | 1523 | 1476.0142 | Bay Area (CC) (86 months) | 505 | 1,523* | N/A | N/A | N/A | Wind
PG&E South 500 kV Study Area Constraints
Gates-Panoche #1 and #2 230kV Lines | Westlands and Carizzo | On-peak, Off-peak | 10830 | 378 | Gates-Panoche #1 and #2 230kV lines (50 months) | 259 | 10,830* | N/A | Gates-Panoche #1 and #2 230kV lines (50 months) | 259 | Solar
PG&E East Kern Study Area Constraints
Midway – Gates 230kV Line | Kern and Greater Carrizo | On-peak, Off-peak | 1431 | 3136.64 | Gates - Arco - Midway 230 kV-Redraw boundary (98 months) | 142 | 2568* | N/A | Gates - Arco - Midway 230 kV-Redraw boundary (98 months) | 142 | Solar
Kern–Lamont-Stockdale 115kV Line | Carrizo | Off-Peak | 100* | N/A | N/A | N/A | 124.8 | 30 | Lamont-Stockdale 115kV ( 74 months) | 83.7 | Solar
PG&E West Kern Study Area Constraints
Morro Bay-Templeton 230kV Line | Westlands Kern and Carizzo | On-peak, Off-peak | 1707.56 | 738.69 | Morro Bay 230 kV (98 months) | 1248 | 1903* | N/A | Morro Bay 230 kV (98 months) | 1248 | Solar
PG&E Fresno Study Area Constraints
Gates 500/230kV Bank #13 Constraint | Westlands, Carrizo and Kern | On-peak, Off-peak | 3151 | 4453 | Gates TB # 13 ADNU (48 months) | 39.6 | 3279 | 964 | Gates TB # 13 ADNU (48 months) | 39.6 | Solar
Wilson-Storey-Borden #1 & #2 230 kV Lines | Within Westlands | On-peak | 113 | 96 | Wilson-Storey-Borden #1 and #2 230kV lines (50months) | 232.1 | 816* | N/A | N/A | N/A | Solar
Los Banos 500/230kV TB | Westlands | On-peak | 1127 | 446 | Manining ADNU (72 months) | 369.9 | 2,534* | N/A | N/A | N/A | Solar
Tesla-Westley 230kV Line | Los Banos and Central Valley | On-peak | 1098 | 114 | Reconductor Tesla-Westley 230 kV Line (50months) | 89.9 | 1,098* | N/A | N/A | N/A | Solar
Moss Landing 500kV | Unconstrained zone | On-peak | 1,500* | N/A | None | N/A | 1,500* | N/A | N/A | N/A | Solar
Warnerville-Wilson 230kV | Westlands | Off-Peak | 272* | N/A | N/A | N/A | 737 | 364 | Warnerville-Wilson 230kV (86 months) | 36.1 | Solar
Moss Landing-Las Aguilas 230kV | Los Banos and Central Valley | Off-Peak | 316* | N/A | N/A | N/A | - | 1308 | Moss Landing-Las Aguilas 230kV (98 months) | 47.7 | Solar
Las Aguillas-Panoche #1 and #2 230kV | Los Banos and Central Valley | Off-Peak | 334* | N/A | N/A | N/A | 516 | 939 | Las Aguillas sw sta-Panoche #1 and #2 230kV (78 months) | 316.6 | Solar
Moss Landing-Los Banos 230kV | Los Banos and Central Valley | Off-Peak | 1,611* | N/A | N/A | N/A | 3102 | 1822 | Moss Landing-Los Banos 230kV (98 months) | 67.8 | Solar
Los Bano-Gates #1 500kV line | Westlands/Los Banos | Off-Peak | 1,265* | N/A | N/A | N/A | 2595 | 2076 | Los Banos-Gates #1 500kV line (98 months) | 640 | Solar
* Capability estimate reflects the amount of resources studied in the corresponding deliverability case as binding constraints are not identified
** The transmission capability estimates are based on the resource-type specific output assumptions that are used in deliverbility studies rather than the resources’ installed capacity. The values can be translated into any combination of resource types by applying the applicable deliverability study resource output factors.
***The transmission capability estimates are over and above the baseline contracted future resource amounts the CPUC transmitted as part of its resource prortfolios for use in the CAISO 2020-2021 TPP. The CPUC will need to adjust the estimates to account for additional resources that have been added to the baseline resource list since then. Retirements of Diablo Canyon and OTC generating units are accounted for in the estimates assuming the replacement resources are at the same or similar locations.