## Cost Details
All costs are $x1,000
2012 Final SCE Generator Interconnection Unit Cost Guide |  |  |  | "Voltages" | 66 kV | 115 kV | 138 kV | 230 kV | 500 kV | Notes/Comments:
Revised as of: 04/03/2012
Equipment Categories |  |  |  | Units | [5 empty] | Note: SCE Unit Costs for equipment at voltages 33 kV and below are estimated on an as-needed basis, and are not published on the CAISO website.
New Substation Equipment
|  | Complete Loop-in Substation, equipped with one line position to |  |  | 3690 | 3900 | N/A | 17940 | 38970 | Includes all necessary equipment, including operating buses, one double-breaker line position on a breaker-and-a-half (BAAH) configuration for gen-tie, one three-breaker line position on a BAAH configuration to loop transmission line, substation control building (MEER), and associated protective relays. Also includes base costs of site preparation, ground grid, fencing, and driveway. Does not include licensing or environmental mitigations.
terminate a single gen-tie
|  | Transformer Banks: | [7 empty] | Unit cost of transformer banks reflects
|  |  | 500/230 kV 4-1 Phase | per unit | N/A | N/A | N/A | N/A | 51780 | cost of the highest MVA rated transformer
|  |  | 500/230 kV 3-1 Phase | per unit | N/A | N/A | N/A | N/A | 38560 | for the given voltage.
|  |  | 500/115 kV 1-3 Phase | per unit | N/A | N/A | N/A | N/A | 20510 | (500/230 kV = 1120 MVA)
|  |  | 230/115 kV | per unit | N/A | N/A | N/A | 8100 | N/A | (500/115 kV = 560 MVA)
|  |  | 230/66 kV | per unit | N/A | N/A | N/A | 9130 | N/A | (230/66 kV = 280 MVA)
|  | Line Positions to terminate gen-ties and Transformer Bank positions | [7 empty] | Position cost estimate includes cost
|  |  | Single Breaker (add third breaker to breaker and a half) | per unit | 790 | 850 | N/A | 1740 | 6670 | of any related disconnect switches
|  |  | Breaker and a half (2CB) | per unit | 1230 | 1390 | N/A | 2970 | 9840 | and protection equipment located within
|  |  | Breaker and a half (3CB) | per unit | 1640 | 1900 | N/A | 4410 | 15380 | the position
|  |  | Double Breaker (2CB, double bus) | per unit | N/A | N/A | N/A | 3110 | N/A
|  |  | Operating / Transfer Bus | per unit | 920 | 1000 | N/A | N/A | N/A
|  | Double Operating Bus Sections - 2 new buses, spanning 2 positions |  | per unit | N/A | N/A | N/A | 750 | 2590 | Typical configuration for 500 kV, includes "pair" of N/S or E/W buses
|  | Double Operating Bus Sections - 2 new buses, spanning 4 positions |  | per unit | 140 | 310 | N/A | 930 | N/A | Typical configuration for 230/115/66 kV, includes "pair" of N/S or E/W buses
|  | Double Operating Bus Sections - 2 bus extensions, spanning 2 positions |  | per unit | N/A | N/A | N/A | 500 | 1740 | Used in substation expansion
|  | Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  | per unit | 100 | 260 | N/A | 620 | N/A | Used in substation expansion
|  | Sectionalizing Breaker |  | per unit | 450 | 820 | N/A | 1300 | N/A
|  | Shunt Capacitors |  | per unit | 1440 | 1620 | N/A | 4310 | 25000 | Includes cost of CB
| Miscellaneous Equipment (see comments) | [8 empty] | These items are rarely required for
|  | Bus Tie (1CB) |  | lump sum | [5 empty] | high-voltage substations. If required,
|  | Shunt Reactors |  | lump sum | [5 empty] | would be estimated as a lump sum.
|  | Phase Shifter |  | lump sum
|  | Ground Bank |  | lump sum
|  | Series Capacitors |  | lump sum
|  | Static VAR Compensator (SVC) |  | lump sum
|  | Tertiary Reactors (1 reactor, 1 bay) |  | lump sum
| Gas Insulated Substation (in lieu of open air construction) |  |  | lump sum | [5 empty] | Not typical, would be estimated as a
Lump sum, if GIS required
Replacement Substation Equipment
|  | Line drops - 3 phases |  | per unit | 80 | 80 | N/A | 120 | 260
|  | Circuit Breakers (including replacement of foundation) |  | per unit | N/A | N/A | N/A | 790 | 2670
|  | Circuit Breakers (without TRV caps) |  | per unit | 410 | 510 | N/A | 720 | 2460
|  | Transient recovery voltage capacitors (set of 3, separate from CBs) |  | per unit | N/A | N/A | N/A | 140 | 240
|  | Disconnect switches (incl. steel structures and foundations) |  | per unit | 130 | 140 | N/A | 300 | 700
|  | Line protection relays (other end of line) |  | per set | 180 | 190 | N/A | 250 | 340
|  | Wave Trap - 1 phase only |  | per unit | N/A | N/A | N/A | 70 | 140
|  | Wave Trap removal |  | per unit | N/A | N/A | N/A | 40 | 260
New Protection Equipment
|  | New SPS |  | lump sum | [5 empty] | Costs vary widely, will be lump sum
|  | SPS Relays |  | lump sum | [5 empty] | Costs vary widely, will be lump sum
|  | Additional set of bushing current transformers (3) at existing CBs |  | lump sum | [5 empty] | Not separately estimated, but rolled into cost of SPS
Information Technology (IT) Equipment
IT interface equipment - Control Rooms
|  |  | Communication rack placed in existing B station MEER bldg | per set | 34.5 | 34.5 | N/A | 34.5 | 34.5 | Used primarily for distribution-level (B) substations
|  |  | Comm. Rack with own environmental enclosure | per set | 73 | 73 | N/A | N/A | N/A | Used primarily for distribution-level substations without MEER bldg
|  |  | Full Comm. package for AA or A stations | per set | N/A | N/A | N/A | 238.5 | 238.5 | Excludes battery room, cable trays, power supply (in MEER bldg cost)
|  |  | Prefab communications building | per unit | 515.4 | 515.4 | N/A | 515.4 | 515.4 | If needed to build from scratch
|  |  | 48V DC power supply for comm. equipment | per set | 74.7 | 74.7 | N/A | 74.7 | 74.7 | Excludes batteries (in MEER bldg cost)
|  |  | 100' self-supporting comm. tower (3 legs) | per unit | N/A | N/A | N/A | 369.9 | 369.9 | Not used on high density or mountaintop locations
|  |  | 120' self-supporting comm. tower (4 legs) | per unit | N/A | N/A | N/A | 630.7 | 630.7 | Any towers over 120" will be lump sum estimates due to high permit costs
IT interface equipment - miscellaneous equipment
|  |  | Lightwave terminal | per unit | 96.5 | 96.5 | N/A | 96.5 | 96.5 | One needed for each comm. system connected (SPS requirement)
|  |  | Microwave terminal and dish antennas | per set | N/A | N/A | N/A | 287.6 | 287.6 | One set typically needed for each end of path, includes cost of FCC license
|  |  | Dehydrator for microwave antennas | per unit | N/A | N/A | N/A | 12.5 | 12.5
|  |  | Channel bank | per unit | 44.6 | 44.6 | N/A | 44.6 | 44.6 | Also referred to as a multiplexer
|  |  | Digital Access Cross Connect (DACS) | per unit | 151.3 | 151.3 | N/A | 151.3 | 151.3
|  |  | Network synchronization equipment (BITS clock) | per unit | 99.3 | 99.3 | N/A | 99.3 | 99.3
|  |  | Large router for network access to work bases | per unit | N/A | N/A | N/A | 188 | 188 | Selection of large or small router
|  |  | Small router for equipment monitoring, "data beyond SCADA" | per unit | 32.7 | 32.7 | N/A | 32.7 | 32.7 | depends on amount of substation automation and data requirements
|  |  | T1 cross connect | per unit | 3.1 | 3.1 | N/A | 3.1 | 3.1 | Interconnects new facility to existing network
|  |  | Fiber to Telco connection (high voltage protected) | per unit | 110.9 | 110.9 | N/A | 110.9 | 110.9 | For subs requiring local phone service
|  |  | Satellite Terminal for "RTU only" locations | per unit | 65.2 | 65.2 | N/A | N/A | N/A | For "RTU only" locations without line protection or other communication requirements
IT interface equipment - T/L
|  |  | Fiber optic cable on existing poles | per mile | 75 | 75 | N/A | 75 | 75 | Fiber optic cable on new T/L included in
|  |  | Fiber optic cable on new poles | per mile | 105 | 105 | N/A | 105 | 105 | transmission line cost per mile
New HV Transmission Line
|  | Double Circuit, Strung on both sides, Lattice Tower |  | per mile | N/A | N/A | N/A | 2970 | 5950 | Unit cost per mile shown is based on
|  | Double Circuit, Strung on one side, Lattice Tower |  | per mile | N/A | N/A | N/A | 2260 | 5130 | flat land/rural setting. Additional factors
|  | Single Circuit, Lattice Tower |  | per mile | N/A | N/A | N/A | 1640 | 2970 | applied for hilly (1.5X), mountainous (2.0X),
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | per mile | N/A | N/A | N/A | 5740 | 8920 | and forested (3.0X) terrain (see factors tab)
|  | Double Circuit, Strung on one side, Tubular Steel Pole |  | per mile | N/A | N/A | N/A | N/A | *** | Factors also apply for suburban (2.0X)
|  | Single Circuit, Tubular Steel Pole |  | per mile | N/A | N/A | N/A | 3280 | 4610 | or urban (3.0X) population density.
*** Not recommended by SCE Transmission Engineering
|  | Wood poles |  | per mile | N/A | N/A | N/A | N/A | N/A | May be used at lower voltages
SubTransmission Line (Overhead Facilities)
|  | New single circuit line - Metropolitan |  | per mile | 1508.76 | 1369.17 | N/A | N/A | N/A | New Facilities: 8 lb wind (Metro) & 12 lb wind (Rural), 954 SAC conductor, light weight steel (LWS) poles, 2 tubular steel poles (TSPs), Distribution & Telecom
|  | New single circuit line - Rural/Desert |  | per mile | 1513.215 | 1559.25 | N/A | N/A | N/A
|  | New double circuit line - Metropolitan |  | per mile | 1741.905 | 1759.725 | N/A | N/A | N/A
|  | New double circuit line - Rural/Desert |  | per mile | 1819.125 | 1819.125 | N/A | N/A | N/A
|  | Reconductor existing single circuit line section - Metropolitan |  | per mile | 738.045 | 801.9 | N/A | N/A | N/A | Reconductor/Modify Existing Facilities: 8 lb wind (Metro) & 12 lb wind (Rural), 954 SAC conductor, replace 1/4 of existing wood poles (Metro) & 1/2 of existing wood poles (Rural), Distribution & Telecom under-build
|  | Reconductor existing single circuit line section - Rural/Desert |  | per mile | 772.2 | 1470.15 | N/A | N/A | N/A
|  | Reconductor existing double circuit line section - Metropolitan |  | per mile | 868.725 | 905.85 | N/A | N/A | N/A
|  | Reconductor existing double circuit line section - Rural/Desert |  | per mile | 994.95 | 1039.5 | N/A | N/A | N/A
|  | Double circuit existing single circuit line section - Metropolitan |  | per mile | 1079.595 | 1113.75 | N/A | N/A | N/A
|  | Double circuit existing single circuit line section - Rural/Desert |  | per mile | 1278.585 | 1321.65 | N/A | N/A | N/A
|  | New Remote Transmission Switch (RTS) - Any area |  | per mile | 118.8 | 118.8 | N/A | N/A | N/A | RTS: Includes replacing pole
|  | New single circuit "tap" line to new sub from existing pole line |  | 400 linear ckt ft | 574.695 | 599.94 | N/A | N/A | N/A | Tap: 336 ACSR conductor, 2 TSPs
|  | New double circuit "loop-in" line to new sub from existing pole line |  | 400 linear ckt ft | 610.335 | 629.64 | N/A | N/A | N/A | Loop: 954 SAC conductor, 2 TSPs
|  | PTO gen-tie line section from sub to 1st structure outside sub |  | 200 linear ckt ft | 250.2225 | 259.875 | N/A | N/A | N/A | Gen-Tie: 336 ACSR conductor, 1 TSP
SubTransmission Line (Underground Facilities)
|  | New single circuit line (w/3000 Copper cable) - Any area |  | per mile | 5916.24 | 6165.72 | N/A | N/A | N/A | New Facilities: 2 TSP risers, substructure (ducts & vaults)
|  | New double circuit line (w/3000 Copper cable) - Any area |  | per mile | 8662.005 | 9174.33 | N/A | N/A | N/A
|  | Re-cable existing single circuit line section (w/2000 Copper cable) - Any area |  | per mile | 2450.25 | N/A | N/A | N/A | N/A | Use existing substructure
|  | Re-cable existing single circuit line section (w/3000 Copper cable) - Any area |  | per mile | 3197.205 | 5019.3 | N/A | N/A | N/A | Add 2 additional vaults
|  | Bundle existing single circuit line section (w/1750 Aluminum cable) - Any area |  | per mile | N/A | 2169.585 | N/A | N/A | N/A | Use existing TSPs & add steel arms
|  | Open shields on existing line section - Any area |  | per vault | 44.55 | 44.55 | N/A | N/A | N/A | Install vault arresters
| Removal of HV Transmission Line (complete tear down) | [8 empty] | Cost of removal only, assume any rebuild
|  | Double Circuit |  | per mile | N/A | N/A | N/A | 920 | N/A | would use "new transmission line" from
|  | Single Circuit |  | per mile | N/A | N/A | N/A | 510 | 1070 | section above. Will include similar factors
as new transmission line
Reconductor/Upgrade Transmission Line
|  | Double Circuit, Strung on both sides, Lattice Tower |  | lump sum | [5 empty] | Costs vary widely depending on
|  | Double Circuit, Strung on one side, Lattice Tower |  | lump sum | [5 empty] | number of structures that require
|  | Single Circuit, Lattice Tower |  | lump sum | [5 empty] | upgrade. As a result, will be estimated
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | lump sum | [5 empty] | as a lump sum.
|  | Double Circuit, Strung on one side, Tubular Steel Pole |  | lump sum
|  | Single Circuit, Tubular Steel Pole |  | lump sum
Metering
|  | Upgrade of existing RTUs |  | lump sum | [5 empty] | Cost varies widely, will be lump sum
Lump Sum costs below are in addition to per-unit or lump-sum costs listed above: | [9 empty] | Lump-sum costs are not published on CAISO website, but are included in Phase I cost estimates
| Engineering costs |  |  | lump sum | [5 empty] | These costs are generally included
in the per-unit cost of equipment.
However, if any identified incremental
costs exceed the per-unit amount, they
will be estimated as a lump sum.
| Capitalized Licensing and Permitting Costs, including |  |  | lump sum | [5 empty] | As best estimated at time of Phase I
| mitigation measures, FAA permits, etc. | [8 empty] | study
| Civil work: Site Preparation including site grading, ground grid, | [8 empty] | Civil, general facilities, MEER buildings, and any other facilities that are unique to a given project are lump sums
| and walls/fencing/containment |  |  | lump sum
| General Facilities: station light & power, backup generator, |  |  | lump sum
station utilities (water, gas, etc. if manned substation)
| Substation Control (MEER) Buildings |  |  | lump sum | [5 empty] | Includes cost of batteries, DC power supply, cable trays
| Incremental cost for transmission line crossings (roads, |  |  | lump sum | [5 empty] | Number of crossings are highly variable.
| streams, rail, highway, other T\L) | [8 empty] | As a result, will be estimated as a lump sum
| Land cost for substations and T/L ROW |  |  | lump sum | [5 empty] | Land costs are highly variable.
As a result, will be estimated as a lump sum
| Incremental cost of soil/geotechnical mitigation measures |  |  | lump sum | [5 empty] | Unable to perform detailed geotechnical
analysis of land in Phase I study, but
any known geotech mitigation measures
will be estimated as a lump sum
| Incremental environmental monitoring and mitigations |  |  | lump sum
| Corporate Overheads (A&G, P&B, and AFUDC) |  |  | lump sum | [5 empty] | Per-unit costs shown above do not include
| Income Tax Component of Contribution (ITCC) |  |  | lump sum | [5 empty] | A&G, P&B, AFUDC, or ITCC.
Note on O21: Standard Configuration: Added highest MVA rating following stakeholder meeting on 1/24/2012
DRAFT

## BulkTrans Factors & Assumptions
2012 Proposed SCE Generator Interconnection Unit Cost Guide
Bulk Transmission (500 & 220 kV) Factors for use in developing cost estimates in Phase I Generator Interconnection Studies
As of January 2012
Simplified example on how to apply factors:
[10 empty] | $ millions | Apply Factor | Delta
| Hypothetical baseline cost per mile for Double Circuit 220 kV line (strung one side) using Lattice Towers: | [8 empty] | 2
Known characteristics of proposed transmission line ROW at Phase I study:
|  | Will be constructed in mountainous terrain | [7 empty] | 2 | 2.0 x 2.0 =4 | 2
No population density issues
|  | High wind-prone area (but not icy) | [7 empty] | 1.35 | 2.0 x 1.35 =2.7 | 0.7
|  |  | Total Delta (summation of applied factor) | [8 empty] | 2.7
|  |  | Estimated cost per mile | [8 empty] | 2
|  |  | Estimated cost per mile including applied factors ($ million/ mile) | [8 empty] | 4.7
|  | Factor Types: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | flat |  |  | hilly |  | mountain |  | forest
|  |  | Population density |  | rural |  | desert | suburban |  | urban/metro
|  |  | Weather study (increase in |  | 1/2" ice, or 20# wind |  |  | 1" ice, 6# wind |  | > 2" ice, 6# wind
structural steel amount and foundation volume)
|  | Factor Amounts: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  | 2.0X to 3.0X
|  |  | Population density |  |  | 1.00X to 1.10X |  |  | 1.33X |  | 1.67X
|  |  | Weather study |  |  | 1.35X |  |  | 1.45X |  | 1.60X
|  |  | Factor Type | Explanation of Factor issues and Factor multipliers
|  |  | Terrain | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
|  |  | Population density | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
|  |  | Weather study | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure types or an increased number of structures to reduce the span lengths.
Other assumptions underlying unit cost guide:
Assumption
General labor overtime: based on 6-10 work schedule.
General contingency factor: 35% - SCE Standard Contingency Policy used for preliminary project estimating based on AACE guidelines, and used in previous regulatory filings.
Owner's Representative Fee for EPC Construction: 10% of the total project cost.
Unit cost guide assumes facilities are constructed under an Engineer, Procurement and Construction (EPC) agreement. All facilities are owned by SCE.
Unit costs include costs to procure materials, installation, engineering, project management costs, home office costs, and contingency.
Unit costs exclude allocated corporate overhead, including P&B, A&G, and AFUDC (these will be added to total cost estimates).
Unit costs exclude generator's responsibility for Income Tax Component of Contribution (ITCC), (these will be added to total cost estimates, if required).
Unit costs exclude environmental monitoring and mitigations.
Unit cost are given w/out the benefit of any preliminary & final engineering. Unforeseen conflicts and/or scope will increase costs. These unit costs do not include: right-of-way & easements requirements, environmental engineering/mitigation, GO 131-D engineering /permitting, other permitting, associated SCE/3rd Party under-build work, etc. A signed Interconnection Agreement is required before final design/engineering can start. Construction will not commence until all of the above conditions have been addressed.
Transmission line cost per mile assumes conventional construction.
Cost per mile of T\L requiring helicopter construction (or deconstruction) will have higher than published per-unit cost, the labor component of helicopter construction is incrementally higher, which is not included in the per-unit cost.
Cost of teardown of existing lines includes temporary bypass line (also referred to as a "shoe-fly") costs.
Towers assumption for single-circuit 220 kV construction:
4.25 towers/mile, 68,785 lbs. of steel/mile for lattice towers strung with 2B-1590kcmil ACSR conductor.
3.8 towers/mile, 56,905 lbs. of steel/mile - for suspension structures.
0.45 towers/mile, 10,880 lbs. of steel/mile - for dead-end structures.

## SubTrans Assumptions & Caveats
2012 Proposed SCE Generator Interconnection Unit Cost Guide
SubTransmission Elements (115 & 66 kV)
Assumptions:
· All Direct Costs
· EPC Basis w/ 6day – 10hr workweek --> 50% overtime
· Division Overhead
· 35% Contingency
· 10% EPC Fee / Owner’s Rep
· 2012 Constant Dollars
Caveats:
· Unit Costs are given without the benefit of final design/engineering
· Unforeseen conflicts and/or scope will increase costs and interconnection schedule
· Assumes a base minimum of 18 months to design/engineer, procure, and construct
· Assumes an additional month per mile of construction added to base schedule of 18 months
· Costs do not consider, and are not limited to following:
o Review of customer/developer existing and proposed plans (i.e. surveyed base map, street/land
improvements, profiles, grading, overhead & underground utilities, temp construction roads &
laydown/staging yards, etc.)
o Property rights study
o Right-of-way improvements/acquisitions (i.e. easements, access/maintenance roads, grading, etc.)
o GO 131-D engineering/permitting per CEQA requirements
o Non-GO 131-D Permitting (i.e. Railroad, City, County, State, Federal Agency, etc.)
o Governing regulation impacts (i.e. CPUC, FERC, OSHA, etc.)
o Environmental study and mitigations
o EMF study and potential reduction mitigations as required by the CPUC
o Geotechnical investigation and mitigations
o Surveys
o Potholing
o Traffic plans/control
o Concrete and/or asphalt repairs
o Associated SCE Substation work (i.e. breaker replacements, switch-rack position relocations, etc.)
o Associated SCE Distribution voltage under-build work (i.e. 16 kV, 12 kV, 4 kV, and secondary
conductors)
o Associated SCE Telecommunication under-build work
o Associated 3rd Party Joint Owners and renters/tenants under-build work (i.e. cable TV,
communication cable, fiber optic, etc.)
o Conflicts associated with other projects in the same geographical area or electrical system
o Availability of line outages required for construction
· SCE will not commence on final design/engineering until an Interconnection Agreement has been signed
· SCE will not consider temporary, non-standard, and/or substandard construction to expedite the
interconnection schedule
· SCE will not commence construction until all required permits, rights-of-way, and environmental
clearances have been secured
· A minimum of 30 foot wide easement will be required for overhead SubTransmission pole lines not located
in the public right-of-way
· Assumes all proposed/new SCE owned switching substation to be adjacent to existing SubTransmission
facilities/lines, for “tap” or “loop-in” options, unless otherwise noted
· The generation tie-line Point of Interconnection (POI) between the Interconnection Customer (IC) and the
Participating Transmission Owner (PTO) is assumed to be at the first structure outside of SCE’s substation,
unless another location outside of SCE’s substation and fee owned right-of-way is pre-determined

## Escalation Rates & Factors
SUPPLEMENT TO SCE 2012 UNIT COST GUIDE
OVERVIEW :
Current SCE Unit Cost Guide as posted on the CAISO website is in 2012 Constant Dollars.
SCE’s cost estimating is done in constant dollars and then escalated over the years during which the
project will be constructed, arriving at project costs in nominal dollars.
Current escalation rates used to arrive at costs in nominal dollars are the rates as filed in SCE’s 2012
CPUC General Rate Case (A.10-11-015), plus SCE projected rates.
DEFINITIONS :
Project Cost in Constant Dollars represents the cost of the Project if all costs were paid for at a single point in time
Project Cost in Nominal Dollars represents the cost of the Project taking into account when actual dollars will be spent.
Mathematical formula: Cost in Nominal Dollars |  |  |  |  | = Cost in Constant Dollars + Escalation
= Cost in Constant Dollars x Escalation Factor
CURRENT SCE ESCALATION RATES *:
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022
Escalation Rates |  | 2.75% | 2.43% | 3.02% | 2.72% | 2.57% | 2.45% | 2.58% | 2.51% | 2.48% | 2.47%
2012 Escalation Factors | 1 | 1.0275 | 1.0525 | 1.0843 | 1.1137 | 1.1424 | 1.1704 | 1.2006 | 1.2307 | 1.2612 | 1.2924
* Note (e.g. Rates for 2011 – 2014 are as filed in SCE's 2012 CPUC General Rate Case (A.10-11-015). Rates for 2015 - 2022 are SCE's projected rates.)

## Other Documentation
Telecommunications: A project’s Electrical Plan of Service (e.g. the electrical one-line contained in AF/IF Substation’s request letter for Qxxx generation interconnection customer) and its other related requirements (e.g. line protection, SPS, and SCADA requirements) are the basis of the Telecommunications Plan of Service. Using the drawing in the Telecommunications Plan of Service as a guide, the project’s relevant Telecom elements are selected from the Unit Cost Guide to arrive at a Total Cost for the Telecom terminal equipment. For example, the Qxxx generation interconnection customer’s Telecom Plan of Service may include Lightwave, Channel, and Common Equipment elements to support Gen-Tie Line Protection, SCADA, and SPS requirements between the Point of Interconnection and the IC’s Generation Facility. Additionally, In Phase 1 of cluster generation interconnection projects, Telecommunications provides a desktop estimate using units costs for fiber optic cable installation. For all Serial and Cluster Phase II generation interconnection projects, and Method of Service customer load projects, Edison Carrier Solution (ECS) surveys all routes in the field to provide the estimate for installing fiber optic cables designated in the Telecommunications Plan of Service.