## Cost Details
All costs are $x1,000
2017 Final SDG&E Generator Interconnection Unit Cost Guide |  |  |  | "Voltages" | 69 kV | 138 kV | 230 kV | 500 kV | Notes/Comments:
Revised as of: 2/3/2017
Equipment Categories |  |  |  | Units |  |  |  |  | (Example PTO specific Note: Unit costs for equipment at lower voltages estimated on as-needed basis, not published on CAISO website)
New Substation Equipment
|  | Complete Loop-in Substation, equipped with one line position to |  |  | 4685 | 8318 | 15150 | 46073 | Three element switchyards
terminate a single gen-tie
New Substation Equipment
|  | Transformer Banks: | [6 empty] | Unit cost of transformer banks
|  |  | 500/230 kV 4-1 Phase | per unit |  |  |  | 47745 | reflects cost of the highest MVA
|  |  | 500/230 kV 3-1 Phase | per unit |  |  |  | 37842 | rated transformer for the given
|  |  | 230/138 kV | per unit |  |  | 10156 |  | voltage
|  |  | 230/69 kV | per unit |  |  | 8052
|  |  | 138/69 kV | per unit |  | 7000
|  |  | (Add additional options) | per unit
|  | Line Positions to terminate gen-ties and Transformer Bank positions | [6 empty] | Position cost estimate includes cost
|  |  | Single Breaker (add third breaker to breaker and a half) | per unit | 596 | 772 | 2338 | 4529 | of any related disconnect switches
|  |  | Breaker and a half (2CB) | per unit | n/a | n/a | 4668 | 9377 | and protection equipment located within
|  |  | Breaker and a half (3CB) | per unit | n/a | n/a | 5046 | 11254 | the position
|  |  | Double Breaker (2CB, double bus) | per unit | 982 | 1677 | 4668 | 9337
|  | Double Operating Bus Sections - 2 new buses, spanning 2 positions |  | per unit | 1122 | 1486 | 1804 | 2732 | Typical configuration for 500 kV, includes "pair" of N/S or E/W buses
|  | Double Operating Bus Sections - 2 new buses, spanning 4 positions |  | per unit | 1968 | 2930 | 4011 | 5092 | Typical configuration for 230 kV, includes "pair" of N/S or E/W buses
|  | Double Operating Bus Sections - 2 bus extensions, spanning 2 positions |  | per unit | n/a | n/a | n/a | n/a | Used in substation expansion
|  | Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  | per unit | n/a | n/a | n/a | n/a | Used in substation expansion
|  | Sectionalizing Breaker |  | per unit
|  | Shunt Capacitors |  | per unit | 925 | 1006 | 2737 | n/a | Includes cost of CB
| Miscellaneous Equipment (see comments) | [7 empty] | These items are rarely required for
|  | Bus Tie (1CB) |  | lump sum |  |  |  |  | high-voltage substations. If required,
|  | Shunt Reactors |  | lump sum |  |  |  |  | would be estimated as a lump sum.
|  | Phase Shifter |  | lump sum
|  | Ground Bank |  | lump sum
|  | Series Capacitors |  | lump sum
|  | Static VAR Compensator (SVC) |  | lump sum
|  | Tertiary Reactors (1 reactor, 1 bay) |  | lump sum
| Gas Insulated Substation (in lieu of open air construction) |  |  | lump sum |  |  |  |  | Not typical, would be estimated as a
Lump sum, if GIS required
Replacement Substation Equipment
|  | Line drops (Tie Downs)- 3 phases |  | per unit |  |  |  |  | Shaded areas are n/a to SDG&E construction
|  | Circuit Breakers (including replacement of foundation) |  | per unit | 265 | 356 | 677 | 2067
|  | Circuit Breakers (without TRV caps) |  | per unit
|  | Transient recovery voltage capacitors (set of 3, separate from CBs) |  | per unit
|  | Disconnect switches (incl. steel structures and foundations) |  | per unit | 175 | 232 | 236 | 658
|  | Line protection relays (other end of line) |  | per set | 601 | 601 | 601 | 601
|  | Bank Protection |  | per unit | 694 | 694 | 694 | 694
|  | Bus Protection |  | per unit | 601 | 601 | 601 | 601
New Protection Equipment
|  | New SPS |  | lump sum
|  | SPS Relays |  | lump sum
|  | Additional set of bushing current transformers (3) at existing CBs |  | lump sum
Information Technology (IT) Equipment
IT interface equipment - Control Rooms
|  |  | Communication rack placed in existing B station MEER bldg | per set
|  |  | Comm. Rack with own environmental enclosure | per set
|  |  | Full Comm. package for AA or A stations | per set
|  |  | Prefab communications building | per unit
|  |  | 48V DC power supply for comm. equipment | per set
|  |  | 100' self-supporting comm. tower (3 legs) | per unit
|  |  | 120' self-supporting comm. tower (4 legs) | per unit
IT interface equipment - miscellaneous equipment
|  |  | Lightwave terminal | per unit
|  |  | Microwave terminal and dish antennas | per set
|  |  | Dehydrator for microwave antennas | per unit
|  |  | Channel bank | per unit
|  |  | Digital Access Cross Connect (DACS) | per unit
|  |  | Network synchronization equipment (BITS clock) | per unit
|  |  | Large router for network access to work bases | per unit
|  |  | Small router for equipment monitoring, "data beyond SCADA" | per unit
|  |  | T1 cross connect | per unit
|  |  | Fiber to Telco connection (high voltage protected) | per unit
IT interface equipment - T/L
|  |  | Fiber optic cable on existing poles | per mile
|  |  | Fiber optic cable on new poles | per mile
New Transmission Line
|  | Single Circuit, Lattice Tower (6 structures per mile) |  | per mile | N/A | N/A | N/A | 5939 | Assumes 2-900 ACSS/AW per phase for 230/500kV plus OHGW and 1-1033.5 ACSR/AW for 69/138kV. 138kV DC is Mix of wood equivalent steel + AB steel poles, SC is H-frame config. 69kV is 16 SW poles (12 structures). Assumes average road grading.
|  | Double Circuit, 6 Tubular Steel Poles w/ Anchor Bolt Foundations |  | per mile | N/A | 5284 | 6558 | N/A
|  | Single Circuit, 6 Tubular Steel Poles w/ Anchor Bolt Foundations |  | per mile | N/A | 4626 | 5260 | N/A
|  | Double Circuit: Mix of wood equivalent steel + AB steel poles |  | lump sum | 3033 | 2727 | N/A | N/A
|  | Single Circuit, wood = steel poles in H-frame configuration |  | lump sum | 2475 | 2304 | N/A | N/A
|  | Wood poles |  | per mile
| Removal of Transmission Line (complete tear down) | [7 empty] | Cost of removal assumes wood poles and one conductor per phase removed. These costs do not include contingency.
|  | Double Circuit |  | per mile | N/A | N/A | N/A
|  | Single Circuit |  | per mile | 200 | 249 | N/A | N/A
Reconductor/Upgrade Transmission Line
|  | Double Circuit, wood equivalent steel poles |  | lump sum | 2705 | 2976 | N/A | N/A | Assumes minor road grading. 230kV assumes only conductor and hardware replaced. Existing structures are adequate and are not replaced. 69/138kV include removals.
|  | Single Circuit, wood equivalent steel poles |  | lump sum | 2148 | 2533 | N/A | N/A
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | lump sum |  |  | 2522
|  | Double Circuit, Strung on one side, Tubular Steel Pole |  | lump sum | N/A | N/A | N/A | N/A
|  | Single Circuit, Tubular Steel Pole |  | lump sum |  |  | 1648
Metering
|  | Upgrade of existing RTUs |  | lump sum
Lump Sum costs, in addition to per-unit or lump-sum costs listed above:
| Engineering costs |  |  | lump sum |  |  |  |  | Costs per mile estimate is $221K to $351K and includes Project management, Env. Monitoring, and construction contract services.
| Capitalized Licensing and Permitting Costs, including |  |  | lump sum |  |  |  |  | N/A
mitigation measures, FAA permits, etc.
| Civil work: Site Preparation including site grading, ground grid, | [7 empty] | Site Development costs are highly variable and will be estimated as a lump sum. For Line Const.: Avg. grading assumed for new const. is $833K and Minor grading is $473K.
| and walls/fencing/containment |  |  | lump sum
| General Facilities: station light & power, backup generator, |  |  | lump sum
station utilities (water, gas, etc. if manned substation)
| Substation Control (MEER) Buildings |  |  | lump sum
| Incremental cost for transmission line crossings (roads, |  |  | lump sum
streams, rail, highway, other T\L)
| Land cost for substations and T/L ROW |  |  | lump sum |  |  |  |  | Land costs are highly variable.
As a result, will be estimated as a lump sum
| Incremental cost of soil/geotechnical mitigation measures |  |  | lump sum |  |  |  |  | Unable to perform detailed geotechnical
analysis of land in Phase I study, but
any known geotech mitigation measures
will be estimated as a lump sum
| Incremental environmental monitoring and mitigations |  |  | lump sum
| Corporate Overheads (A&G, P&B, and AFUDC) | [7 empty] | N/A
Income Tax Component of Contribution (ITCC)

## Factors & Assumptions
SDG&E Draft Unit Cost Guide
Factors for use in developing cost estimates in Phase I Generator Interconnection Studies
As of 2/3/2017
How to apply factors:
[9 empty] | $ millions | Factor | Applied Factor | Delta
| Hypothetical baseline cost per mile for Double Circuit 69 kV line using standard construction: | [7 empty] | 2
Known characteristics of proposed transmission line ROW at Phase I study:
|  | Terrain access: high impact | [6 empty] | 2 | 1.3 | 2.6 | 0.6
|  | Will be constructed in remote east county | [6 empty] | 2 | 1.2 | 2.4 | 0.4
|  | Will be constructed in a high fire risk area | [6 empty] | 2 | 1.5 | 3 | 1
|  | Is in an environmentally sensitive area | [6 empty] | 2 | 1.2 | 2.4 | 0.4
|  |  | Total Delta (summation of applied factor) | [8 empty] | 2.4
|  |  | Original estimated cost per mile | [8 empty] | 2
|  |  | Estimated cost per mile including applied factors ($ million/ mile) | [8 empty] | 4.4
|  | Factor Type: |  |  | Low Impact Areas: |  | Medium Impact areas: |  | High Impact areas:
|  |  | Terrain Access |  | Developed land / existing roads |  | relatively flat terrian with existing roads |  | mountainous with environmental restrictions
|  |  | High Fire Risk Area |  | Coastal |  | Transition Zone |  | SD East / North County
|  |  | Line Length |  |  | Greater than 5 miles |  | 3 to 5 miles |  | Less than 3 miles
|  |  | Remoteness |  |  | SD City / Coastal |  | East County / Inland | Cuyamaca Mts. / IV / Borrego**
|  |  | Environmental Sensitivity |  | previously disturbed / maintained |  | Existing easement / new disturbance |  | Wetlands, BLM, CNF, new ROW undisturbed
|  | Factor Amounts: |  |  | Low Impact factors: |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain Access |  | 1 |  | 1.2 |  | 1.3
|  |  | High Fire Risk Area |  | 1 | 1 | 1.2 | 1 | 1.5 | 1.2
|  |  | Line Length |  | 0.8 | 0.8 | 1 | 1 | 1.1 | 1.1
|  |  | Remoteness |  | 1 | 1 | 1.1 | 1.05 | Line 1.2** (Substation 1.25) | 1.1
|  |  | Environmental Sensitivity |  | 1 | 1 | 1.1 | 1.1 | 1.2 | 1.2
|  |  | Factor Type | Explanation of Factor issues and Factor multipliers
|  |  | High Fire Risk Area | Refer to CALFIRE FRAP fire threat area map. No wood construction, only wood equivalent steel or engineered structures. Steel structures designed using extreme wind criteria.
|  |  | Line Length | Higher cost for lines less than 3 miles long. Factor in Economy of scale for lines longer than 5 miles
|  |  | Remoteness | Includes travel time for crews and material suppliers
|  |  | Environmental Sensitivity | This includes the use of Helicopters for construction and regulatory impacts to licensing by agencies such as BLM, CNF and CPUC that impact schedule and cost
Assumptions in the unit cost guide
All labor is straight time and based on a 5 day work week schedule.
General contingency factor: 35%. Estimates include a mandatory 4% for estimate for EMF field management plan implementation.
Transmission line design in high wind areas is based on NESC 250C design criteria. This typically results in a significant cost increase as the design goes from wood equivalent steel to engineered steel poles with foundations. Foundations assume a mix of micro-pile and pier type.
** For Substation construction costs in remote areas a factor multiplier should be applied for labor and labor overheads. Apply a Factor amount of 1.25 to the total cost of the Substation work. Site Purchase, site Development or grading costs are not included in Substation costs.
Unit cost guide assumes facilities are constructed by Union crews under the direction of SDG&E.
In addition to material and construction costs the unit costs include exemplary costs for engineering, project management, construction management, contracted surveying, internal Land Services support, environmental monitoring, and labor overhead costs.
Unit costs exclude environmental licensing, all permitting ( ie; Environmental, GO 131-D, CPUC, FERC BLM, CNF) and costs for land mitigation.
Unit costs exclude AFUDC.
Unit costs exclude generator's responsibility for Income Tax Component of Contribution (ITCC), (will be added to total cost estimates, if required)
Transmission line cost per mile assumes conventional construction.
Cost per mile of T\L requiring helicopter construction (or deconstruction) will have higher than published per-unit cost, the labor component of helicopter construction is incrementally higher, which is not included in the per-unit cost
Typically SDG&E will perform project specific costs estimates for PTO Interconnections, Reliability and Delivery Network upgrades instead of using the per-unit costs. These costs are provided for the IC to use in their selection of alternative sites or methods of interconnection.

## Escalation Rates & Factors
SUPPLEMENT TO THE SDG&E PTO 2017 UNIT COST GUIDE
OVERVIEW :
Current PTO Unit Cost Guide as posted on the CAISO website is in 2017 Constant Dollars.
PTO’s cost estimating is done in constant dollars and then escalated over the years during which the
project will be constructed, arriving at project costs in nominal dollars.
DEFINITIONS USED :
Project Cost in Constant Dollars represents the cost of the Project if all costs were paid for at a single point
in time.
Project Cost in Nominal Dollars represents the cost of the Project taking into account when actual dollars will be spent.
Mathematical formula: Cost in Nominal Dollars |  |  |  |  | = Cost in Constant Dollars + Escalation
= Cost in Constant Dollars x Escalation Factor
CURRENT PTO ESCALATION RATES *: Revised 2/3/2017
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Escalation Rates |  | 2.159% | 2.189% | 2.39% | 2.369% | 2.394% | 2.473% | 2.463% | 2.332% | 2.39% | 2.076%
2016 Escalation Factors | 1 | 1.0216 | 1.044 | 1.0689 | 1.0942 | 1.1204 | 1.1482 | 1.1764 | 1.2039 | 1.2326 | 1.2582
* Escalation Rates are from IHS Global Insight's 4th Quarter 2016 Power Planner (released Jan.2017) electric utility construction cost forecast for "Total Transmission Plant, Pacific Region--JUEPT@PCF".