## Cost Details
All costs are $x1,000
2021 Proposed DesertLink Generator Interconnection Unit Cost Guide |  |  |  | "Voltages" |  | 138 kV | 500 kV | Notes/Comments: DesertLink does not currently have 138 kV nor 230 kV facilities on their system. These connections will be estimated on an as-needed basis.
Revised as of: January 2021
Equipment Categories |  |  |  | Units |  |  | All Costs are $x1000
New Substation Equipment
|  | Complete 3-CB ring bus Substation, equipped with one line position to |  |  |  |  | 20000 | Cost includes all site prep and protection and control equipment. Land cost and permitting are not included and will be estimated on a case by case basis.
terminate a single gen-tie with as many as (2) outgoing lines.
New Substation Equipment
Transformer Banks:
|  |  | 500/230 kV 1-3 phase | per unit |  |  | 12000 | Assumes 600MVA XFMR.
|  |  | 500/230 kV 4-1 phase | per unit |  |  | 15000 | Assumes 600MVA XFMR.
Line Positions to terminate gen-ties and Transformer Bank positions
|  |  | Single Breaker (add third breaker to breaker and a half) | per unit |  |  | 5000 | Assumes 4000A Rating
|  |  | Breaker and a half (2CB) | per unit |  | N/A | 8500
|  |  | Breaker and a half (3CB) | per unit |  |  | 12000
|  | Sectionalizing Breaker |  | lump sum |  | lump sum | N/A
|  | Shunt Capacitors |  | lump sum |  | lump sum | 1500 | Assumes 100MVAR 3-Phase. Cost does not include any Circuit Breaker positions
Miscellaneous Equipment (see comments)
|  | Bus Tie (1CB) |  | lump sum |  | lump sum | Lump Sum | Shunt Reactor assumes 100MVAR 3-Phase. Cost does not include any Circuit Breaker positions. Other devices vary greatly depending on size and location. If required estimate would be provided lump-sum.
|  | Shunt Reactors |  | lump sum |  | lump sum | 4500
|  | Phase Shifter |  | lump sum |  | lump sum | Lump Sum
|  | Ground Bank |  | lump sum |  | lump sum | Lump Sum
|  | Series Capacitors |  | lump sum |  | lump sum | Lump Sum
|  | Static VAR Compensator (SVC) |  | lump sum |  | lump sum | Lump Sum
|  | Tertiary Reactors (1 reactor, 1 bay) |  | lump sum |  | lump sum | Lump Sum
| Gas Insulated Substation (in lieu of open air construction) |  |  | lump sum |  | lump sum | N/A
Replacement Substation Equipment
|  | Circuit Breakers |  | per unit |  |  | 2500 | Assumes in-kind equipment replacement. 4000A Rating
|  | Disconnect switches (incl. steel structures and foundations) |  | per unit |  |  | 750
|  | Line protection relays (other end of line) |  | per set |  |  | 500
|  | Wave Trap - 1 phase only |  | per unit |  |  | 100
New Protection Equipment
|  | New SPS |  | lump sum |  | lump sum | Lump Sum | Costs will very widely - estimates will be provided as lump sum as needed.
|  | SPS Relays |  | lump sum |  | lump sum | Lump Sum
|  | Additional set of bushing current transformers (3) at existing CBs |  | lump sum |  | lump sum | Lump Sum
Information Technology (IT) Equipment
IT interface equipment - Control Rooms
|  |  | Communication rack placed in existing B station MEER bldg |  | per set | Lump Sum | Lump Sum | This equipment is included in lump sum substation cost above. Individual equipment costs will be estimated on an as needed basis.
|  |  | Comm. Rack with own environmental enclosure |  | per set | Lump Sum | Lump Sum
|  |  | Full Comm. package for AA or A stations |  | per set | Lump Sum | Lump Sum
|  |  | Prefab communications building |  | per unit | Lump Sum | Lump Sum
|  |  | 48V DC power supply for comm. equipment |  | per set | Lump Sum | Lump Sum
|  |  | 100' self-supporting comm. tower (3 legs) |  | per unit | Lump Sum | Lump Sum
|  |  | 120' self-supporting comm. tower (4 legs) |  | per unit | Lump Sum | Lump Sum
IT interface equipment - miscellaneous equipment
|  |  | Lightwave terminal |  | per unit | Lump Sum | Lump Sum
|  |  | Microwave terminal and dish antennas |  | per set | Lump Sum | Lump Sum
|  |  | Dehydrator for microwave antennas |  | per unit | Lump Sum | Lump Sum
|  |  | Channel bank |  | per unit | Lump Sum | Lump Sum
|  |  | Digital Access Cross Connect (DACS) |  | per unit | Lump Sum | Lump Sum
|  |  | Network synchronization equipment (BITS clock) |  | per unit | Lump Sum | Lump Sum
|  |  | Large router for network access to work bases |  | per unit | Lump Sum | Lump Sum
|  |  | Small router for equipment monitoring, "data beyond SCADA" |  | per unit | Lump Sum | Lump Sum
|  |  | T1 cross connect |  | per unit | Lump Sum | Lump Sum
|  |  | Fiber to Telco connection (high voltage protected) |  | per unit | Lump Sum | Lump Sum
|  |  | Satellite Terminal for "RTU only" locations |  | per unit |  | Lump Sum
FO cost is included in New T/L below
IT interface equipment - T/L
|  |  | Fiber optic cable on existing poles |  | per mile |  | 300
|  |  | Fiber optic cable on new poles |  | per mile |  | Lump Sum
New HV Transmission Line
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | per mile |  |  | 5000 | Assumes no environmental, permitting or ROW acquisition.
|  | Double Circuit Capable, Strung on one side, Tubular Steel Pole |  | per mile |  |  | 3250
|  | Single Circuit, Tubular Steel Pole |  | per mile |  |  | 2750
|  | Double Circuit, Strung on both sides, Lattice Tower |  | per mile |  |  | 5250
|  | Double Circuit Capable, Strung on one side, Lattice Tower |  | per mile |  |  | 3500
|  | Single Circuit, Lattice Tower |  | per mile |  |  | 3000
Removal of HV Transmission Line (complete tear down)
|  | Double Circuit |  | per mile |  |  | N/A
|  | Single Circuit |  | per mile |  |  | N/A
| Reconductor/Upgrade Transmission Line | [7 empty] | Total
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | per mile |  |  | N/A | Assumes no structure upgrades are required. Assumes removal of existing conductor and installation of new conductor.
|  | Single Circuit, Tubular Steel Pole |  | per mile |  |  | 1000
|  | Double Circuit, Strung on both sides, Lattice Tower |  |  |  |  | N/A
|  | Single Circuit, Lattice Tower |  |  |  |  | 1000
Metering
|  | Upgrade of existing RTUs |  | lump sum |  | lump sum | N/A
Lump Sum costs below are in addition to per-unit or lump-sum costs listed above:
| Engineering costs |  |  | lump sum |  | lump sum | Lump Sum | Lump sum line and substation costs above include engineering, general facilities, control buildings, overheads, and taxes. Land Costs and Permitting will very widely - estimates will be provided as lump sum. Additional costs will be estimated on an as needed basis.
| Capitalized Licensing and Permitting Costs, including |  |  | lump sum |  | lump sum | Lump Sum
mitigation measures, FAA permits, etc.
| Civil work: Site Preparation including site grading, ground grid, |  |  | lump sum |  | lump sum | Lump Sum
and walls/fencing/containment
| General Facilities: station light & power, backup generator, |  |  | lump sum |  | lump sum | Lump Sum
station utilities (water, gas, etc. if manned substation)
| Substation Control (MEER) Buildings |  |  | lump sum |  | lump sum | Lump Sum
| Incremental cost for transmission line crossings (roads, |  |  | lump sum |  | lump sum | Lump Sum
streams, rail, highway, other T\L)
| Land cost for substations and T/L ROW |  |  | lump sum |  | lump sum | Lump Sum
| Incremental cost of soil/geotechnical mitigation measures |  |  | lump sum |  | lump sum | Lump Sum
| Incremental environmental monitoring and mitigations |  |  | lump sum |  | lump sum | Lump Sum
| Corporate Overheads (A&G, P&B, and AFUDC) |  |  | lump sum |  | lump sum | Lump Sum
| Income Tax Component of Contribution (ITCC) |  |  | lump sum |  | lump sum | Lump Sum

## BulkTrans Factors & Assumptions
Bulk Transmission (230 kV) Factors for use in developing cost estimates in Phase I Generator Interconnection Studies
As of January 2020
Simplified example on how to apply factors:
[10 empty] | $ millions | Apply Factor | Delta
| Hypothetical baseline cost per mile for Double Circuit 220 kV line (strung one side) using Lattice Towers: | [8 empty] | 2
Known characteristics of proposed transmission line ROW at Phase I study:
|  | Will be constructed in mountainous terrain | [7 empty] | 2 | 2.0 x 2.0 =4 | 2
No population density issues
|  | High wind-prone area (but not icy) | [7 empty] | 1.35 | 2.0 x 1.35 =2.7 | 0.7
|  |  | Total Delta (summation of applied factor) | [8 empty] | 2.7
|  |  | Estimated cost per mile | [8 empty] | 2
|  |  | Estimated cost per mile including applied factors ($ million/ mile) | [8 empty] | 4.7
|  | Factor Types: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | flat |  |  | hilly |  | mountain |  | forest
|  |  | Population density |  | rural |  | desert | suburban |  | urban/metro
|  |  | Weather study (increase in |  | 1/2" ice, or 20# wind |  |  | 1" ice, 6# wind |  | > 2" ice, 6# wind
structural steel amount and foundation volume)
|  | Factor Amounts: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  | 2.0X to 3.0X
|  |  | Population density |  |  | 1.00X to 1.10X |  |  | 1.33X |  | 1.67X
|  |  | Weather study |  |  | 1.35X |  |  | 1.45X |  | 1.60X
|  |  | Factor Type | Explanation of Factor issues and Factor multipliers
|  |  | Terrain | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
|  |  | Population density | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
|  |  | Weather study | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure types or an increased number of structures to reduce the span lengths.
Other assumptions underlying unit cost guide:
Assumption
N/A

## Escalation Rates & Factors
ESCALATION OVERVIEW :
DSL cost estimating is done in 2021 constant dollars and then escalated over the years during which the project will be
constructed, arriving at project costs in 2021 Constant Dollars Escalated to OD Year.
DEFINITIONS :
Project Cost in 2021 Constant Dollars represents the cost of the Project if all costs were paid for in 2021.
Project Cost Escalated to OD Year represents the cost of the Project if all costs were paid for in the OD Year.
Mathematical formula: Constant Dollars Escalated to OD Year | [5 empty] | = Cost in Constant Dollars + Escalation to OD Year
= Cost in Constant Dollars x Escalation Factor
Proposed Escalation Rate - Effective 1/1/2021
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Escalation Rate | 1.7% | 1.8% | 2.2% | 2.2% | 2.1% | 2% | 2% | 2% | 2% | 1.8% | 1.933%
Escalation Factors | 1 | 1.018 | 1.0404 | 1.0633 | 1.0856 | 1.1073 | 1.1295 | 1.1521 | 1.1751 | 1.1963 | 1.2194
2021-2030 | Escalation Rates are from IHS Global Insight's 3rd Quarter 2020 Power Planner (released November 2020) electric utility construction cost forecast for "Total Transmission Plant, Pacific Region--JUEPT@PCF".
2031 | 3 Year average escalation rate (2028-2030)