## Overview
Variable Operations and Maintenance Cost Review
Draft Final Proposal
Supporting Calculations
This set of supporting calculations supplements the discussion of the proposed calculation methodology for default maintenance adders. This appendix is intended to aid in understanding some of the more complicated aspects of the calculation. As a reminder, the steps to calculate the default maintenance adder are: 1) Estimate variable maintenance costs using external sources 2) Determine which adder type ($/run-hour, $/start, or $/MWh adder) is most appropriate for each technology type 3) Convert the variable maintenance costs to the appropriate adder type 4) Cross-validate the estimate from external sources against median major maintenance adder values to determine a default O&M Adder value 5) Using the default O&M Adder value, calculate a resource-specific O&M Adder Step 5 will be performed on a resource-by-resource (or, for MSGs, on a configuration-by-configuration) basis and is thus not included in this workbook. See Appendix B of the paper for examples of how Step 5 is performed.
CAISO PUBLIC

## Step 1 - Gather Data
Step 1: Estimate variable maintenance costs using external sources
See the subsequent tabs for data gathered from external sources

## 1a. NYISO
Source: NYISO 2010, NYISO 2016
The calculations below are performed from left to right, with final values highlighted in bold
Note 1: The CAISO utilized the NYISO 2010 report for the estimates of aeroderivative CTs and the 2016 NYISO report for estimates of CTs and CCGTs
Note 2: The NYISO expresses maintenance costs in both: 1) $/start or $/run-hour and 2) $/MWh values. These represent the same maintenance costs and thus only the $/start and $/run-hour values are used to arrive at an estimate of total variable maintenance costs.
Note 3: The CAISO scales labor costs based on the relative wages in NY versus the states in the CAISO/EIM operating area. To convert these values, the CAISO used BLS wage data from May 2019, for OCC_Code 49-2095: Electrical and Electronics Repairers, Powerhouse, Substation, and Relay. The labor scaling factor is a ratio of the weighted average of the wages in states representing the CAISO/EIM operating area and the wages in NY. https://www.bls.gov/oes/current/oes_nat.htm
Note 4: The CAISO scales the maintenance cost estimates from the $-year used in the source documents to $2019. The NYISO 2016 report was presented in 2015 dollars. See Inflation Rates tab.
Note 5: See the Technology Grouping section of paper for discussion of which technologies were used for the estimates below.
Option 1
[5 empty] | ¦--------- Major maintenance costs expressed in $/starts or $/run-hours, converted to $/cycle---------¦ | [5 empty] | ¦--------------------- Major maintenance costs expressed in $/MWh, converted to $/cycle---------------------¦
|  | A | B | C | D | E | F | G = E * F | H = D + G | I = H * Inf Rate | J | K | L | M = K * L | N = J + M | O = N * Inf Rate | P = B * C * O | Q = I + Q | R = Q / C
Source: 2016 Report | Note 5 | Page 47 | Page 47 | Page 52 | Page 47 | Pages 133, 136 | Note 3 |  |  | Note 4 | Page 136 | Page 136 | Note 3 |  |  | Note 4
Source: 2010 Report | Note 5 |  | Page 31 | Page 90 | Page 32 | Pages 32, 29 | Note 3 |  |  | Note 4 | Page 32 |  | Note 3 |  |  | Note 4
[5 empty] | $/cycle | $/cycle |  | $/cycle | $/cycle | $/cycle | $/MWh | $/MWh | $/MWh | $/MWh | $/MWh | $/MWh
Tech type | Model | Starts per Cycle | Run-hours per Cycle | Average Degraded Net Plant Capacity ICAP | Cost of Parts | Cost of Labor | Labor Scaling Factor | Geo-scaled Costs of Labor | Costs per Cycle | Time-scaled Costs per Cycle | Cost of Parts | Cost of Labor | Labor Scaling Factor | Geo-Scaled Costs of Labor | Costs per MWh | Time-scaled Costs per Cycle | Time-scaled Costs per Cycle | Total Costs per Cycle | $/cycle per MW
Combined Cycle Gas Turbines | 1x1x1 5000F 5 | 2400 | 48000 | 327.25 | 22100000 | 2880000 | 1.1035 | 3178027.4757 | 25278027.4757 | 27281719.4359 | [7 empty] | 27281719.4359 | 83366.5987
Combustion Turbines | 1x0 Siemens 5000F5 | 2400 | 48000 | 217.6667 | 22100000 | 2840000 | 1.1035 | 3133888.2052 | 25233888.2052 | 27234081.4153 | [7 empty] | 27234081.4153 | 125118.2913
Aeroderivative | LM6000 |  | 50000 | 88.28 | 14870000 | 1452000 | 1.1035 | 1602255.519 | 16472255.519 | 19324111.6126 | [7 empty] | 19324111.6126 | 218895.6911

## 1b. EPA 2016
Source: EPA 2016
The calculations below are performed from left to right, with final values highlighted in bold
Note 1: The CAISO utilized an estimated capacity factor based on EPA estimates of capacity factors for areas within the CAISO/EIM operating area. The CAISO also corroborated the capacity factor by comparing the value to the capacity factors using CAISO/EIM operating data (see tab 1c) noting that they were very similar. The CAISO also notes that page 6 of the USDOE Hydropower Market Report states that the median capacity factor of hydro units in the United States was 38.1% from 2005-2016. As this is similar to the 33% used below, the CAISO believes the 33% is appropriate for use in our calculations.
Note 2: The CAISO scales the maintenance cost estimates from the $-year used in the source documents to $2019. See Inflation Rates tab.
Note 3: The CAISO used an average capacity across the 3,818 resources presented in the EPA report.
Source: | Page 4-3 | Note 1 | Page 4-12 | Note 2
| A | B | C | D = C * Inf Rate | E = A * B * C * 8760 | F = E / A
| Annual Capacity (Note 3) | Capacity Factor | Variable O&M | Variable O&M | Convert to $/yr | ($/year)/MW
| MW |  | (2016$/MWh) | (2020$/MWh)
Hydro | 20.7504 | 33.38% | 2.66 | 2.8462 | 172670.091 | 8321.2926
Capacity factors derived from EIA form 923 data for 2007-2016 period
Region | Annual CF
WEC_BANC | 23%
WEC_CALN | 31%
WEC_LADW | 16%
WEC_SDGE | 37%
WECC_AZ | 29%
WECC_CO | 30%
WECC_ID | 38%
WECC_IID | 45%
WECC_MT | 43%
WECC_NM | 27%
WECC_NNV | 49%
WECC_PNW | 43%
WECC_SCE | 32%
WECC_SNV | 24%
WECC_UT | 33%
WECC_WY | 34%
WECC_average | 33.38% | B

## 1c. EIA 2020
Source: EIA 2020
The calculations below are performed from left to right, with final values highlighted in bold
Note 1: The EIA report did not have the capacity factors that were used to estimate the VOM values. In order to convert the values to $/year units, the CAISO estimates capacity factors using CAISO/EIM operating data for these technologies. The CAISO corroborated this capacity factor by comparing the value to the capacity factors estimated using the EPA report (see tab 1b) noting that they were very similar. The CAISO also notes that page 6 of the USDOE 2017 Hydropower Market Report (USDOE 2018) states that the median capacity factor of hydro units in the United States was 38.1% from 2005-2016. As this is similar to the 33% used below, the CAISO believes the 33% is appropriate for use in our calculations.
Source: | Page 2 | Note 2 | Page 2
| A | B | C | D = A * B * C * 8760 | E = D / A
| Nominal Capacity | Capacity Factor | Variable O&M | Convert to $/yr | ($/year)/MW
| MW |  | (2019$/MWh)
Hydro | 100 | 33.03% | 1.39 | 402138.0732 | 4021.3807

## Step 2 - Determine Adder Type
Step 2: Determine which adder type ($/run-hour, $/start, or $/MWh adder) is most appropriate for each technology type
Once the external estimates have been converted to consistent units, the CAISO needs to determine which adder type is most appropriate as a default value for each technology type. The rationale for the CAISO's determination of the default adder type by technology is laid out further in the main paper.
Default Adder Type
Combined Cycle Gas Turbines | $/run-hour
Combustion Turbines | $/start
Aeroderivative | $/run-hour
Hydro | $/run-hour

## Step 3 - Convert Ext. Estimates
Step 3: Convert the variable maintenance costs to the appropriate adder type
In this step, the CAISO converts the Variable Maintenance costs from the source documentation to $/start per MW or $/run-hour per MW Variable Maintenance cost values.
Tab 1a
NYISO
VM Costs |  | ($/cycle)/MW
Combined Cycle Gas Turbines |  | 83366.5987
Combustion Turbines |  | 125118.2913
Aeroderivative |  | 218895.6911
Conversion Factor |  | Starts per cycle | RH per cycle
Combined Cycle Gas Turbines |  |  | 48000
Combustion Turbines |  | 2400
Aeroderivative |  |  | 50000
VM Costs |  | ($/start)/MW | ($/RH)/MW
Combined Cycle Gas Turbines |  |  | 1.7368 | See Step 4
Combustion Turbines |  | 52.1326 |  | See Step 4
Aeroderivative |  |  | 4.3779 | See Step 4
|  | Tab 1b | Tab 1c
|  | EPA 2016 | EIA 2020
VM Costs |  | ($/year)/MW | ($/year)/MW
Hydro |  | 8321.2926 | 4021.3807
Conversion Factor |  | RH per Year | RH per Year
| Operating Data from | All CAISO/EIM | All CAISO/EIM
Hydro |  | 5506.9935 | 5506.9935
VM Costs by Source |  | ($/RH)/MW | ($/RH)/MW
Hydro |  | 1.511 | 0.73023
Average VM Costs |  | ($/RH)/MW
Hydro |  | 1.1206 | See Step 4

## Step 4 Cross-validate
Step 4: Cross-validate the estimate from external sources against interpolated major maintenance adder values to determine a default O&M Adder
In this step, the CAISO cross-validates the external estimates from Step 3 against interpolated MMA values. The CAISO only discloses the interpolated MMA values when they are lower than the external estimate values. The values in the black boxes are the default O&M adder values proposed.
Note 1: the CAISO uses the median MMA values by technology type to cap the external estimates, thus ensuring the proposal of conservative adder values.
Note 2: in cases where the external estimate was more conservative (i.e. lower than) the median MMA values, the external estimate was used and the median MMA values were excluded for confidentiality purposes.
|  | Note 1 |  | Note 1
| ($/MW)/Start | ($/MW)/Start | ($/MW)/RH | ($/MW)/RH
| External Estimate VM Costs | Median MMA Values | External Estimate VM Costs | Median MMA Values
Technology Types | From Step 3 |  | From Step 3
Combined Cycle Gas Turbines |  |  | 1.7368 | Note 2
Combustion Turbines | 52.1326 | Note 2 | #REF!
Aeroderivative |  |  | 4.3779 | Note 2
Hydro |  |  | 1.1206 | 0.65

## Inflation Rates
Appendix A- Inflation Rates
For the purposes of the default maintenance adder calculation, the CAISO uses the Consumer Price Index from the BLS to inflate the values from the source documentation to 2019 dollars. See the paper for more details.
Base Year | Inflation Factor to 2019
2010 | 1.1731
2015 | 1.0793
2016 | 1.07
2017 | 1.0436
2018 | 1.0218