## summary
K:K |  | 2020 CP | 2020 CAISO+PAC | 2020 Regional | 2030 1 | 2030 1B | 2030 2 | 2030 3 | 2030 1 CPP | 2030 3 CPP | 2030 1 Regional | 2030 3 No Addl Renew | 2020 CP | 2020 CAISO+PAC | 2020 Regional | 2030 1 | 2030 1B | 2030 2 | 2030 3 | 2030 1 CPP | 2030 3 CPP | 2030 1 Regional | 2030 3 No Addl Renew | 2020 CP | 2020 CAISO+PAC | 2020 Regional | 2030 1 | 2030 1B | 2030 2 | 2030 3 | 2030 1 CPP | 2030 3 CPP | 2030 1 Regional | 2030 3 No Addl Renew
|  | Q:Q | [10 empty] | L:L | [10 empty] | M:M
Summary of Binding Constraints Across Cases
|  | Path Revenue (2014 $000) | [10 empty] | Path Minimum Rating (MW) if Binding | [10 empty] | Path Maximum Rating (MW) if Binding
|  | 2020 CP | 2020 CAISO+PAC | 2020 Regional | 2030 1 | 2030 1B | 2030 2 | 2030 3 | 2030 1 CPP | 2030 3 CPP | 2030 1 Regional | 2030 3 No Addl Renew | 2020 CP | 2020 CAISO+PAC | 2020 Regional | 2030 1 | 2030 1B | 2030 2 | 2030 3 | 2030 1 CPP | 2030 3 CPP | 2030 1 Regional | 2030 3 No Addl Renew | 2020 CP | 2020 CAISO+PAC | 2020 Regional | 2030 1 | 2030 1B | 2030 2 | 2030 3 | 2030 1 CPP | 2030 3 CPP | 2030 1 Regional | 2030 3 No Addl Renew | Note
| 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | 0 | 0 | 0 | 4.9572 | 77.4692 | 3.9505 | 0 | 4.8863 | 10.0495 | 0 | 2.9551 | n/a | n/a | n/a | -351 | -351 | -351 | n/a | -351 | -351 | n/a | -351 | n/a | n/a | n/a | 351 | 351 | 351 | n/a | 351 | 351 | n/a | 351
| 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | 0 | 0 | 0 | 1.705 | 2.6539 | 11.7283 | 6.8727 | 1.9279 | 21.9919 | 25.6917 | 13.4245 | n/a | n/a | n/a | -796 | -796 | -796 | -796 | -796 | -796 | -796 | -796 | n/a | n/a | n/a | 796 | 796 | 796 | 796 | 796 | 796 | 796 | 796
| 2136-cont 0 | 17.0026 | 21.086 | 276.2884 | 25.3733 | 102.914 | 271.1494 | 280.4857 | 46.3678 | 365.3123 | 180.4699 | 295.3423 | -796 | -796 | -796 | -796 | -796 | -796 | -796 | -796 | -796 | -796 | -796 | 796 | 796 | 796 | 796 | 796 | 796 | 796 | 796 | 796 | 796 | 796
| 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | 0.05258 | 0.037045 | 0.01673 | 0 | 0 | 111.4696 | 0 | 0 | 83.0489 | 418.4555 | 12.8259 | -1195 | -1195 | -1195 | n/a | n/a | -1195 | n/a | n/a | -1195 | -1195 | -1195 | 1195 | 1195 | 1195 | n/a | n/a | 1195 | n/a | n/a | 1195 | 1195 | 1195
| 2422-N-2 SCE Serrano-Lewis #1 and Serrano-Villa PK #2 230 kV | 0 | 0 | 16.6191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | n/a | -1518 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 1518 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| 3105-CA500kV C1 L-1 LosBanos-Midway | 0 | 0 | 0 | 298.1084 | 11609.3847 | 25291.8452 | 1193.154 | 342.7697 | 4999.5185 | 334.134 | 1355.3489 | n/a | n/a | n/a | -3464 | -3464 | -3464 | -3464 | -3464 | -3464 | -3464 | -3464 | n/a | n/a | n/a | 3464 | 3464 | 3464 | 3464 | 3464 | 3464 | 3464 | 3464
| 3111-cont 0 | 0 | 0 | 0 | 3097.166 | 29932.9664 | 43496.1632 | 23723.9968 | 3027.4989 | 22253.8614 | 4990.9445 | 18292.4103 | n/a | n/a | n/a | -1503 | -1503 | -1503 | -1503 | -1503 | -1503 | -1503 | -1503 | n/a | n/a | n/a | 1503 | 1503 | 1503 | 1503 | 1503 | 1503 | 1503 | 1503
| 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | 0 | 0 | 0 | 20.3038 | 76.3734 | 137.2449 | 65.0175 | 35.1678 | 83.1698 | 74.6466 | 45.5497 | n/a | n/a | n/a | -1139 | -1139 | -1139 | -1139 | -1139 | -1139 | -1139 | -1139 | n/a | n/a | n/a | 1139 | 1139 | 1139 | 1139 | 1139 | 1139 | 1139 | 1139
| 34576-cont 0 | 0 | 0 | 0 | 16.5326 | 270.9897 | 445.3877 | 353.7381 | 66.3547 | 521.7577 | 99.4768 | 353.9363 | n/a | n/a | n/a | -1139 | -1139 | -1139 | -1139 | -1139 | -1139 | -1139 | -1139 | n/a | n/a | n/a | 1139 | 1139 | 1139 | 1139 | 1139 | 1139 | 1139 | 1139
| 4915-PG&E LCR Fresno Wilson Cat B | 0 | 0 | 0 | 27.9409 | 0 | 0 | 20.6198 | 19.8118 | 20.0711 | 27.6946 | 14.185 | n/a | n/a | n/a | -119.5 | n/a | n/a | -119.5 | -119.5 | -119.5 | -119.5 | -119.5 | n/a | n/a | n/a | 119.5 | n/a | n/a | 119.5 | 119.5 | 119.5 | 119.5 | 119.5
| BPA_PreferredRate | 59075.749 | 54939.5308 | 64616.2593 | 78212.6028 | 78867.2894 | 77337.263 | 68777.7487 | 39891.065 | 35447.823 | 92372.6615 | 88265.4472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
| CA Path26 N2S with RAS | 469.4243 | 234.1618 | 9802.5816 | 20.869 | 648.9933 | 7.1518 | 24.2224 | 25.3299 | 13.3688 | 58.5569 | 31.019 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450 | 3450
| CAISO Zero Net Export | 28.2637 | 428.0522 | 60.2533 | 70617.3578 | 1312.6845 | 169988.3181 | 27998.9477 | 72146.9092 | 32383.7061 | 209382.1782 | 38070.0827 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | 0.01 | 776 | 0.01 | 2000 | 8000 | 8000 | 8000 | 2000 | 8000 | 8000 | 8000 | CAISO physical export constraint
| CAISO_Plus_Renewables_Limit | 0 | 0 | 0 | 281395.498 | 335445.44 | 0 | 0 | 298571.636 | 0 | 0 | 0 | n/a | n/a | n/a | -99999 | -99999 | n/a | n/a | -99999 | n/a | n/a | n/a | n/a | n/a | n/a | 2000 | 8000 | n/a | n/a | 2000 | n/a | n/a | n/a | CAISO constraint on bilateral sales
| COI 1 | 54.1852 | 17.5635 | 36.7704 | 49.6675 | 15.8322 | 104.2043 | 139.8183 | 55.3011 | 141.8066 | 47.7468 | 78.3223 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | 6763 | 6763 | 6763 | 6763 | 6763 | 6763 | 6763 | 6763 | 6763 | 6763 | 6763
| COI 2 | 5.6909 | 1.213 | 88.4914 | 119.1528 | 54.7063 | 816.2674 | 2635.5523 | 38.3542 | 2028.2652 | 373.7741 | 441.5722 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560 | 4560
| FreqResponse-1 | 0 | 0 | 0 | 589.38 | 403.26 | 0 | 0 | 217.14 | 0 | 0 | 0 | n/a | n/a | n/a | -99999 | -99999 | n/a | n/a | -99999 | n/a | n/a | n/a | n/a | n/a | n/a | 0 | 0 | n/a | n/a | 0 | n/a | n/a | n/a
| FreqResponse-128 | 0 | 0 | 0 | 70.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | n/a | n/a | -99999 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0 | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| FreqResponse-129 | 0 | 0 | 0 | 70.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | n/a | n/a | -99999 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0 | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| FreqResponse-157 | 0 | 0 | 0 | 0 | 380.25 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | n/a | n/a | n/a | -99999 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0 | n/a | n/a | n/a | n/a | n/a | n/a
| FreqResponse-197 | 0 | 0 | 0 | 491.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n/a | n/a | n/a | -99999 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0 | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| FreqResponse-25 | 0 | 0 | 0 | 2552.55 | 1113.84 | 0 | 0 | 556.92 | 0 | 0 | 0 | n/a | n/a | n/a | -99999 | -99999 | n/a | n/a | -99999 | n/a | n/a | n/a | n/a | n/a | n/a | 0 | 0 | n/a | n/a | 0 | n/a | n/a | n/a
| FreqResponse-3506 | 0 | 0 | 0 | 39954.48 | 35699.4 | 0 | 0 | 34984.65 | 0 | 0 | 0 | n/a | n/a | n/a | -99999 | -99999 | n/a | n/a | -99999 | n/a | n/a | n/a | n/a | n/a | n/a | 0 | 0 | n/a | n/a | 0 | n/a | n/a | n/a
| IPP DC | 1082.8751 | 641.2201 | 8143.4458 | 28.8175 | 200.0756 | 353.463 | 333.5203 | 26.2862 | 332.3056 | 328.4075 | 255.9046 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361
| LDWP 25% LocalMinGen | 24004.1093 | 19411.2447 | 123291.7313 | 178774.1947 | 211179.8889 | 102235.0816 | 199395.4518 | 73812.4159 | 199647.394 | 87751.1966 | 83563.0629 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | -99999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999 | 999999
| P01 Alberta-British Columbia | 248095.5208 | 162343.6154 | 312422.636 | 24052.809 | 57003.2308 | 67370.8314 | 49934.4686 | 40433.7396 | 104538.9562 | 69055.5926 | 45315.3012 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| P03 Northwest-British Columbia | 0 | 0 | 0 | 14.199 | 131.343 | 244.581 | 127.215 | 6.552 | 30.948 | 121.23 | 167.181 | n/a | n/a | n/a | -3150 | -3150 | -3150 | -3150 | -3150 | -3150 | -3150 | -3150 | n/a | n/a | n/a | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
| P09 West of Broadview | 0 | 0 | 26.4401 | 26.6794 | 46.1879 | 21748.7251 | 2771.3757 | 5.7121 | 1063.9587 | 214.8532 | 195.3267 | n/a | n/a | -2573 | -2573 | -2573 | -2573 | -2573 | -2573 | -2573 | -2573 | -2573 | n/a | n/a | 2573 | 2573 | 2573 | 2573 | 2573 | 2573 | 2573 | 2573 | 2573
| P11 West of Crossover | 4.1256 | 2.0342 | 11.4728 | 0 | 5.952 | 65.3085 | 13.5018 | 0 | 10.179 | 3.7047 | 4.3205 | -2598 | -2598 | -2598 | n/a | -2598 | -2598 | -2598 | n/a | -2598 | -2598 | -2598 | 2598 | 2598 | 2598 | n/a | 2598 | 2598 | 2598 | n/a | 2598 | 2598 | 2598
| P14 Idaho to Northwest | 3.8328 | 0 | 2.694 | 575.2777 | 494.5387 | 716.6453 | 284.7149 | 812.6258 | 673.4295 | 1465.5532 | 512.55 | -1200 | n/a | -1200 | -2250 | -2250 | -2250 | -2250 | -2250 | -2250 | -2250 | -2250 | 2400 | n/a | 2400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | Upgrade in 2030 due to Boardman-Hemingway 500 kV
| P15 Midway-LosBanos | 1.4634 | 0.3078 | 27.1998 | 3715.256 | 12.2046 | 72.1108 | 40.1889 | 3558.8067 | 0.18937 | 30536.9031 | 113.1061 | -3265 | -3265 | -3265 | -3265 | -3265 | -3265 | -3265 | -3265 | -3265 | -3265 | -3265 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400
| P16 Idaho-Sierra | 0 | 0 | 0.65196 | 23.7465 | 36.7193 | 79.2677 | 39.1722 | 21.91 | 121.68 | 85.0245 | 117.825 | n/a | n/a | -360 | -360 | -360 | -360 | -360 | -360 | -360 | -360 | -360 | n/a | n/a | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
| P18 Montana-Idaho | 2501.551 | 2848.5785 | 17523.6056 | 3933.2743 | 4270.741 | 3908.065 | 2557.3892 | 4352.7304 | 2976.4221 | 5112.7547 | 3223.9755 | -256 | -256 | -256 | -256 | -256 | -256 | -256 | -256 | -256 | -256 | -256 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337
| P19 Bridger West | 0 | 0 | 0 | 9.6792 | 16.5192 | 228507.582 | 116684.9611 | 2.6424 | 8788.3377 | 39.684 | 0 | n/a | n/a | n/a | -1250 | -1250 | -1250 | -2300 | -1250 | -2300 | -1250 | n/a | n/a | n/a | n/a | 2400 | 2400 | 2400 | 4100 | 2400 | 4100 | 2400 | n/a | Upgraded in Scenario 3 due to Gateway West Project: Segment D
| P23 Four Corners 345/500 Qualified Path | 0 | 0 | 0.009 | 496.988 | 4338.786 | 7501.762 | 4463.204 | 1060.445 | 10567.337 | 13475.744 | 6666.232 | n/a | n/a | -1000 | -1000 | -1000 | -1000 | -1000 | -1000 | -1000 | -1000 | -1000 | n/a | n/a | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| P24 PG&E-Sierra | 288.5448 | 212.5635 | 6316.1569 | 201.7337 | 373.6945 | 725.7998 | 688.4541 | 221.9591 | 824.4502 | 613.0022 | 588.0599 | -150 | -150 | -150 | -150 | -150 | -150 | -150 | -150 | -150 | -150 | -150 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
| P25 PacifiCorp/PG&E 115 kV Interconnection | 15.0053 | 16.1072 | 144.7444 | 7.8059 | 28.4106 | 58.966 | 52.7214 | 8.9723 | 69.9574 | 74.6183 | 42.3882 | -45 | -45 | -45 | -45 | -45 | -45 | -45 | -45 | -45 | -45 | -45 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| P26 Northern-Southern California | 13363.484 | 8858.808 | 270117.218 | 4014.574 | 12667.877 | 8726.953 | 12430.008 | 3650.726 | 7077.384 | 2323.375 | 9683.165 | -3000 | -3000 | -3000 | -3000 | -3000 | -3000 | -3000 | -3000 | -3000 | -3000 | -3000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
| P28 Intermountain-Mona 345 kV | 218.6112 | 42.258 | 3220.6632 | 554.1802 | 906.1098 | 2172.4372 | 2392.3274 | 782.9472 | 622.8752 | 1053.5602 | 581.5408 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | -1200 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400
| P29 Intermountain-Gonder 230 kV | 0.194 | 4.1544 | 103.0362 | 1217.8378 | 1221.582 | 3278.7844 | 7048.0924 | 1183.1856 | 4773.4526 | 2904.9608 | 3689.455 | -200 | -200 | -200 | -200 | -200 | -200 | -200 | -200 | -200 | -200 | -200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| P30 TOT 1A | 59.1285 | 12.833 | 6.2829 | 330.7181 | 325.9678 | 781.7433 | 62.3942 | 346.6671 | 29.4781 | 41.7579 | 101.0731 | -650 | -650 | -650 | -650 | -650 | -650 | -650 | -650 | -650 | -650 | -650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650
| P31 TOT 2A | 3.9178 | 2.0334 | 8.3718 | 4093.5044 | 6576.5308 | 8472.1954 | 9163.6382 | 4124.3784 | 9867.0531 | 4292.7253 | 4065.0343 | -690 | -690 | -690 | -690 | -690 | -690 | -690 | -690 | -690 | -690 | -690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
| P32 Pavant-Gonder InterMtn-Gonder 230 kV | 35.1318 | 6.5292 | 70.0347 | 28.0898 | 123.4777 | 276.0834 | 78.2134 | 34.1676 | 177.4652 | 581.4368 | 203.2933 | -235 | -235 | -235 | -235 | -235 | -235 | -235 | -235 | -235 | -235 | -235 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 440
| P33 Bonanza West | 31.2516 | 0.021195 | 5079.0063 | 0 | 0 | 7380.0158 | 0 | 0 | 0 | 0 | 0 | -785 | -785 | -785 | n/a | n/a | -785 | n/a | n/a | n/a | n/a | n/a | 785 | 785 | 785 | n/a | n/a | 785 | n/a | n/a | n/a | n/a | n/a
| P35 TOT 2C | 567.4014 | 252.3372 | 9758.07 | 747.785 | 2480.9675 | 5905.8597 | 4665.7163 | 830.6135 | 3899.973 | 3486.8579 | 2671.098 | -580 | -580 | -580 | -580 | -580 | -580 | -580 | -580 | -580 | -580 | -580 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
| P36 TOT 3 | 925.4532 | 564.144 | 54760.4172 | 29760.0583 | 30361.0702 | 239526.1522 | 94664.6182 | 30070.5859 | 54454.1256 | 12755.5445 | 9190.1174 | -1680 | -1680 | -1680 | -1680 | -1680 | -1680 | -1680 | -1680 | -1680 | -1680 | -1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680
| P38 TOT 4B | 0 | 0 | 0 | 0 | 0 | 81250.6297 | 2188.3629 | 0 | 1510.5059 | 5.9426 | 34.5022 | n/a | n/a | n/a | n/a | n/a | -880 | -880 | n/a | -880 | -880 | -880 | n/a | n/a | n/a | n/a | n/a | 880 | 880 | n/a | 880 | 880 | 880
| P39 TOT 5 | 0 | 0 | 68.3726 | 32963.9023 | 33068.7091 | 2434.9954 | 1280.7967 | 33394.6721 | 914.3887 | 3507.3494 | 1506.5954 | n/a | n/a | -1680 | -1680 | -1680 | -1680 | -1680 | -1680 | -1680 | -1680 | -1680 | n/a | n/a | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680
| P40 TOT 7 | 0 | 0 | 247.566 | 0 | 0 | 35.7282 | 99.308 | 0 | 0 | 192.1608 | 67.1443 | n/a | n/a | -890 | n/a | n/a | -890 | -890 | n/a | n/a | -890 | -890 | n/a | n/a | 890 | n/a | n/a | 890 | 890 | n/a | n/a | 890 | 890
| P45 SDG&E-CFE | 13332.5104 | 33418.2264 | 5297.1528 | 107427.801 | 110986.6773 | 82254.5201 | 31614.9211 | 201080.6274 | 95963.8701 | 39257.0628 | 21620.4623 | -800 | -800 | -800 | -800 | -800 | -800 | -800 | -800 | -800 | -800 | -800 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408
| P47 Southern New Mexico (NM1) | 0 | 0 | 84228.785 | 6579.9513 | 23.2488 | 41897.4884 | 34362.3807 | 0 | 20181.6172 | 46395.4399 | 12941.9992 | n/a | n/a | -1048 | -1048 | -1048 | -1048 | -1048 | n/a | -1048 | -1048 | -1048 | n/a | n/a | 1048 | 1048 | 1048 | 1048 | 1048 | n/a | 1048 | 1048 | 1048
| P48 Northern New Mexico (NM2) | 377.4028 | 489.3086 | 180847.4468 | 0 | 0 | 534313.5588 | 482631.4023 | 0 | 483949.6973 | 35525.424 | 11822.64 | -1970 | -1970 | -1970 | n/a | n/a | -1970 | -1970 | n/a | -1970 | -1970 | -1970 | 1970 | 1970 | 1970 | n/a | n/a | 1970 | 1970 | n/a | 1970 | 1970 | 1970
| P52 Silver Peak-Control 55 kV | 61.7971 | 49.2219 | 325.9697 | 224.0537 | 357.4189 | 576.5733 | 512.8123 | 217.4131 | 480.518 | 447.5066 | 413.1135 | -17 | -17 | -17 | -17 | -17 | -17 | -17 | -17 | -17 | -17 | -17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
| P60 Inyo-Control 115 kV Tie | 13.6549 | 12.5444 | 42.7298 | 11.0209 | 60.5548 | 93.0494 | 52.6734 | 9.0901 | 69.8862 | 75.1187 | 48.5539 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
| P61 Lugo-Victorville 500 kV Line | 0.0639 | 0.0081 | 0.1053 | 310.9878 | 8582.0364 | 16653.3525 | 7677.9216 | 352.6884 | 10060.5978 | 10676.2338 | 7211.7036 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900
| P65 Pacific DC Intertie (PDCI) | 0 | 0 | 0 | 235.0141 | 6846.8956 | 11355.145 | 0 | 276.5014 | 0 | 2551.0303 | 0 | n/a | n/a | n/a | -3100 | -3100 | -3100 | n/a | -3100 | n/a | -3100 | n/a | n/a | n/a | n/a | 3220 | 3220 | 3220 | n/a | 3220 | n/a | 3220 | n/a
| P66 COI | 0 | 0 | 0 | 0 | 1563.8779 | 4636.5564 | 3061.5095 | 6.1483 | 4017.1021 | 5024.25 | 2578.1461 | n/a | n/a | n/a | n/a | -3675 | -3675 | -3675 | -3675 | -3675 | -3675 | -3675 | n/a | n/a | n/a | n/a | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
| P76 Alturas Project | 339.1029 | 310.2855 | 8986.6707 | 321.3039 | 524.6367 | 801.0012 | 787.1478 | 348.642 | 903.2994 | 648.6729 | 660.0009 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
| P77 Crystal-Allen | 23.3938 | 9.8278 | 452.7519 | 37.7549 | 150.4487 | 316.0498 | 216.9829 | 41.6404 | 267.1258 | 150.2178 | 170.3967 | -950 | -950 | -950 | -950 | -950 | -950 | -950 | -950 | -950 | -950 | -950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950
| P80 Montana Southeast | 1.5744 | 2.0004 | 15.9066 | 12.1902 | 21.801 | 12249.8988 | 512.1486 | 11.6652 | 134.499 | 149.4252 | 96.4494 | -600 | -600 | -600 | -600 | -600 | -600 | -600 | -600 | -600 | -600 | -600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
| P83 Montana Alberta Tie Line | 27091.4816 | 23444.4352 | 43962.3893 | 6599.4271 | 11285.5185 | 19630.1644 | 16590.9997 | 6569.512 | 25898.9317 | 12817.0223 | 7288.2444 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325
| xy AB-MT | 30633.1379 | 14422.1961 | 30673.6195 | 583.3447 | 6247.3612 | 2840.8323 | 479.8707 | 4473.5176 | 6158.3211 | 8307.4758 | 6208.2527 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | -300 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325
| xy WA-BC East | 57.9992 | 33.3332 | 281.4324 | 122.6812 | 308.3264 | 1196.0516 | 1232.6512 | 127.1596 | 975.066 | 582.3956 | 443.812 | -400 | -400 | -400 | -400 | -400 | -400 | -400 | -400 | -400 | -400 | -400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
| xy WA-BC West | 16.5072 | 0 | 0.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2850 | n/a | -2850 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 3000 | n/a | 3000 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| z AZ Palo Verde East | 0 | 0 | 47.3551 | 15710.3815 | 151204.6659 | 258268.9291 | 176954.7172 | 43421.5612 | 273264.2579 | 106636.2169 | 194701.2327 | n/a | n/a | -8010 | -8010 | -8010 | -8010 | -8010 | -8010 | -8010 | -8010 | -8010 | n/a | n/a | 8010 | 8010 | 8010 | 8010 | 8010 | 8010 | 8010 | 8010 | 8010
| z CA PDCI South | 0.46426 | 100.4775 | 5.3598 | 74.4183 | 604.3649 | 1108.264 | 7228.5847 | 122.1247 | 6476.4075 | 634.3593 | 3603.4243 | -3100 | -3100 | -3100 | -3100 | -3100 | -3100 | -3100 | -3100 | -3100 | -3100 | -3100 | 2780 | 2780 | 2780 | 2780 | 2780 | 2780 | 2780 | 2780 | 2780 | 2780 | 2780
| z WA North of Hanford | 0 | 0 | 0 | 1808.3946 | 9848.8995 | 38344.978 | 34934.0683 | 1438.624 | 30581.9064 | 22046.4028 | 17022.2532 | n/a | n/a | n/a | -2948 | -2948 | -2948 | -2948 | -2948 | -2948 | -2948 | -2948 | n/a | n/a | n/a | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100

## 2020 CP
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Path | P01 Alberta-British Columbia | -1200 | 1000 | -346.2859 | 6 | 91 | 248095.5208 | Path | P01 Alberta-British Columbia | -1200 | 1000 | -346.2859 | 6 | 91 | 248095.5208
Nomogram | BPA_PreferredRate | 0 | 3500 | 1016.6418 | 7578 | 0 | 59075.749 | Nomogram | BPA_PreferredRate | 0 | 3500 | 1016.6418 | 7578 | 0 | 59075.749
Path | xy AB-MT | -300 | 325 | -48.3214 | 3 | 80 | 30633.1379 | Path | xy AB-MT | -300 | 325 | -48.3214 | 3 | 80 | 30633.1379
Path | P83 Montana Alberta Tie Line | -300 | 325 | -48.3214 | 35 | 212 | 27091.4816 | Path | P83 Montana Alberta Tie Line | -300 | 325 | -48.3214 | 35 | 212 | 27091.4816
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1021.2002 | 0 | 4848 | 24004.1093 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1021.2002 | 0 | 4848 | 24004.1093
Path | P26 Northern-Southern California | -3000 | 4000 | 2475.2378 | 1317 | 0 | 13363.484 | Path | P26 Northern-Southern California | -3000 | 4000 | 2475.2378 | 1317 | 0 | 13363.484
Path | P45 SDG&E-CFE | -800 | 408 | -2.0146 | 9 | 7 | 13332.5104 | Path | P45 SDG&E-CFE | -800 | 408 | -2.0146 | 9 | 7 | 13332.5104
Path | P18 Montana-Idaho | -256 | 337 | 121.4128 | 213 | 0 | 2501.551 | Path | P18 Montana-Idaho | -256 | 337 | 121.4128 | 213 | 0 | 2501.551
Nomogram | IPP DC | -99999 | 361 | 86.8156 | 2518 | 0 | 1082.8751 | Nomogram | IPP DC | -99999 | 361 | 86.8156 | 2518 | 0 | 1082.8751
Path | P36 TOT 3 | -1680 | 1680 | 1132.8027 | 195 | 0 | 925.4532 | Path | P36 TOT 3 | -1680 | 1680 | 1132.8027 | 195 | 0 | 925.4532
Path | P35 TOT 2C | -580 | 600 | 457.1193 | 1061 | 0 | 567.4014 | Path | P35 TOT 2C | -580 | 600 | 457.1193 | 1061 | 0 | 567.4014
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 1632.6746 | 86 | 0 | 469.4243 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 1632.6746 | 86 | 0 | 469.4243
Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | 1058.5038 | 52 | 0 | 377.4028 | Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | 1058.5038 | 52 | 0 | 377.4028
Path | P76 Alturas Project | -300 | 300 | 186.8332 | 559 | 13 | 339.1029 | Path | P76 Alturas Project | -300 | 300 | 186.8332 | 559 | 13 | 339.1029
Path | P24 PG&E-Sierra | -150 | 160 | 71.9405 | 792 | 24 | 288.5448 | Path | P24 PG&E-Sierra | -150 | 160 | 71.9405 | 792 | 24 | 288.5448
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 33.3757 | 0 | 147 | 218.6112 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 33.3757 | 0 | 147 | 218.6112
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 5.3036 | 194 | 14 | 61.7971 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 5.3036 | 194 | 14 | 61.7971
Path | P30 TOT 1A | -650 | 650 | 303.5848 | 20 | 0 | 59.1285 | Path | P30 TOT 1A | -650 | 650 | 303.5848 | 20 | 0 | 59.1285
Path | xy WA-BC East | -400 | 400 | 17.7387 | 211 | 80 | 57.9992 | Path | xy WA-BC East | -400 | 400 | 17.7387 | 211 | 80 | 57.9992
Nomogram | COI 1 | -99999 | 6763 | 2424.1561 | 2 | 0 | 54.1852 | Nomogram | COI 1 | -99999 | 6763 | 2424.1561 | 2 | 0 | 54.1852
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 95.5947 | 0 | 14 | 35.1318 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 95.5947 | 0 | 14 | 35.1318
Path | P33 Bonanza West | -785 | 785 | 405.6676 | 5 | 0 | 31.2516 | Path | P33 Bonanza West | -785 | 785 | 405.6676 | 5 | 0 | 31.2516
Path | CAISO Zero Net Export | -99999 | 0.01 | -3734.5565 | 80 | 0 | 28.2637 | Path | CAISO Zero Net Export | -99999 | 0.01 | -3734.5565 | 80 | 0 | 28.2637
Path | P77 Crystal-Allen | -950 | 950 | -139.0371 | 65 | 486 | 23.3938 | Path | P77 Crystal-Allen | -950 | 950 | -139.0371 | 65 | 486 | 23.3938
Path | 2136-cont 0 | -796 | 796 | -354.062 | 0 | 105 | 17.0026 | Path | 2136-cont 0 | -796 | 796 | -354.062 | 0 | 105 | 17.0026
Path | xy WA-BC West | -2850 | 3000 | -257.3561 | 0 | 2 | 16.5072 | Path | xy WA-BC West | -2850 | 3000 | -257.3561 | 0 | 2 | 16.5072
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | -26.9601 | 0 | 140 | 15.0053 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | -26.9601 | 0 | 140 | 15.0053
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -37.777 | 0 | 138 | 13.6549 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -37.777 | 0 | 138 | 13.6549
Nomogram | COI 2 | -99999 | 4560 | 1374.1748 | 1 | 0 | 5.6909 | Nomogram | COI 2 | -99999 | 4560 | 1374.1748 | 1 | 0 | 5.6909
Path | P11 West of Crossover | -2598 | 2598 | 1895.067 | 15 | 0 | 4.1256 | Path | P11 West of Crossover | -2598 | 2598 | 1895.067 | 15 | 0 | 4.1256
Path | P31 TOT 2A | -690 | 690 | 156.7649 | 54 | 0 | 3.9178 | Path | P31 TOT 2A | -690 | 690 | 156.7649 | 54 | 0 | 3.9178
Path | P14 Idaho to Northwest | -1200 | 2400 | 102.8613 | 0 | 1 | 3.8328 | Path | P14 Idaho to Northwest | -1200 | 2400 | 102.8613 | 0 | 1 | 3.8328
Path | P80 Montana Southeast | -600 | 600 | -54.4278 | 0 | 18 | 1.5744 | Path | P80 Montana Southeast | -600 | 600 | -54.4278 | 0 | 18 | 1.5744
Path | P15 Midway-LosBanos | -3265 | 5400 | 1000.2832 | 3 | 0 | 1.4634 | Path | P15 Midway-LosBanos | -3265 | 5400 | 1000.2832 | 3 | 0 | 1.4634
Path | z CA PDCI South | -3100 | 2780 | 114.5028 | 4 | 0 | 0.46426 | Path | z CA PDCI South | -3100 | 2780 | 114.5028 | 4 | 0 | 0.46426
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 53.4399 | 1 | 0 | 0.194 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 53.4399 | 1 | 0 | 0.194
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -24.0261 | 2 | 0 | 0.0639 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -24.0261 | 2 | 0 | 0.0639
Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 279.0256 | 4 | 0 | 0.05258 | Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 279.0256 | 4 | 0 | 0.05258

## 2020 CAISO+PAC
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Path | P01 Alberta-British Columbia | -1200 | 1000 | -362.3418 | 6 | 101 | 162343.6154 | Path | P01 Alberta-British Columbia | -1200 | 1000 | -362.3418 | 6 | 101 | 162343.6154
Nomogram | BPA_PreferredRate | 0 | 3500 | 1018.6461 | 7574 | 0 | 54939.5308 | Nomogram | BPA_PreferredRate | 0 | 3500 | 1018.6461 | 7574 | 0 | 54939.5308
Path | P45 SDG&E-CFE | -800 | 408 | -0.88174 | 12 | 5 | 33418.2264 | Path | P45 SDG&E-CFE | -800 | 408 | -0.88174 | 12 | 5 | 33418.2264
Path | P83 Montana Alberta Tie Line | -300 | 325 | -67.3124 | 30 | 88 | 23444.4352 | Path | P83 Montana Alberta Tie Line | -300 | 325 | -67.3124 | 30 | 88 | 23444.4352
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1061.9937 | 0 | 4172 | 19411.2447 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1061.9937 | 0 | 4172 | 19411.2447
Path | xy AB-MT | -300 | 325 | -67.3124 | 4 | 70 | 14422.1961 | Path | xy AB-MT | -300 | 325 | -67.3124 | 4 | 70 | 14422.1961
Path | P26 Northern-Southern California | -3000 | 4000 | 2507.4321 | 1236 | 0 | 8858.808 | Path | P26 Northern-Southern California | -3000 | 4000 | 2507.4321 | 1236 | 0 | 8858.808
Path | P18 Montana-Idaho | -256 | 337 | 120.5644 | 158 | 0 | 2848.5785 | Path | P18 Montana-Idaho | -256 | 337 | 120.5644 | 158 | 0 | 2848.5785
Nomogram | IPP DC | -99999 | 361 | 63.4114 | 1692 | 0 | 641.2201 | Nomogram | IPP DC | -99999 | 361 | 63.4114 | 1692 | 0 | 641.2201
Path | P36 TOT 3 | -1680 | 1680 | 1135.737 | 148 | 0 | 564.144 | Path | P36 TOT 3 | -1680 | 1680 | 1135.737 | 148 | 0 | 564.144
Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | 1058.3427 | 59 | 0 | 489.3086 | Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | 1058.3427 | 59 | 0 | 489.3086
Path | CAISO Zero Net Export | -99999 | 0.01 | -3860.9241 | 40 | 0 | 428.0522 | Path | CAISO Zero Net Export | -99999 | 776 | -3860.9241 | 40 | 0 | 428.0522
Path | P76 Alturas Project | -300 | 300 | 187.3576 | 348 | 7 | 310.2855 | Path | P76 Alturas Project | -300 | 300 | 187.3576 | 348 | 7 | 310.2855
Path | P35 TOT 2C | -580 | 600 | 416.1949 | 582 | 0 | 252.3372 | Path | P35 TOT 2C | -580 | 600 | 416.1949 | 582 | 0 | 252.3372
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 1660.3414 | 95 | 0 | 234.1618 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 1660.3414 | 95 | 0 | 234.1618
Path | P24 PG&E-Sierra | -150 | 160 | 67.2668 | 488 | 13 | 212.5635 | Path | P24 PG&E-Sierra | -150 | 160 | 67.2668 | 488 | 13 | 212.5635
Path | z CA PDCI South | -3100 | 2780 | 163.4205 | 34 | 0 | 100.4775 | Path | z CA PDCI South | -3100 | 2780 | 163.4205 | 34 | 0 | 100.4775
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 5.4125 | 177 | 2 | 49.2219 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 5.4125 | 177 | 2 | 49.2219
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 5.4777 | 0 | 147 | 42.258 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 5.4777 | 0 | 147 | 42.258
Path | xy WA-BC East | -400 | 400 | -29.9028 | 55 | 83 | 33.3332 | Path | xy WA-BC East | -400 | 400 | -29.9028 | 55 | 83 | 33.3332
Path | 2136-cont 0 | -796 | 796 | -487.7421 | 0 | 112 | 21.086 | Path | 2136-cont 0 | -796 | 796 | -487.7421 | 0 | 112 | 21.086
Nomogram | COI 1 | -99999 | 6763 | 2492.0852 | 2 | 0 | 17.5635 | Nomogram | COI 1 | -99999 | 6763 | 2492.0852 | 2 | 0 | 17.5635
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | -28.0492 | 0 | 197 | 16.1072 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | -28.0492 | 0 | 197 | 16.1072
Path | P30 TOT 1A | -650 | 650 | 280.1103 | 7 | 0 | 12.833 | Path | P30 TOT 1A | -650 | 650 | 280.1103 | 7 | 0 | 12.833
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -38.9091 | 0 | 149 | 12.5444 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -38.9091 | 0 | 149 | 12.5444
Path | P77 Crystal-Allen | -950 | 950 | -242.2074 | 65 | 153 | 9.8278 | Path | P77 Crystal-Allen | -950 | 950 | -242.2074 | 65 | 153 | 9.8278
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 107.967 | 0 | 11 | 6.5292 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 107.967 | 0 | 11 | 6.5292
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 57.9336 | 3 | 0 | 4.1544 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 57.9336 | 3 | 0 | 4.1544
Path | P11 West of Crossover | -2598 | 2598 | 1931.3932 | 7 | 0 | 2.0342 | Path | P11 West of Crossover | -2598 | 2598 | 1931.3932 | 7 | 0 | 2.0342
Path | P31 TOT 2A | -690 | 690 | 164.6563 | 34 | 0 | 2.0334 | Path | P31 TOT 2A | -690 | 690 | 164.6563 | 34 | 0 | 2.0334
Path | P80 Montana Southeast | -600 | 600 | -97.1154 | 0 | 18 | 2.0004 | Path | P80 Montana Southeast | -600 | 600 | -97.1154 | 0 | 18 | 2.0004
Nomogram | COI 2 | -99999 | 4560 | 1442.1038 | 1 | 0 | 1.213 | Nomogram | COI 2 | -99999 | 4560 | 1442.1038 | 1 | 0 | 1.213
Path | P15 Midway-LosBanos | -3265 | 5400 | 984.5156 | 4 | 0 | 0.3078 | Path | P15 Midway-LosBanos | -3265 | 5400 | 984.5156 | 4 | 0 | 0.3078
Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 261.9637 | 1 | 0 | 0.037045 | Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 261.9637 | 1 | 0 | 0.037045
Path | P33 Bonanza West | -785 | 785 | 411.7717 | 1 | 0 | 0.021195 | Path | P33 Bonanza West | -785 | 785 | 411.7717 | 1 | 0 | 0.021195
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -39.566 | 2 | 0 | 0.0081 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -39.566 | 2 | 0 | 0.0081

## 2020 Regional
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Path | P01 Alberta-British Columbia | -1200 | 1000 | -290.4481 | 27 | 108 | 312422.636 | Path | P01 Alberta-British Columbia | -1200 | 1000 | -290.4481 | 27 | 108 | 312422.636
Path | P26 Northern-Southern California | -3000 | 4000 | 2597.5539 | 1803 | 0 | 270117.218 | Path | P26 Northern-Southern California | -3000 | 4000 | 2597.5539 | 1803 | 0 | 270117.218
Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | 1060.6434 | 32 | 0 | 180847.4468 | Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | 1060.6434 | 32 | 0 | 180847.4468
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 990.6123 | 0 | 5852 | 123291.7313 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 990.6123 | 0 | 5852 | 123291.7313
Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 448.0647 | 41 | 0 | 84228.785 | Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 448.0647 | 41 | 0 | 84228.785
Nomogram | BPA_PreferredRate | 0 | 3500 | 945.6043 | 7346 | 0 | 64616.2593 | Nomogram | BPA_PreferredRate | 0 | 3500 | 945.6043 | 7346 | 0 | 64616.2593
Path | P36 TOT 3 | -1680 | 1680 | 1382.8418 | 1512 | 0 | 54760.4172 | Path | P36 TOT 3 | -1680 | 1680 | 1382.8418 | 1512 | 0 | 54760.4172
Path | P83 Montana Alberta Tie Line | -300 | 325 | -115.3381 | 42 | 497 | 43962.3893 | Path | P83 Montana Alberta Tie Line | -300 | 325 | -115.3381 | 42 | 497 | 43962.3893
Path | xy AB-MT | -300 | 325 | -115.3381 | 6 | 175 | 30673.6195 | Path | xy AB-MT | -300 | 325 | -115.3381 | 6 | 175 | 30673.6195
Path | P18 Montana-Idaho | -256 | 337 | 132.2768 | 437 | 0 | 17523.6056 | Path | P18 Montana-Idaho | -256 | 337 | 132.2768 | 437 | 0 | 17523.6056
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 1741.3067 | 115 | 0 | 9802.5816 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 1741.3067 | 115 | 0 | 9802.5816
Path | P35 TOT 2C | -580 | 600 | 445.4455 | 1686 | 3 | 9758.07 | Path | P35 TOT 2C | -580 | 600 | 445.4455 | 1686 | 3 | 9758.07
Path | P76 Alturas Project | -300 | 300 | 232.9249 | 1179 | 0 | 8986.6707 | Path | P76 Alturas Project | -300 | 300 | 232.9249 | 1179 | 0 | 8986.6707
Nomogram | IPP DC | -99999 | 361 | -59.373 | 1259 | 0 | 8143.4458 | Nomogram | IPP DC | -99999 | 361 | -59.373 | 1259 | 0 | 8143.4458
Path | P24 PG&E-Sierra | -150 | 160 | 104.8118 | 1414 | 7 | 6316.1569 | Path | P24 PG&E-Sierra | -150 | 160 | 104.8118 | 1414 | 7 | 6316.1569
Path | P45 SDG&E-CFE | -800 | 408 | -6.0922 | 2 | 16 | 5297.1528 | Path | P45 SDG&E-CFE | -800 | 408 | -6.0922 | 2 | 16 | 5297.1528
Path | P33 Bonanza West | -785 | 785 | 246.418 | 15 | 0 | 5079.0063 | Path | P33 Bonanza West | -785 | 785 | 246.418 | 15 | 0 | 5079.0063
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | -129.3266 | 0 | 323 | 3220.6632 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | -129.3266 | 0 | 323 | 3220.6632
Path | P77 Crystal-Allen | -950 | 950 | -643.3803 | 45 | 847 | 452.7519 | Path | P77 Crystal-Allen | -950 | 950 | -643.3803 | 45 | 847 | 452.7519
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 4.544 | 270 | 21 | 325.9697 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 4.544 | 270 | 21 | 325.9697
Path | xy WA-BC East | -400 | 400 | 108.7281 | 490 | 82 | 281.4324 | Path | xy WA-BC East | -400 | 400 | 108.7281 | 490 | 82 | 281.4324
Path | 2136-cont 0 | -796 | 796 | -349.087 | 0 | 164 | 276.2884 | Path | 2136-cont 0 | -796 | 796 | -349.087 | 0 | 164 | 276.2884
Path | P40 TOT 7 | -890 | 890 | 526.4757 | 39 | 0 | 247.566 | Path | P40 TOT 7 | -890 | 890 | 526.4757 | 39 | 0 | 247.566
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | -15.9694 | 0 | 214 | 144.7444 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | -15.9694 | 0 | 214 | 144.7444
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 69.9536 | 96 | 0 | 103.0362 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 69.9536 | 96 | 0 | 103.0362
Nomogram | COI 2 | -99999 | 4560 | 1434.7091 | 10 | 0 | 88.4914 | Nomogram | COI 2 | -99999 | 4560 | 1434.7091 | 10 | 0 | 88.4914
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 139.8495 | 0 | 40 | 70.0347 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 139.8495 | 0 | 40 | 70.0347
Path | P39 TOT 5 | -1680 | 1680 | 415.1589 | 13 | 0 | 68.3726 | Path | P39 TOT 5 | -1680 | 1680 | 415.1589 | 13 | 0 | 68.3726
Path | CAISO Zero Net Export | -99999 | 0.01 | -3484.6205 | 215 | 0 | 60.2533 | Path | CAISO Zero Net Export | -99999 | 0.01 | -3484.6205 | 215 | 0 | 60.2533
Path | z AZ Palo Verde East | -8010 | 8010 | 4704.5752 | 1 | 0 | 47.3551 | Path | z AZ Palo Verde East | -8010 | 8010 | 4704.5752 | 1 | 0 | 47.3551
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -33.8551 | 0 | 182 | 42.7298 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -33.8551 | 0 | 182 | 42.7298
Nomogram | COI 1 | -99999 | 6763 | 2484.6904 | 2 | 0 | 36.7704 | Nomogram | COI 1 | -99999 | 6763 | 2484.6904 | 2 | 0 | 36.7704
Path | P15 Midway-LosBanos | -3265 | 5400 | 907.0752 | 10 | 0 | 27.1998 | Path | P15 Midway-LosBanos | -3265 | 5400 | 907.0752 | 10 | 0 | 27.1998
Path | P09 West of Broadview | -2573 | 2573 | 1747.0911 | 6 | 0 | 26.4401 | Path | P09 West of Broadview | -2573 | 2573 | 1747.0911 | 6 | 0 | 26.4401
Contingency | 2422-N-2 SCE Serrano-Lewis #1 and Serrano-Villa PK #2 230 kV | -1518 | 1518 | 877.4235 | 1 | 0 | 16.6191 | Contingency | 2422-N-2 SCE Serrano-Lewis #1 and Serrano-Villa PK #2 230 kV | -1518 | 1518 | 877.4235 | 1 | 0 | 16.6191
Path | P80 Montana Southeast | -600 | 600 | -104.2475 | 3 | 56 | 15.9066 | Path | P80 Montana Southeast | -600 | 600 | -104.2475 | 3 | 56 | 15.9066
Path | P11 West of Crossover | -2598 | 2598 | 1970.0953 | 27 | 0 | 11.4728 | Path | P11 West of Crossover | -2598 | 2598 | 1970.0953 | 27 | 0 | 11.4728
Path | P31 TOT 2A | -690 | 690 | 10.5187 | 42 | 35 | 8.3718 | Path | P31 TOT 2A | -690 | 690 | 10.5187 | 42 | 35 | 8.3718
Path | P30 TOT 1A | -650 | 650 | 42.1883 | 3 | 0 | 6.2829 | Path | P30 TOT 1A | -650 | 650 | 42.1883 | 3 | 0 | 6.2829
Path | z CA PDCI South | -3100 | 2780 | 299.6155 | 10 | 0 | 5.3598 | Path | z CA PDCI South | -3100 | 2780 | 299.6155 | 10 | 0 | 5.3598
Path | P14 Idaho to Northwest | -1200 | 2400 | 81.4902 | 0 | 1 | 2.694 | Path | P14 Idaho to Northwest | -1200 | 2400 | 81.4902 | 0 | 1 | 2.694
Path | P16 Idaho-Sierra | -360 | 500 | 101.8668 | 0 | 5 | 0.65196 | Path | P16 Idaho-Sierra | -360 | 500 | 101.8668 | 0 | 5 | 0.65196
Path | xy WA-BC West | -2850 | 3000 | -393.6889 | 0 | 1 | 0.3363 | Path | xy WA-BC West | -2850 | 3000 | -393.6889 | 0 | 1 | 0.3363
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -3.957 | 5 | 0 | 0.1053 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -3.957 | 5 | 0 | 0.1053
Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 262.5357 | 2 | 0 | 0.01673 | Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 262.5357 | 2 | 0 | 0.01673
Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -309.3749 | 0 | 1 | 0.009 | Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -309.3749 | 0 | 1 | 0.009
[8 empty] | Path | 763
[8 empty] | Path | 788
[8 empty] | Path | 2314
[8 empty] | Path | 2353
[8 empty] | Path | 2392
[8 empty] | Path | 2394
[8 empty] | Path | 2743
[8 empty] | Path | 2748
[8 empty] | Path | 2852
[8 empty] | Path | 2853
[8 empty] | Path | 2853
[8 empty] | Path | 3550
[8 empty] | Path | 3551
[8 empty] | Path | 3552
[8 empty] | Path | 3554
[8 empty] | Path | 3561
[8 empty] | Path | 3562
[8 empty] | Path | 3563
[8 empty] | Path | 3716
[8 empty] | Path | 4916
[8 empty] | Path | 5544
[8 empty] | Path | 5966
[8 empty] | Path | 6001
[8 empty] | Path | 6001
[8 empty] | Path | 6007
[8 empty] | Path | 6007
[8 empty] | Path | 27186
[8 empty] | Path | 27700
[8 empty] | Path | 27705
[8 empty] | Path | 34160
[8 empty] | Path | 36197
[8 empty] | Path | 36197
[8 empty] | Path | 36197
[8 empty] | Path | 36197
[8 empty] | Path | 36245
[8 empty] | Path | 27700-cont 0
[8 empty] | Path | 27703-cont 0
[8 empty] | Path | 27705-cont 0
[8 empty] | Path | 2810-cont 0
[8 empty] | Path | 2851-cont 0
[8 empty] | Path | 2852-cont 0
[8 empty] | Path | 2853-cont 0
[8 empty] | Path | 28580-CAISOborder
[8 empty] | Path | 28581-CAISOborder
[8 empty] | Path | 28601-CAISOborder
[8 empty] | Path | 28602-CAISOborder
[8 empty] | Path | 28651-CAISOborder
[8 empty] | Path | 28652-CAISOborder
[8 empty] | Path | 28691-CAISOborder
[8 empty] | Path | 2899-cont 0
[8 empty] | Path | 2990-CAISOborder
[8 empty] | Path | 3000-CAISOborder
[8 empty] | Path | 3090-cont 0
[8 empty] | Path | 3091-cont 0
[8 empty] | Path | 3092-cont 0
[8 empty] | Path | 3093-cont 0
[8 empty] | Path | 3572-cont 0
[8 empty] | Path | 3582-cont 0
[8 empty] | Path | 3583-cont 0
[8 empty] | Path | 36179-CAISOborder
[8 empty] | Path | 36197-cont 0
[8 empty] | Path | 36241-CAISOborder
[8 empty] | Path | 36241-CAISOborder
[8 empty] | Path | 36244-cont 0
[8 empty] | Path | 36245-cont 0
[8 empty] | Path | 36245-cont 0
[8 empty] | Path | 36246-CAISOborder
[8 empty] | Path | 36250-cont 0
[8 empty] | Path | 36251-cont 0
[8 empty] | Path | 36252-cont 0
[8 empty] | Path | 36252-cont 0
[8 empty] | Path | 36253-cont 0
[8 empty] | Path | 3812-cont 0
[8 empty] | Path | 3813-cont 0
[8 empty] | Path | 3814-cont 0
[8 empty] | Path | 4039-cont 0
[8 empty] | Path | 4648-CAISOborder
[8 empty] | Path | 4648-CAISOborder
[8 empty] | Path | 4864-cont 0
[8 empty] | Path | 4912-cont 0
[8 empty] | Path | 4914-cont 0
[8 empty] | Path | 4915-cont 0
[8 empty] | Path | 4916-cont 0
[8 empty] | Path | 5451-cont 0
[8 empty] | Path | 5544-cont 0
[8 empty] | Path | 5946-cont 0
[8 empty] | Path | 5966-cont 0
[8 empty] | Path | 5967-CAISOborder
[8 empty] | Path | 5967-cont 0
[8 empty] | Path | 5976-CAISOborder
[8 empty] | Path | 6001-cont 0
[8 empty] | Path | 6007-cont 0
[8 empty] | Path | 763-CAISOborder
[8 empty] | Path | 763-cont 0
[8 empty] | Path | 788-cont 0

## 2030 1
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Nomogram | CAISO_Plus_Renewables_Limit | -99999 | 2000 | -2949.8067 | 1253 | 0 | 281395.498 | Nomogram | CAISO_Plus_Renewables_Limit | -99999 | 2000 | -2949.8067 | 1253 | 0 | 281395.498
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1026.1023 | 0 | 5415 | 178774.1947 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1026.1023 | 0 | 5415 | 178774.1947
Path | P45 SDG&E-CFE | -800 | 408 | 79.1162 | 1263 | 2 | 107427.801 | Path | P45 SDG&E-CFE | -800 | 408 | 79.1162 | 1263 | 2 | 107427.801
Nomogram | BPA_PreferredRate | 0 | 3500 | 761.1595 | 5922 | 0 | 78212.6028 | Nomogram | BPA_PreferredRate | 0 | 3500 | 761.1595 | 5922 | 0 | 78212.6028
Path | CAISO Zero Net Export | -99999 | 2000 | -3726.659 | 327 | 0 | 70617.3578 | Path | CAISO Zero Net Export | -99999 | 2000 | -3726.659 | 327 | 0 | 70617.3578
Nomogram | FreqResponse-3506 | -99999 | 0 | -51.6017 | 578 | 0 | 39954.48 | Nomogram | FreqResponse-3506 | -99999 | 0 | -51.6017 | 578 | 0 | 39954.48
Path | P39 TOT 5 | -1680 | 1680 | 234.5724 | 13 | 0 | 32963.9023 | Path | P39 TOT 5 | -1680 | 1680 | 234.5724 | 13 | 0 | 32963.9023
Path | P36 TOT 3 | -1680 | 1680 | 815.7521 | 42 | 0 | 29760.0583 | Path | P36 TOT 3 | -1680 | 1680 | 815.7521 | 42 | 0 | 29760.0583
Path | P01 Alberta-British Columbia | -1200 | 1000 | 205.8018 | 395 | 5 | 24052.809 | Path | P01 Alberta-British Columbia | -1200 | 1000 | 205.8018 | 395 | 5 | 24052.809
Path | z AZ Palo Verde East | -8010 | 8010 | 5271.2235 | 311 | 0 | 15710.3815 | Path | z AZ Palo Verde East | -8010 | 8010 | 5271.2235 | 311 | 0 | 15710.3815
Path | P83 Montana Alberta Tie Line | -300 | 325 | 1.8869 | 179 | 92 | 6599.4271 | Path | P83 Montana Alberta Tie Line | -300 | 325 | 1.8869 | 179 | 92 | 6599.4271
Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 333.1007 | 13 | 0 | 6579.9513 | Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 333.1007 | 13 | 0 | 6579.9513
Path | P31 TOT 2A | -690 | 690 | 108.4914 | 52 | 62 | 4093.5044 | Path | P31 TOT 2A | -690 | 690 | 108.4914 | 52 | 62 | 4093.5044
Path | P26 Northern-Southern California | -3000 | 4000 | 881.1209 | 121 | 313 | 4014.574 | Path | P26 Northern-Southern California | -3000 | 4000 | 881.1209 | 121 | 313 | 4014.574
Path | P18 Montana-Idaho | -256 | 337 | 155.9341 | 174 | 0 | 3933.2743 | Path | P18 Montana-Idaho | -256 | 337 | 155.9341 | 174 | 0 | 3933.2743
Path | P15 Midway-LosBanos | -3265 | 5400 | 870.4604 | 221 | 4 | 3715.256 | Path | P15 Midway-LosBanos | -3265 | 5400 | 870.4604 | 221 | 4 | 3715.256
Path | 3111-cont 0 | -1503 | 1503 | -50.397 | 0 | 155 | 3097.166 | Path | 3111-cont 0 | -1503 | 1503 | -50.397 | 0 | 155 | 3097.166
Nomogram | FreqResponse-25 | -99999 | 0 | -10.7759 | 690 | 0 | 2552.55 | Nomogram | FreqResponse-25 | -99999 | 0 | -10.7759 | 690 | 0 | 2552.55
Path | z WA North of Hanford | -2948 | 4100 | -679.8181 | 0 | 59 | 1808.3946 | Path | z WA North of Hanford | -2948 | 4100 | -679.8181 | 0 | 59 | 1808.3946
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 95.6266 | 445 | 0 | 1217.8378 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 95.6266 | 445 | 0 | 1217.8378
Path | P35 TOT 2C | -580 | 600 | 102.8684 | 317 | 468 | 747.785 | Path | P35 TOT 2C | -580 | 600 | 102.8684 | 317 | 468 | 747.785
Nomogram | FreqResponse-1 | -99999 | 0 | -0.055308 | 790 | 0 | 589.38 | Nomogram | FreqResponse-1 | -99999 | 0 | -0.055308 | 790 | 0 | 589.38
Path | xy AB-MT | -300 | 325 | 1.8869 | 133 | 78 | 583.3447 | Path | xy AB-MT | -300 | 325 | 1.8869 | 133 | 78 | 583.3447
Path | P14 Idaho to Northwest | -2250 | 3400 | -267.1103 | 0 | 28 | 575.2777 | Path | P14 Idaho to Northwest | -2250 | 3400 | -267.1103 | 0 | 28 | 575.2777
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 488.1789 | 139 | 0 | 554.1802 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 488.1789 | 139 | 0 | 554.1802
Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -281.5051 | 0 | 30 | 496.988 | Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -281.5051 | 0 | 30 | 496.988
Nomogram | FreqResponse-197 | -99999 | 0 | -46.1648 | 217 | 0 | 491.4 | Nomogram | FreqResponse-197 | -99999 | 0 | -46.1648 | 217 | 0 | 491.4
Path | P30 TOT 1A | -650 | 650 | 163.3843 | 6 | 1 | 330.7181 | Path | P30 TOT 1A | -650 | 650 | 163.3843 | 6 | 1 | 330.7181
Path | P76 Alturas Project | -300 | 300 | 62.7648 | 427 | 272 | 321.3039 | Path | P76 Alturas Project | -300 | 300 | 62.7648 | 427 | 272 | 321.3039
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 131.9233 | 30 | 0 | 310.9878 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 131.9233 | 30 | 0 | 310.9878
Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -402.5108 | 0 | 41 | 298.1084 | Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -402.5108 | 0 | 41 | 298.1084
Path | P65 Pacific DC Intertie (PDCI) | -3100 | 3220 | -40.6039 | 0 | 15 | 235.0141 | Path | P65 Pacific DC Intertie (PDCI) | -3100 | 3220 | -40.6039 | 0 | 15 | 235.0141
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 1.3125 | 178 | 330 | 224.0537 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 1.3125 | 178 | 330 | 224.0537
Path | P24 PG&E-Sierra | -150 | 160 | -1.5718 | 561 | 365 | 201.7337 | Path | P24 PG&E-Sierra | -150 | 160 | -1.5718 | 561 | 365 | 201.7337
Path | xy WA-BC East | -400 | 400 | 173.8523 | 426 | 10 | 122.6812 | Path | xy WA-BC East | -400 | 400 | 173.8523 | 426 | 10 | 122.6812
Nomogram | COI 2 | -99999 | 4560 | 1218.899 | 12 | 0 | 119.1528 | Nomogram | COI 2 | -99999 | 4560 | 1218.899 | 12 | 0 | 119.1528
Path | z CA PDCI South | -3100 | 2780 | -40.6039 | 8 | 2 | 74.4183 | Path | z CA PDCI South | -3100 | 2780 | -40.6039 | 8 | 2 | 74.4183
Nomogram | FreqResponse-128 | -99999 | 0 | -0.027854 | 10 | 0 | 70.68 | Nomogram | FreqResponse-128 | -99999 | 0 | -0.027854 | 10 | 0 | 70.68
Nomogram | FreqResponse-129 | -99999 | 0 | -0.024722 | 9 | 0 | 70.68 | Nomogram | FreqResponse-129 | -99999 | 0 | -0.024722 | 9 | 0 | 70.68
Nomogram | COI 1 | -99999 | 6763 | 2267.4371 | 4 | 0 | 49.6675 | Nomogram | COI 1 | -99999 | 6763 | 2267.4371 | 4 | 0 | 49.6675
Path | P77 Crystal-Allen | -950 | 950 | 572.8176 | 492 | 96 | 37.7549 | Path | P77 Crystal-Allen | -950 | 950 | 572.8176 | 492 | 96 | 37.7549
Nomogram | IPP DC | -99999 | 361 | 79.2693 | 20 | 0 | 28.8175 | Nomogram | IPP DC | -99999 | 361 | 79.2693 | 20 | 0 | 28.8175
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 163.944 | 0 | 13 | 28.0898 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 163.944 | 0 | 13 | 28.0898
Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 37.0324 | 1 | 0 | 27.9409 | Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 37.0324 | 1 | 0 | 27.9409
Path | P09 West of Broadview | -2573 | 2573 | 1908.0979 | 11 | 0 | 26.6794 | Path | P09 West of Broadview | -2573 | 2573 | 1908.0979 | 11 | 0 | 26.6794
Path | 2136-cont 0 | -796 | 796 | -54.1494 | 2 | 148 | 25.3733 | Path | 2136-cont 0 | -796 | 796 | -54.1494 | 2 | 148 | 25.3733
Path | P16 Idaho-Sierra | -360 | 500 | 88.7123 | 6 | 2 | 23.7465 | Path | P16 Idaho-Sierra | -360 | 500 | 88.7123 | 6 | 2 | 23.7465
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 188.777 | 3 | 0 | 20.869 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 188.777 | 3 | 0 | 20.869
Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 115.8733 | 22 | 0 | 20.3038 | Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 115.8733 | 22 | 0 | 20.3038
Path | 34576-cont 0 | -1139 | 1139 | 133.2656 | 33 | 0 | 16.5326 | Path | 34576-cont 0 | -1139 | 1139 | 133.2656 | 33 | 0 | 16.5326
Path | P03 Northwest-British Columbia | -3150 | 3000 | 561.0192 | 4 | 0 | 14.199 | Path | P03 Northwest-British Columbia | -3150 | 3000 | 561.0192 | 4 | 0 | 14.199
Path | P80 Montana Southeast | -600 | 600 | -159.8659 | 6 | 31 | 12.1902 | Path | P80 Montana Southeast | -600 | 600 | -159.8659 | 6 | 31 | 12.1902
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -15.1509 | 7 | 55 | 11.0209 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -15.1509 | 7 | 55 | 11.0209
Path | P19 Bridger West | -1250 | 2400 | 1662.7615 | 3 | 0 | 9.6792 | Path | P19 Bridger West | -1250 | 2400 | 1662.7615 | 3 | 0 | 9.6792
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 14.4117 | 0 | 50 | 7.8059 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 14.4117 | 0 | 50 | 7.8059
Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -96.5345 | 0 | 2 | 4.9572 | Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -96.5345 | 0 | 2 | 4.9572
Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -36.7571 | 4 | 2 | 1.705 | Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -36.7571 | 4 | 2 | 1.705

## 2030 1B
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Nomogram | CAISO_Plus_Renewables_Limit | -99999 | 2000 | -2331.5056 | 446 | 0 | 335445.44 | Nomogram | CAISO_Plus_Renewables_Limit | -99999 | 8000 | -2331.5056 | 446 | 0 | 335445.44
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1025.6712 | 0 | 5463 | 211179.8889 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1025.6712 | 0 | 5463 | 211179.8889
Path | z AZ Palo Verde East | -8010 | 8010 | 5378.0073 | 937 | 0 | 151204.6659 | Path | z AZ Palo Verde East | -8010 | 8010 | 5378.0073 | 937 | 0 | 151204.6659
Path | P45 SDG&E-CFE | -800 | 408 | 81.0347 | 1470 | 2 | 110986.6773 | Path | P45 SDG&E-CFE | -800 | 408 | 81.0347 | 1470 | 2 | 110986.6773
Nomogram | BPA_PreferredRate | 0 | 3500 | 752.7079 | 5878 | 0 | 78867.2894 | Nomogram | BPA_PreferredRate | 0 | 3500 | 752.7079 | 5878 | 0 | 78867.2894
Path | P01 Alberta-British Columbia | -1200 | 1000 | 208.5068 | 454 | 26 | 57003.2308 | Path | P01 Alberta-British Columbia | -1200 | 1000 | 208.5068 | 454 | 26 | 57003.2308
Nomogram | FreqResponse-3506 | -99999 | 0 | -51.1498 | 613 | 0 | 35699.4 | Nomogram | FreqResponse-3506 | -99999 | 0 | -51.1498 | 613 | 0 | 35699.4
Path | P39 TOT 5 | -1680 | 1680 | 256.1324 | 14 | 0 | 33068.7091 | Path | P39 TOT 5 | -1680 | 1680 | 256.1324 | 14 | 0 | 33068.7091
Path | P36 TOT 3 | -1680 | 1680 | 813.4036 | 51 | 0 | 30361.0702 | Path | P36 TOT 3 | -1680 | 1680 | 813.4036 | 51 | 0 | 30361.0702
Path | 3111-cont 0 | -1503 | 1503 | -160.2031 | 0 | 405 | 29932.9664 | Path | 3111-cont 0 | -1503 | 1503 | -160.2031 | 0 | 405 | 29932.9664
Path | P26 Northern-Southern California | -3000 | 4000 | 537.0852 | 92 | 583 | 12667.877 | Path | P26 Northern-Southern California | -3000 | 4000 | 537.0852 | 92 | 583 | 12667.877
Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -694.5372 | 0 | 276 | 11609.3847 | Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -694.5372 | 0 | 276 | 11609.3847
Path | P83 Montana Alberta Tie Line | -300 | 325 | 0.23056 | 274 | 286 | 11285.5185 | Path | P83 Montana Alberta Tie Line | -300 | 325 | 0.23056 | 274 | 286 | 11285.5185
Path | z WA North of Hanford | -2948 | 4100 | -696.7041 | 0 | 157 | 9848.8995 | Path | z WA North of Hanford | -2948 | 4100 | -696.7041 | 0 | 157 | 9848.8995
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 148.9407 | 378 | 0 | 8582.0364 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 148.9407 | 378 | 0 | 8582.0364
Path | P65 Pacific DC Intertie (PDCI) | -3100 | 3220 | -171.9205 | 0 | 138 | 6846.8956 | Path | P65 Pacific DC Intertie (PDCI) | -3100 | 3220 | -171.9205 | 0 | 138 | 6846.8956
Path | P31 TOT 2A | -690 | 690 | 79.8917 | 66 | 365 | 6576.5308 | Path | P31 TOT 2A | -690 | 690 | 79.8917 | 66 | 365 | 6576.5308
Path | xy AB-MT | -300 | 325 | 0.23056 | 84 | 85 | 6247.3612 | Path | xy AB-MT | -300 | 325 | 0.23056 | 84 | 85 | 6247.3612
Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -329.0137 | 0 | 234 | 4338.786 | Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -329.0137 | 0 | 234 | 4338.786
Path | P18 Montana-Idaho | -256 | 337 | 148.1543 | 133 | 0 | 4270.741 | Path | P18 Montana-Idaho | -256 | 337 | 148.1543 | 133 | 0 | 4270.741
Path | P35 TOT 2C | -580 | 600 | 53.1852 | 304 | 901 | 2480.9675 | Path | P35 TOT 2C | -580 | 600 | 53.1852 | 304 | 901 | 2480.9675
Path | P66 COI | -3675 | 4800 | 823.9644 | 0 | 138 | 1563.8779 | Path | P66 COI | -3675 | 4800 | 823.9644 | 0 | 138 | 1563.8779
Path | CAISO Zero Net Export | -99999 | 2000 | -2895.4267 | 44 | 0 | 1312.6845 | Path | CAISO Zero Net Export | -99999 | 8000 | -2895.4267 | 44 | 0 | 1312.6845
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 97.4567 | 516 | 0 | 1221.582 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 97.4567 | 516 | 0 | 1221.582
Nomogram | FreqResponse-25 | -99999 | 0 | -10.9233 | 597 | 0 | 1113.84 | Nomogram | FreqResponse-25 | -99999 | 0 | -10.9233 | 597 | 0 | 1113.84
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 494.9763 | 160 | 3 | 906.1098 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 494.9763 | 160 | 3 | 906.1098
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | -155.6186 | 12 | 0 | 648.9933 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | -155.6186 | 12 | 0 | 648.9933
Path | z CA PDCI South | -3100 | 2780 | -171.9205 | 16 | 7 | 604.3649 | Path | z CA PDCI South | -3100 | 2780 | -171.9205 | 16 | 7 | 604.3649
Path | P76 Alturas Project | -300 | 300 | 37.0872 | 492 | 472 | 524.6367 | Path | P76 Alturas Project | -300 | 300 | 37.0872 | 492 | 472 | 524.6367
Path | P14 Idaho to Northwest | -2250 | 3400 | -224.8718 | 0 | 25 | 494.5387 | Path | P14 Idaho to Northwest | -2250 | 3400 | -224.8718 | 0 | 25 | 494.5387
Nomogram | FreqResponse-1 | -99999 | 0 | -0.033934 | 293 | 0 | 403.26 | Nomogram | FreqResponse-1 | -99999 | 0 | -0.033934 | 293 | 0 | 403.26
Nomogram | FreqResponse-157 | -99999 | 0 | -12.9299 | 1777 | 0 | 380.25 | Nomogram | FreqResponse-157 | -99999 | 0 | -12.9299 | 1777 | 0 | 380.25
Path | P24 PG&E-Sierra | -150 | 160 | -4.3317 | 799 | 467 | 373.6945 | Path | P24 PG&E-Sierra | -150 | 160 | -4.3317 | 799 | 467 | 373.6945
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 0.4147 | 228 | 745 | 357.4189 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 0.4147 | 228 | 745 | 357.4189
Path | P30 TOT 1A | -650 | 650 | 159.791 | 8 | 1 | 325.9678 | Path | P30 TOT 1A | -650 | 650 | 159.791 | 8 | 1 | 325.9678
Path | xy WA-BC East | -400 | 400 | 159.9954 | 601 | 24 | 308.3264 | Path | xy WA-BC East | -400 | 400 | 159.9954 | 601 | 24 | 308.3264
Path | 34576-cont 0 | -1139 | 1139 | 299.4387 | 173 | 0 | 270.9897 | Path | 34576-cont 0 | -1139 | 1139 | 299.4387 | 173 | 0 | 270.9897
Nomogram | IPP DC | -99999 | 361 | 75.3729 | 229 | 0 | 200.0756 | Nomogram | IPP DC | -99999 | 361 | 75.3729 | 229 | 0 | 200.0756
Path | P77 Crystal-Allen | -950 | 950 | 24.0555 | 447 | 802 | 150.4487 | Path | P77 Crystal-Allen | -950 | 950 | 24.0555 | 447 | 802 | 150.4487
Path | P03 Northwest-British Columbia | -3150 | 3000 | 558.2139 | 20 | 0 | 131.343 | Path | P03 Northwest-British Columbia | -3150 | 3000 | 558.2139 | 20 | 0 | 131.343
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 171.3061 | 0 | 40 | 123.4777 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 171.3061 | 0 | 40 | 123.4777
Path | 2136-cont 0 | -796 | 796 | -218.404 | 6 | 416 | 102.914 | Path | 2136-cont 0 | -796 | 796 | -218.404 | 6 | 416 | 102.914
Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -99.7031 | 0 | 5 | 77.4692 | Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -99.7031 | 0 | 5 | 77.4692
Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 280.7808 | 41 | 0 | 76.3734 | Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 280.7808 | 41 | 0 | 76.3734
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -26.2088 | 3 | 276 | 60.5548 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -26.2088 | 3 | 276 | 60.5548
Nomogram | COI 2 | -99999 | 4560 | 880.4713 | 6 | 0 | 54.7063 | Nomogram | COI 2 | -99999 | 4560 | 880.4713 | 6 | 0 | 54.7063
Path | P09 West of Broadview | -2573 | 2573 | 1890.4594 | 22 | 0 | 46.1879 | Path | P09 West of Broadview | -2573 | 2573 | 1890.4594 | 22 | 0 | 46.1879
Path | P16 Idaho-Sierra | -360 | 500 | 72.8552 | 3 | 13 | 36.7193 | Path | P16 Idaho-Sierra | -360 | 500 | 72.8552 | 3 | 13 | 36.7193
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 7.3449 | 0 | 151 | 28.4106 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 7.3449 | 0 | 151 | 28.4106
Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 318.3991 | 4 | 0 | 23.2488 | Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 318.3991 | 4 | 0 | 23.2488
Path | P80 Montana Southeast | -600 | 600 | -139.7447 | 7 | 28 | 21.801 | Path | P80 Montana Southeast | -600 | 600 | -139.7447 | 7 | 28 | 21.801
Path | P19 Bridger West | -1250 | 2400 | 1636.9814 | 4 | 0 | 16.5192 | Path | P19 Bridger West | -1250 | 2400 | 1636.9814 | 4 | 0 | 16.5192
Nomogram | COI 1 | -99999 | 6763 | 1929.1335 | 1 | 0 | 15.8322 | Nomogram | COI 1 | -99999 | 6763 | 1929.1335 | 1 | 0 | 15.8322
Path | P15 Midway-LosBanos | -3265 | 5400 | 995.8244 | 0 | 3 | 12.2046 | Path | P15 Midway-LosBanos | -3265 | 5400 | 995.8244 | 0 | 3 | 12.2046
Path | P11 West of Crossover | -2598 | 2598 | 1922.884 | 6 | 0 | 5.952 | Path | P11 West of Crossover | -2598 | 2598 | 1922.884 | 6 | 0 | 5.952
Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -199.7461 | 1 | 4 | 2.6539 | Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -199.7461 | 1 | 4 | 2.6539

## 2030 2
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | -234.594 | 4227 | 4533 | 534313.5588 | Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | -234.594 | 1 | 1523 | 534313.5588
Path | z AZ Palo Verde East | -8010 | 8010 | 5252.6696 | 8760 | 0 | 258268.9291 | Path | z AZ Palo Verde East | -8010 | 8010 | 5252.6696 | 1116 | 0 | 258268.9291
Path | P36 TOT 3 | -1680 | 1680 | 1309.6525 | 8737 | 23 | 239526.1522 | Path | P36 TOT 3 | -1680 | 1680 | 1309.6525 | 3065 | 0 | 239526.1522
Path | P19 Bridger West | -1250 | 2400 | 1839.6325 | 8760 | 0 | 228507.582 | Path | P19 Bridger West | -1250 | 2400 | 1839.6325 | 1892 | 0 | 228507.582
Path | CAISO Zero Net Export | -99999 | 2000 | -3832.7227 | 1689 | 7071 | 169988.3181 | Path | CAISO Zero Net Export | -99999 | 8000 | -3832.7227 | 238 | 0 | 169988.3181
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1038.5527 | 8760 | 0 | 102235.0816 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1038.5527 | 0 | 6038 | 102235.0816
Path | P45 SDG&E-CFE | -800 | 408 | 45.2815 | 2674 | 746 | 82254.5201 | Path | P45 SDG&E-CFE | -800 | 408 | 45.2815 | 725 | 1 | 82254.5201
Path | P38 TOT 4B | -880 | 880 | 565.1241 | 8747 | 13 | 81250.6297 | Path | P38 TOT 4B | -880 | 880 | 565.1241 | 877 | 0 | 81250.6297
Nomogram | BPA_PreferredRate | 0 | 3500 | 689.8275 | 5772 | 0 | 77337.263 | Nomogram | BPA_PreferredRate | 0 | 3500 | 689.8275 | 5345 | 0 | 77337.263
Path | P01 Alberta-British Columbia | -1200 | 1000 | 230.9168 | 6714 | 2045 | 67370.8314 | Path | P01 Alberta-British Columbia | -1200 | 1000 | 230.9168 | 597 | 64 | 67370.8314
Path | 3111-cont 0 | -1503 | 1503 | -241.8677 | 4225 | 4535 | 43496.1632 | Path | 3111-cont 0 | -1503 | 1503 | -241.8677 | 0 | 421 | 43496.1632
Path | 3111-cont 0 | -1503 | 1503 | -241.8677 | 4225 | 4535 | 43496.1632 | <duplicate of above row>
Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 320.7782 | 7288 | 1472 | 41897.4884 | Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 320.7782 | 84 | 0 | 41897.4884
Path | z WA North of Hanford | -2948 | 4100 | -728.4513 | 2034 | 6726 | 38344.978 | Path | z WA North of Hanford | -2948 | 4100 | -728.4513 | 0 | 261 | 38344.978
Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -892.9226 | 3153 | 5607 | 25291.8452 | Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -892.9226 | 0 | 524 | 25291.8452
Path | P09 West of Broadview | -2573 | 2573 | 2082.2443 | 8760 | 0 | 21748.7251 | Path | P09 West of Broadview | -2573 | 2573 | 2082.2443 | 917 | 0 | 21748.7251
Path | z Aeolus West | -2670 | 2670 | 731.7013 | 6769 | 1991 | 19869.7582 | Path | z Aeolus West | -2670 | 2670 | 731.7013 | 113 | 0 | 19869.7582
Path | P83 Montana Alberta Tie Line | -300 | 325 | -61.807 | 3432 | 5327 | 19630.1644 | Path | P83 Montana Alberta Tie Line | -300 | 325 | -61.807 | 278 | 729 | 19630.1644
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 49.3184 | 4281 | 4478 | 16653.3525 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 49.3184 | 572 | 0 | 16653.3525
Path | P80 Montana Southeast | -600 | 600 | -241.9642 | 1917 | 6843 | 12249.8988 | Path | P80 Montana Southeast | -600 | 600 | -241.9642 | 50 | 1184 | 12249.8988
Path | P65 Pacific DC Intertie (PDCI) | -3100 | 3220 | -209.9931 | 4332 | 3905 | 11355.145 | Path | P65 Pacific DC Intertie (PDCI) | -3100 | 3220 | -209.9931 | 0 | 212 | 11355.145
Path | P26 Northern-Southern California | -3000 | 4000 | 236.5332 | 5089 | 3671 | 8726.953 | Path | P26 Northern-Southern California | -3000 | 4000 | 236.5332 | 173 | 530 | 8726.953
Path | P31 TOT 2A | -690 | 690 | -37.7856 | 4137 | 4623 | 8472.1954 | Path | P31 TOT 2A | -690 | 690 | -37.7856 | 472 | 856 | 8472.1954
Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -144.9133 | 3305 | 5455 | 7501.762 | Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -144.9133 | 43 | 248 | 7501.762
Path | P33 Bonanza West | -785 | 785 | 277.433 | 7409 | 1351 | 7380.0158 | Path | P33 Bonanza West | -785 | 785 | 277.433 | 277 | 0 | 7380.0158
Path | P35 TOT 2C | -580 | 600 | 126.5008 | 5424 | 3335 | 5905.8597 | Path | P35 TOT 2C | -580 | 600 | 126.5008 | 1630 | 1032 | 5905.8597
Path | P66 COI | -3675 | 4800 | 936.4024 | 6367 | 2393 | 4636.5564 | Path | P66 COI | -3675 | 4800 | 936.4024 | 0 | 187 | 4636.5564
Nomogram | Path 22 | -99999 | 3113 | 1238.9872 | 7519 | 1241 | 4547.1186 | Nomogram | Path 22 | -99999 | 3113 | 1238.9872 | 228 | 0 | 4547.1186
Path | P18 Montana-Idaho | -256 | 337 | 139.3186 | 8170 | 590 | 3908.065 | Path | P18 Montana-Idaho | -256 | 337 | 139.3186 | 240 | 0 | 3908.065
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 102.7119 | 7436 | 1324 | 3278.7844 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 102.7119 | 1245 | 0 | 3278.7844
Path | xy AB-MT | -300 | 325 | -61.807 | 3432 | 5327 | 2840.8323 | Path | xy AB-MT | -300 | 325 | -61.807 | 101 | 325 | 2840.8323
Path | P39 TOT 5 | -1680 | 1680 | 469.3662 | 6558 | 2202 | 2434.9954 | Path | P39 TOT 5 | -1680 | 1680 | 469.3662 | 259 | 0 | 2434.9954
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 366.805 | 6534 | 2226 | 2172.4372 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 366.805 | 131 | 20 | 2172.4372
Path | P22 Southwest of Four Corners | -2325 | 2325 | 918.0429 | 7520 | 1240 | 1653.3586 | Path | P22 Southwest of Four Corners | -2325 | 2325 | 918.0429 | 130 | 0 | 1653.3586
Path | xy WA-BC East | -400 | 400 | 215.8877 | 7440 | 1320 | 1196.0516 | Path | xy WA-BC East | -400 | 400 | 215.8877 | 1374 | 20 | 1196.0516
Path | z CA PDCI South | -3100 | 2780 | -209.9931 | 4332 | 3905 | 1108.264 | Path | z CA PDCI South | -3100 | 2780 | -209.9931 | 16 | 11 | 1108.264
Nomogram | COI 2 | -99999 | 4560 | 1040.2494 | 6391 | 2369 | 816.2674 | Nomogram | COI 2 | -99999 | 4560 | 1040.2494 | 85 | 0 | 816.2674
Path | P76 Alturas Project | -300 | 300 | 84.4268 | 5753 | 3007 | 801.0012 | Path | P76 Alturas Project | -300 | 300 | 84.4268 | 1050 | 476 | 801.0012
Path | P30 TOT 1A | -650 | 650 | 101.9873 | 5569 | 3191 | 781.7433 | Path | P30 TOT 1A | -650 | 650 | 101.9873 | 109 | 3 | 781.7433
Path | P24 PG&E-Sierra | -150 | 160 | 27.4756 | 5178 | 3582 | 725.7998 | Path | P24 PG&E-Sierra | -150 | 160 | 27.4756 | 1435 | 630 | 725.7998
Path | P14 Idaho to Northwest | -2250 | 3400 | -53.1731 | 4471 | 4289 | 716.6453 | Path | P14 Idaho to Northwest | -2250 | 3400 | -53.1731 | 0 | 27 | 716.6453
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 0.64206 | 4863 | 3897 | 576.5733 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 0.64206 | 456 | 1026 | 576.5733
Path | xy COI plus PDCI | -6455 | 7900 | 726.4093 | 6217 | 2543 | 569.9184 | Path | xy COI plus PDCI | -6455 | 7900 | 726.4093 | 0 | 13 | 569.9184
Path | 34576-cont 0 | -1139 | 1139 | 243.862 | 5323 | 3437 | 445.3877 | Path | 34576-cont 0 | -1139 | 1139 | 243.862 | 180 | 0 | 445.3877
Nomogram | IPP DC | -99999 | 361 | 41.7276 | 6530 | 2059 | 353.463 | Nomogram | IPP DC | -99999 | 361 | 41.7276 | 310 | 0 | 353.463
Path | P77 Crystal-Allen | -950 | 950 | -225.8618 | 3366 | 5393 | 316.0498 | Path | P77 Crystal-Allen | -950 | 950 | -225.8618 | 533 | 1762 | 316.0498
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 188.4151 | 7658 | 1102 | 276.0834 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 188.4151 | 0 | 76 | 276.0834
Path | 2136-cont 0 | -796 | 796 | -198.5806 | 3432 | 5328 | 271.1494 | Path | 2136-cont 0 | -796 | 796 | -198.5806 | 3 | 689 | 271.1494
Path | P03 Northwest-British Columbia | -3150 | 3000 | 544.4392 | 5854 | 2906 | 244.581 | Path | P03 Northwest-British Columbia | -3150 | 3000 | 544.4392 | 31 | 0 | 244.581
Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 217.6685 | 5310 | 3450 | 137.2449 | Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 217.6685 | 42 | 0 | 137.2449
Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 204.9521 | 7149 | 1611 | 111.4696 | Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 204.9521 | 1 | 0 | 111.4696
Nomogram | COI 1 | -99999 | 6763 | 2088.9433 | 7101 | 1659 | 104.2043 | Nomogram | COI 1 | -99999 | 6763 | 2088.9433 | 8 | 0 | 104.2043
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -25.5371 | 1426 | 7334 | 93.0494 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -25.5371 | 2 | 447 | 93.0494
Contingency | 2853-CA230kV S LAM2 L-2 SCE Serrano-Lewis | -1012 | 1012 | -552.6433 | 0 | 8760 | 84.9787 | Contingency | 2853-CA230kV S LAM2 L-2 SCE Serrano-Lewis | -1012 | 1012 | -552.6433 | 0 | 2 | 84.9787
Path | P16 Idaho-Sierra | -360 | 500 | 95.5954 | 6341 | 2419 | 79.2677 | Path | P16 Idaho-Sierra | -360 | 500 | 95.5954 | 19 | 1 | 79.2677
Path | P15 Midway-LosBanos | -3265 | 5400 | 1271.1613 | 5510 | 3250 | 72.1108 | Path | P15 Midway-LosBanos | -3265 | 5400 | 1271.1613 | 0 | 11 | 72.1108
Path | P49 East of Colorado River (EOR) | -10200 | 9900 | 4792.2881 | 8130 | 630 | 69.7851 | Path | P49 East of Colorado River (EOR) | -10200 | 9900 | 4792.2881 | 5 | 0 | 69.7851
Path | P11 West of Crossover | -2598 | 2598 | 1985.7772 | 8760 | 0 | 65.3085 | Path | P11 West of Crossover | -2598 | 2598 | 1985.7772 | 51 | 0 | 65.3085
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 22.1961 | 6233 | 2526 | 58.966 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 22.1961 | 1 | 165 | 58.966
Nomogram | CA Path15 N2S-MidwayGen | -99999 | 3265 | -1271.1613 | 3250 | 5510 | 49.4648 | Nomogram | CA Path15 N2S-MidwayGen | -99999 | 3265 | -1271.1613 | 9 | 0 | 49.4648
Path | P27 Intermountain Power Project DC Line | -1400 | 2400 | 39.4186 | 5012 | 3225 | 36.432 | Path | P27 Intermountain Power Project DC Line | -1400 | 2400 | 39.4186 | 3 | 0 | 36.432
Path | P40 TOT 7 | -890 | 890 | 373.5464 | 8412 | 348 | 35.7282 | Path | P40 TOT 7 | -890 | 890 | 373.5464 | 3 | 0 | 35.7282
Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -172.387 | 3445 | 5315 | 11.7283 | Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -172.387 | 0 | 36 | 11.7283
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | -451.9495 | 3958 | 4802 | 7.1518 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | -451.9495 | 1 | 0 | 7.1518
Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -111.6347 | 681 | 8079 | 3.9505 | Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -111.6347 | 0 | 2 | 3.9505
Contingency | 3563-PG&E LCR NCNB LV Cat C | -120 | 120 | 46.6696 | 8127 | 633 | 0.2172 | Contingency | 3563-PG&E LCR NCNB LV Cat C | -120 | 120 | 46.6696 | 3 | 0 | 0.2172

## 2030 3
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Path | z Aeolus West | -2670 | 2670 | 1210.0857 | 1322 | 0 | 604683.9157 | Path | z Aeolus West | -2670 | 2670 | 1210.0857 | 1322 | 0 | 604683.9157
Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | -238.8528 | 1 | 1536 | 482631.4023 | Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | -238.8528 | 1 | 1536 | 482631.4023
Path | z Aeolus South | -1700 | 1700 | -589.0394 | 0 | 1113 | 380239.7099 | Path | z Aeolus South | -1700 | 1700 | -589.0394 | 0 | 1113 | 380239.7099
Path | P37 TOT 4A | -99999 | 1025 | -654.8052 | 0 | 1045 | 326656.96 | Path | P37 TOT 4A | -1775 | 1775 | -654.8052 | 0 | 1045 | 326656.96
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1024.2421 | 0 | 6192 | 199395.4518 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1024.2421 | 0 | 6192 | 199395.4518
Path | z AZ Palo Verde East | -8010 | 8010 | 5446.2366 | 923 | 0 | 176954.7172 | Path | z AZ Palo Verde East | -8010 | 8010 | 5446.2366 | 923 | 0 | 176954.7172
Path | P19 Bridger West | -1250 | 2400 | 2639.5331 | 721 | 0 | 116684.9611 | Path | P19 Bridger West | -2300 | 4100 | 2639.5331 | 721 | 0 | 116684.9611
Path | P36 TOT 3 | -1680 | 1680 | 1201.6451 | 2024 | 0 | 94664.6182 | Path | P36 TOT 3 | -1680 | 1680 | 1201.6451 | 2024 | 0 | 94664.6182
Nomogram | BPA_PreferredRate | 0 | 3500 | 671.3365 | 5175 | 0 | 68777.7487 | Nomogram | BPA_PreferredRate | 0 | 3500 | 671.3365 | 5175 | 0 | 68777.7487
Path | P01 Alberta-British Columbia | -1200 | 1000 | 244.3868 | 638 | 37 | 49934.4686 | Path | P01 Alberta-British Columbia | -1200 | 1000 | 244.3868 | 638 | 37 | 49934.4686
Path | z WA North of Hanford | -2948 | 4100 | -704.7699 | 0 | 186 | 34934.0683 | Path | z WA North of Hanford | -2948 | 4100 | -704.7699 | 0 | 186 | 34934.0683
Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 336.6519 | 76 | 0 | 34362.3807 | Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 336.6519 | 76 | 0 | 34362.3807
Path | P45 SDG&E-CFE | -800 | 408 | 34.9373 | 495 | 6 | 31614.9211 | Path | P45 SDG&E-CFE | -800 | 408 | 34.9373 | 495 | 6 | 31614.9211
Path | CAISO Zero Net Export | -99999 | 2000 | -5223.4786 | 45 | 0 | 27998.9477 | Path | CAISO Zero Net Export | -99999 | 8000 | -5223.4786 | 45 | 0 | 27998.9477
Path | P83 Montana Alberta Tie Line | -300 | 325 | -50.6762 | 341 | 1174 | 16590.9997 | Path | P83 Montana Alberta Tie Line | -300 | 325 | -50.6762 | 341 | 1174 | 16590.9997
Path | P26 Northern-Southern California | -3000 | 4000 | 102.6987 | 111 | 862 | 12430.008 | Path | P26 Northern-Southern California | -3000 | 4000 | 102.6987 | 111 | 862 | 12430.008
Path | P31 TOT 2A | -690 | 690 | -164.2104 | 41 | 798 | 9163.6382 | Path | P31 TOT 2A | -690 | 690 | -164.2104 | 41 | 798 | 9163.6382
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -52.6429 | 286 | 0 | 7677.9216 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -52.6429 | 286 | 0 | 7677.9216
Path | z CA PDCI South | -3100 | 2780 | -151.0099 | 6 | 140 | 7228.5847 | Path | z CA PDCI South | -3100 | 2780 | -151.0099 | 6 | 140 | 7228.5847
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 114.066 | 1747 | 0 | 7048.0924 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 114.066 | 1747 | 0 | 7048.0924
Path | P35 TOT 2C | -580 | 600 | 170.3472 | 1716 | 669 | 4665.7163 | Path | P35 TOT 2C | -580 | 600 | 170.3472 | 1716 | 669 | 4665.7163
Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -133.6624 | 23 | 147 | 4463.204 | Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -133.6624 | 23 | 147 | 4463.204
Path | P66 COI | -3675 | 4800 | 1242.8863 | 5 | 104 | 3061.5095 | Path | P66 COI | -3675 | 4800 | 1242.8863 | 5 | 104 | 3061.5095
Path | P09 West of Broadview | -2573 | 2573 | 2034.5299 | 271 | 0 | 2771.3757 | Path | P09 West of Broadview | -2573 | 2573 | 2034.5299 | 271 | 0 | 2771.3757
Nomogram | COI 2 | -99999 | 4560 | 1365.3978 | 243 | 0 | 2635.5523 | Nomogram | COI 2 | -99999 | 4560 | 1365.3978 | 243 | 0 | 2635.5523
Path | P18 Montana-Idaho | -256 | 337 | 92.6444 | 162 | 0 | 2557.3892 | Path | P18 Montana-Idaho | -256 | 337 | 92.6444 | 162 | 0 | 2557.3892
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 269.3402 | 101 | 15 | 2392.3274 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 269.3402 | 101 | 15 | 2392.3274
Path | P38 TOT 4B | -880 | 880 | 536.2333 | 153 | 0 | 2188.3629 | Path | P38 TOT 4B | -880 | 880 | 536.2333 | 153 | 0 | 2188.3629
Path | P49 East of Colorado River (EOR) | -10200 | 9900 | 5695.9324 | 51 | 0 | 1612.7001 | Path | P49 East of Colorado River (EOR) | -10200 | 9900 | 5695.9324 | 51 | 0 | 1612.7001
Nomogram | Path 22 | -99999 | 3113 | 1214.7472 | 72 | 0 | 1321.3533 | Nomogram | Path 22 | -99999 | 3113 | 1214.7472 | 72 | 0 | 1321.3533
Path | P39 TOT 5 | -1680 | 1680 | 712.5524 | 163 | 0 | 1280.7967 | Path | P39 TOT 5 | -1680 | 1680 | 712.5524 | 163 | 0 | 1280.7967
Path | xy WA-BC East | -400 | 400 | 219.2834 | 1574 | 25 | 1232.6512 | Path | xy WA-BC East | -400 | 400 | 219.2834 | 1574 | 25 | 1232.6512
Path | P22 Southwest of Four Corners | -2325 | 2325 | 913.6561 | 96 | 0 | 1209.7975 | Path | P22 Southwest of Four Corners | -2325 | 2325 | 913.6561 | 96 | 0 | 1209.7975
Path | xy COI plus PDCI | -6455 | 7900 | 1091.8764 | 0 | 11 | 1209.4346 | Path | xy COI plus PDCI | -6455 | 7900 | 1091.8764 | 0 | 11 | 1209.4346
Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -806.335 | 0 | 54 | 1193.154 | Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -806.335 | 0 | 54 | 1193.154
Path | P76 Alturas Project | -300 | 300 | 103.0911 | 857 | 556 | 787.1478 | Path | P76 Alturas Project | -300 | 300 | 103.0911 | 857 | 556 | 787.1478
Path | P24 PG&E-Sierra | -150 | 160 | 44.6848 | 1407 | 518 | 688.4541 | Path | P24 PG&E-Sierra | -150 | 160 | 44.6848 | 1407 | 518 | 688.4541
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 0.79436 | 359 | 943 | 512.8123 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 0.79436 | 359 | 943 | 512.8123
Path | P80 Montana Southeast | -600 | 600 | -201.7836 | 29 | 212 | 512.1486 | Path | P80 Montana Southeast | -600 | 600 | -201.7836 | 29 | 212 | 512.1486
Path | xy AB-MT | -300 | 325 | -50.6762 | 76 | 127 | 479.8707 | Path | xy AB-MT | -300 | 325 | -50.6762 | 76 | 127 | 479.8707
Nomogram | IPP DC | -99999 | 361 | 27.8527 | 243 | 0 | 333.5203 | Nomogram | IPP DC | -99999 | 361 | 27.8527 | 243 | 0 | 333.5203
Path | P14 Idaho to Northwest | -2250 | 3400 | 583.0814 | 1 | 18 | 284.7149 | Path | P14 Idaho to Northwest | -2250 | 3400 | 583.0814 | 1 | 18 | 284.7149
Path | P77 Crystal-Allen | -950 | 950 | 181.7441 | 1110 | 1048 | 216.9829 | Path | P77 Crystal-Allen | -950 | 950 | 181.7441 | 1110 | 1048 | 216.9829
Nomogram | COI 1 | -99999 | 6763 | 2414.099 | 8 | 0 | 139.8183 | Nomogram | COI 1 | -99999 | 6763 | 2414.099 | 8 | 0 | 139.8183
Path | P03 Northwest-British Columbia | -3150 | 3000 | 531.3418 | 19 | 0 | 127.215 | Path | P03 Northwest-British Columbia | -3150 | 3000 | 531.3418 | 19 | 0 | 127.215
Nomogram | CA Path15 N2S-MidwayGen | -99999 | 3265 | -1147.9626 | 13 | 0 | 111.6989 | Nomogram | CA Path15 N2S-MidwayGen | -99999 | 3265 | -1147.9626 | 13 | 0 | 111.6989
Path | P40 TOT 7 | -890 | 890 | 400.3743 | 11 | 0 | 99.308 | Path | P40 TOT 7 | -890 | 890 | 400.3743 | 11 | 0 | 99.308
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 210.1223 | 1 | 21 | 78.2134 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 210.1223 | 1 | 21 | 78.2134
Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 338.7004 | 20 | 0 | 65.0175 | Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 338.7004 | 20 | 0 | 65.0175
Path | P30 TOT 1A | -650 | 650 | -85.6787 | 5 | 3 | 62.3942 | Path | P30 TOT 1A | -650 | 650 | -85.6787 | 5 | 3 | 62.3942
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 23.7861 | 3 | 130 | 52.7214 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 23.7861 | 3 | 130 | 52.7214
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -18.5134 | 4 | 248 | 52.6734 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -18.5134 | 4 | 248 | 52.6734
Path | P15 Midway-LosBanos | -3265 | 5400 | 1147.9626 | 0 | 5 | 40.1889 | Path | P15 Midway-LosBanos | -3265 | 5400 | 1147.9626 | 0 | 5 | 40.1889
Path | P16 Idaho-Sierra | -360 | 500 | 111.4995 | 9 | 2 | 39.1722 | Path | P16 Idaho-Sierra | -360 | 500 | 111.4995 | 9 | 2 | 39.1722
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | -567.7607 | 5 | 0 | 24.2224 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | -567.7607 | 5 | 0 | 24.2224
Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 38.5474 | 1 | 0 | 20.6198 | Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 38.5474 | 1 | 0 | 20.6198
Contingency | 2112-N-2 SCE PaloVerde-ColoradoRiver Delaney - ColoradoRiver 500 kV | -2598 | 2598 | 1088.5076 | 1 | 0 | 13.7668 | Contingency | 2112-N-2 SCE PaloVerde-ColoradoRiver Delaney - ColoradoRiver 500 kV | -2598 | 2598 | 1088.5076 | 1 | 0 | 13.7668
Path | P11 West of Crossover | -2598 | 2598 | 1954.5623 | 16 | 0 | 13.5018 | Path | P11 West of Crossover | -2598 | 2598 | 1954.5623 | 16 | 0 | 13.5018
Path | P46 West of Colorado River (WOR) | -11200 | 11800 | 5609.8462 | 1 | 0 | 10.7852 | Path | P46 West of Colorado River (WOR) | -11200 | 11800 | 5609.8462 | 1 | 0 | 10.7852
Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -303.7631 | 0 | 23 | 6.8727 | Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -303.7631 | 0 | 23 | 6.8727
Contingency | 2363-CA500kV S1 L-1 SCE Mohave-Lugo | -2598 | 2598 | -53.845 | 0 | 1 | 4.5803 | Contingency | 2363-CA500kV S1 L-1 SCE Mohave-Lugo | -2598 | 2598 | -53.845 | 0 | 1 | 4.5803
Contingency | 3563-PG&E LCR NCNB LV Cat C | -120 | 120 | 46.6557 | 2 | 0 | 0.0846 | Contingency | 3563-PG&E LCR NCNB LV Cat C | -120 | 120 | 46.6557 | 2 | 0 | 0.0846
[8 empty] | Path | 3111-cont 0 | -1503 | 1503 | -244.2306 | 0 | 223 | 23723.9968
[8 empty] | Path | 34576-cont 0 | -1139 | 1139 | 368.5075 | 135 | 0 | 353.7381
[8 empty] | Path | 2136-cont 0 | -796 | 796 | -333.5702 | 0 | 756 | 280.4857

## 2030 1 CPP
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Nomogram | CAISO_Plus_Renewables_Limit | -99999 | 2000 | -2835.8676 | 1275 | 0 | 298571.636 | Nomogram | CAISO_Plus_Renewables_Limit | -99999 | 2000 | -2835.8676 | 1275 | 0 | 298571.636
Path | P45 SDG&E-CFE | -800 | 408 | 82.1579 | 1273 | 2 | 201080.6274 | Path | P45 SDG&E-CFE | -800 | 408 | 82.1579 | 1273 | 2 | 201080.6274
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1025.8672 | 0 | 5412 | 73812.4159 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1025.8672 | 0 | 5412 | 73812.4159
Path | CAISO Zero Net Export | -99999 | 2000 | -3604.2079 | 374 | 0 | 72146.9092 | Path | CAISO Zero Net Export | -99999 | 2000 | -3604.2079 | 374 | 0 | 72146.9092
Path | z AZ Palo Verde East | -8010 | 8010 | 5657.6983 | 603 | 0 | 43421.5612 | Path | z AZ Palo Verde East | -8010 | 8010 | 5657.6983 | 603 | 0 | 43421.5612
Path | P01 Alberta-British Columbia | -1200 | 1000 | 264.4791 | 474 | 2 | 40433.7396 | Path | P01 Alberta-British Columbia | -1200 | 1000 | 264.4791 | 474 | 2 | 40433.7396
Nomogram | BPA_PreferredRate | 0 | 3500 | 711.1105 | 5353 | 0 | 39891.065 | Nomogram | BPA_PreferredRate | 0 | 3500 | 711.1105 | 5353 | 0 | 39891.065
Nomogram | FreqResponse-3506 | -99999 | 0 | -45.205 | 838 | 0 | 34984.65 | Nomogram | FreqResponse-3506 | -99999 | 0 | -45.205 | 838 | 0 | 34984.65
Path | P39 TOT 5 | -1680 | 1680 | 75.9904 | 13 | 0 | 33394.6721 | Path | P39 TOT 5 | -1680 | 1680 | 75.9904 | 13 | 0 | 33394.6721
Path | P36 TOT 3 | -1680 | 1680 | 900.2297 | 64 | 0 | 30070.5859 | Path | P36 TOT 3 | -1680 | 1680 | 900.2297 | 64 | 0 | 30070.5859
Path | P83 Montana Alberta Tie Line | -300 | 325 | 18.2203 | 198 | 78 | 6569.512 | Path | P83 Montana Alberta Tie Line | -300 | 325 | 18.2203 | 198 | 78 | 6569.512
Path | xy AB-MT | -300 | 325 | 18.2203 | 173 | 71 | 4473.5176 | Path | xy AB-MT | -300 | 325 | 18.2203 | 173 | 71 | 4473.5176
Path | P18 Montana-Idaho | -256 | 337 | 175.2748 | 188 | 0 | 4352.7304 | Path | P18 Montana-Idaho | -256 | 337 | 175.2748 | 188 | 0 | 4352.7304
Path | P31 TOT 2A | -690 | 690 | 24.0671 | 29 | 135 | 4124.3784 | Path | P31 TOT 2A | -690 | 690 | 24.0671 | 29 | 135 | 4124.3784
Path | P26 Northern-Southern California | -3000 | 4000 | 903.004 | 115 | 295 | 3650.726 | Path | P26 Northern-Southern California | -3000 | 4000 | 903.004 | 115 | 295 | 3650.726
Path | P15 Midway-LosBanos | -3265 | 5400 | 871.7367 | 193 | 3 | 3558.8067 | Path | P15 Midway-LosBanos | -3265 | 5400 | 871.7367 | 193 | 3 | 3558.8067
Path | 3111-cont 0 | -1503 | 1503 | -45.9469 | 0 | 145 | 3027.4989 | Path | 3111-cont 0 | -1503 | 1503 | -45.9469 | 0 | 145 | 3027.4989
Path | z WA North of Hanford | -2948 | 4100 | -651.0163 | 0 | 46 | 1438.624 | Path | z WA North of Hanford | -2948 | 4100 | -651.0163 | 0 | 46 | 1438.624
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 90.8029 | 418 | 0 | 1183.1856 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 90.8029 | 418 | 0 | 1183.1856
Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -435.4512 | 0 | 156 | 1060.445 | Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -435.4512 | 0 | 156 | 1060.445
Path | P35 TOT 2C | -580 | 600 | 77.8707 | 288 | 539 | 830.6135 | Path | P35 TOT 2C | -580 | 600 | 77.8707 | 288 | 539 | 830.6135
Path | P14 Idaho to Northwest | -2250 | 3400 | -570.1825 | 0 | 38 | 812.6258 | Path | P14 Idaho to Northwest | -2250 | 3400 | -570.1825 | 0 | 38 | 812.6258
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 541.5105 | 180 | 0 | 782.9472 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 541.5105 | 180 | 0 | 782.9472
Nomogram | FreqResponse-25 | -99999 | 0 | -5.3432 | 1286 | 0 | 556.92 | Nomogram | FreqResponse-25 | -99999 | 0 | -5.3432 | 1286 | 0 | 556.92
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 144.0198 | 33 | 0 | 352.6884 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 144.0198 | 33 | 0 | 352.6884
Path | P76 Alturas Project | -300 | 300 | 87.0688 | 565 | 206 | 348.642 | Path | P76 Alturas Project | -300 | 300 | 87.0688 | 565 | 206 | 348.642
Path | P30 TOT 1A | -650 | 650 | 172.424 | 11 | 1 | 346.6671 | Path | P30 TOT 1A | -650 | 650 | 172.424 | 11 | 1 | 346.6671
Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -400.7694 | 0 | 50 | 342.7697 | Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -400.7694 | 0 | 50 | 342.7697
Path | P65 Pacific DC Intertie (PDCI) | -3100 | 3220 | -38.4061 | 0 | 7 | 276.5014 | Path | P65 Pacific DC Intertie (PDCI) | -3100 | 3220 | -38.4061 | 0 | 7 | 276.5014
Path | P24 PG&E-Sierra | -150 | 160 | 10.6968 | 745 | 281 | 221.9591 | Path | P24 PG&E-Sierra | -150 | 160 | 10.6968 | 745 | 281 | 221.9591
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 1.4341 | 176 | 320 | 217.4131 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 1.4341 | 176 | 320 | 217.4131
Nomogram | FreqResponse-1 | -99999 | 0 | -0.020819 | 222 | 0 | 217.14 | Nomogram | FreqResponse-1 | -99999 | 0 | -0.020819 | 222 | 0 | 217.14
Path | xy WA-BC East | -400 | 400 | 144.4925 | 411 | 32 | 127.1596 | Path | xy WA-BC East | -400 | 400 | 144.4925 | 411 | 32 | 127.1596
Path | z CA PDCI South | -3100 | 2780 | -38.4061 | 10 | 3 | 122.1247 | Path | z CA PDCI South | -3100 | 2780 | -38.4061 | 10 | 3 | 122.1247
Path | 34576-cont 0 | -1139 | 1139 | 302.8589 | 75 | 0 | 66.3547 | Path | 34576-cont 0 | -1139 | 1139 | 302.8589 | 75 | 0 | 66.3547
Nomogram | COI 1 | -99999 | 6763 | 2204.3831 | 3 | 0 | 55.3011 | Nomogram | COI 1 | -99999 | 6763 | 2204.3831 | 3 | 0 | 55.3011
Path | 2136-cont 0 | -796 | 796 | -220.701 | 2 | 261 | 46.3678 | Path | 2136-cont 0 | -796 | 796 | -220.701 | 2 | 261 | 46.3678
Path | P77 Crystal-Allen | -950 | 950 | 400.8398 | 391 | 266 | 41.6404 | Path | P77 Crystal-Allen | -950 | 950 | 400.8398 | 391 | 266 | 41.6404
Nomogram | COI 2 | -99999 | 4560 | 1155.8452 | 6 | 0 | 38.3542 | Nomogram | COI 2 | -99999 | 4560 | 1155.8452 | 6 | 0 | 38.3542
Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 284.9075 | 33 | 0 | 35.1678 | Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 284.9075 | 33 | 0 | 35.1678
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 149.5213 | 0 | 15 | 34.1676 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 149.5213 | 0 | 15 | 34.1676
Nomogram | IPP DC | -99999 | 361 | 80.2717 | 45 | 0 | 26.2862 | Nomogram | IPP DC | -99999 | 361 | 80.2717 | 45 | 0 | 26.2862
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 203.9629 | 4 | 0 | 25.3299 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 203.9629 | 4 | 0 | 25.3299
Path | P16 Idaho-Sierra | -360 | 500 | 95.9176 | 2 | 2 | 21.91 | Path | P16 Idaho-Sierra | -360 | 500 | 95.9176 | 2 | 2 | 21.91
Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 36.9379 | 1 | 0 | 19.8118 | Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 36.9379 | 1 | 0 | 19.8118
Path | P80 Montana Southeast | -600 | 600 | -90.7081 | 7 | 8 | 11.6652 | Path | P80 Montana Southeast | -600 | 600 | -90.7081 | 7 | 8 | 11.6652
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -13.1957 | 5 | 55 | 9.0901 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -13.1957 | 5 | 55 | 9.0901
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 10.1877 | 0 | 66 | 8.9723 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 10.1877 | 0 | 66 | 8.9723
Path | P03 Northwest-British Columbia | -3150 | 3000 | 520.647 | 2 | 0 | 6.552 | Path | P03 Northwest-British Columbia | -3150 | 3000 | 520.647 | 2 | 0 | 6.552
Path | P66 COI | -3675 | 4800 | 1049.3591 | 0 | 1 | 6.1483 | Path | P66 COI | -3675 | 4800 | 1049.3591 | 0 | 1 | 6.1483
Path | P09 West of Broadview | -2573 | 2573 | 1778.9088 | 4 | 0 | 5.7121 | Path | P09 West of Broadview | -2573 | 2573 | 1778.9088 | 4 | 0 | 5.7121
Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -100.7534 | 0 | 1 | 4.8863 | Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -100.7534 | 0 | 1 | 4.8863
Path | P19 Bridger West | -1250 | 2400 | 1332.0964 | 1 | 0 | 2.6424 | Path | P19 Bridger West | -1250 | 2400 | 1332.0964 | 1 | 0 | 2.6424
Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -202.7496 | 2 | 2 | 1.9279 | Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -202.7496 | 2 | 2 | 1.9279

## 2030 3 CPP
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Path | z Aeolus West | -2670 | 2670 | 1264.3916 | 1399 | 0 | 560956.3749 | Path | z Aeolus West | -2670 | 2670 | 1264.3916 | 1399 | 0 | 560956.3749
Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | -200.8612 | 0 | 1465 | 483949.6973 | Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | -200.8612 | 0 | 1465 | 483949.6973
Path | z Aeolus South | -1700 | 1700 | -598.0075 | 0 | 1075 | 317803.268 | Path | z Aeolus South | -1700 | 1700 | -598.0075 | 0 | 1075 | 317803.268
Path | P37 TOT 4A | -99999 | 1025 | -591.9928 | 0 | 1057 | 312437.39 | Path | P37 TOT 4A | -1775 | 1775 | -591.9928 | 0 | 1057 | 312437.39
Path | z AZ Palo Verde East | -8010 | 8010 | 5779.5265 | 1260 | 0 | 273264.2579 | Path | z AZ Palo Verde East | -8010 | 8010 | 5779.5265 | 1260 | 0 | 273264.2579
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1016.7814 | 0 | 6272 | 199647.394 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1016.7814 | 0 | 6272 | 199647.394
Path | P01 Alberta-British Columbia | -1200 | 1000 | 276.9096 | 711 | 17 | 104538.9562 | Path | P01 Alberta-British Columbia | -1200 | 1000 | 276.9096 | 711 | 17 | 104538.9562
Path | P45 SDG&E-CFE | -800 | 408 | 41.1626 | 569 | 3 | 95963.8701 | Path | P45 SDG&E-CFE | -800 | 408 | 41.1626 | 569 | 3 | 95963.8701
Path | P36 TOT 3 | -1680 | 1680 | 1264.9392 | 2321 | 0 | 54454.1256 | Path | P36 TOT 3 | -1680 | 1680 | 1264.9392 | 2321 | 0 | 54454.1256
Nomogram | BPA_PreferredRate | 0 | 3500 | 590.1384 | 4430 | 0 | 35447.823 | Nomogram | BPA_PreferredRate | 0 | 3500 | 590.1384 | 4430 | 0 | 35447.823
Path | CAISO Zero Net Export | -99999 | 2000 | -4746.9135 | 53 | 0 | 32383.7061 | Path | CAISO Zero Net Export | -99999 | 8000 | -4746.9135 | 53 | 0 | 32383.7061
Path | z WA North of Hanford | -2948 | 4100 | -687.256 | 0 | 172 | 30581.9064 | Path | z WA North of Hanford | -2948 | 4100 | -687.256 | 0 | 172 | 30581.9064
Path | P83 Montana Alberta Tie Line | -300 | 325 | -31.0361 | 388 | 949 | 25898.9317 | Path | P83 Montana Alberta Tie Line | -300 | 325 | -31.0361 | 388 | 949 | 25898.9317
Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 99.7178 | 24 | 0 | 20181.6172 | Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 99.7178 | 24 | 0 | 20181.6172
Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -355.7384 | 0 | 385 | 10567.337 | Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -355.7384 | 0 | 385 | 10567.337
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -21.7533 | 350 | 0 | 10060.5978 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -21.7533 | 350 | 0 | 10060.5978
Path | P31 TOT 2A | -690 | 690 | -180.9004 | 35 | 1035 | 9867.0531 | Path | P31 TOT 2A | -690 | 690 | -180.9004 | 35 | 1035 | 9867.0531
Path | P19 Bridger West | -1250 | 2400 | 2265.4174 | 189 | 0 | 8788.3377 | Path | P19 Bridger West | -2300 | 4100 | 2265.4174 | 189 | 0 | 8788.3377
Path | P26 Northern-Southern California | -3000 | 4000 | 214.7716 | 95 | 481 | 7077.384 | Path | P26 Northern-Southern California | -3000 | 4000 | 214.7716 | 95 | 481 | 7077.384
Path | z CA PDCI South | -3100 | 2780 | -121.0998 | 8 | 96 | 6476.4075 | Path | z CA PDCI South | -3100 | 2780 | -121.0998 | 8 | 96 | 6476.4075
Path | xy AB-MT | -300 | 325 | -31.0361 | 80 | 77 | 6158.3211 | Path | xy AB-MT | -300 | 325 | -31.0361 | 80 | 77 | 6158.3211
Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -794.2201 | 0 | 159 | 4999.5185 | Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -794.2201 | 0 | 159 | 4999.5185
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 103.487 | 1316 | 0 | 4773.4526 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 103.487 | 1316 | 0 | 4773.4526
Path | P66 COI | -3675 | 4800 | 1001.1482 | 17 | 132 | 4017.1021 | Path | P66 COI | -3675 | 4800 | 1001.1482 | 17 | 132 | 4017.1021
Path | P35 TOT 2C | -580 | 600 | 124.2769 | 1356 | 821 | 3899.973 | Path | P35 TOT 2C | -580 | 600 | 124.2769 | 1356 | 821 | 3899.973
Path | P18 Montana-Idaho | -256 | 337 | 112.2925 | 198 | 0 | 2976.4221 | Path | P18 Montana-Idaho | -256 | 337 | 112.2925 | 198 | 0 | 2976.4221
Nomogram | COI 2 | -99999 | 4560 | 1152.8337 | 199 | 0 | 2028.2652 | Nomogram | COI 2 | -99999 | 4560 | 1152.8337 | 199 | 0 | 2028.2652
Path | P38 TOT 4B | -880 | 880 | 475.9624 | 118 | 0 | 1510.5059 | Path | P38 TOT 4B | -880 | 880 | 475.9624 | 118 | 0 | 1510.5059
Path | P49 East of Colorado River (EOR) | -10200 | 9900 | 5196.595 | 27 | 0 | 1163.8935 | Path | P49 East of Colorado River (EOR) | -10200 | 9900 | 5196.595 | 27 | 0 | 1163.8935
Path | xy COI plus PDCI | -6455 | 7900 | 880.0484 | 0 | 13 | 1152.3724 | Path | xy COI plus PDCI | -6455 | 7900 | 880.0484 | 0 | 13 | 1152.3724
Path | P09 West of Broadview | -2573 | 2573 | 1910.4558 | 167 | 0 | 1063.9587 | Path | P09 West of Broadview | -2573 | 2573 | 1910.4558 | 167 | 0 | 1063.9587
Path | xy WA-BC East | -400 | 400 | 207.9843 | 1354 | 20 | 975.066 | Path | xy WA-BC East | -400 | 400 | 207.9843 | 1354 | 20 | 975.066
Path | P39 TOT 5 | -1680 | 1680 | 550.1622 | 57 | 0 | 914.3887 | Path | P39 TOT 5 | -1680 | 1680 | 550.1622 | 57 | 0 | 914.3887
Path | P76 Alturas Project | -300 | 300 | 132.2651 | 1197 | 303 | 903.2994 | Path | P76 Alturas Project | -300 | 300 | 132.2651 | 1197 | 303 | 903.2994
Path | P24 PG&E-Sierra | -150 | 160 | 62.8165 | 1749 | 263 | 824.4502 | Path | P24 PG&E-Sierra | -150 | 160 | 62.8165 | 1749 | 263 | 824.4502
Path | P14 Idaho to Northwest | -2250 | 3400 | 277.8163 | 0 | 40 | 673.4295 | Path | P14 Idaho to Northwest | -2250 | 3400 | 277.8163 | 0 | 40 | 673.4295
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 323.5749 | 119 | 9 | 622.8752 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 323.5749 | 119 | 9 | 622.8752
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 0.71957 | 319 | 878 | 480.518 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 0.71957 | 319 | 878 | 480.518
Nomogram | IPP DC | -99999 | 361 | 41.1843 | 356 | 0 | 332.3056 | Nomogram | IPP DC | -99999 | 361 | 41.1843 | 356 | 0 | 332.3056
Path | P77 Crystal-Allen | -950 | 950 | 35.6674 | 805 | 1375 | 267.1258 | Path | P77 Crystal-Allen | -950 | 950 | 35.6674 | 805 | 1375 | 267.1258
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 184.6186 | 0 | 42 | 177.4652 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 184.6186 | 0 | 42 | 177.4652
Nomogram | COI 1 | -99999 | 6763 | 2201.5349 | 9 | 0 | 141.8066 | Nomogram | COI 1 | -99999 | 6763 | 2201.5349 | 9 | 0 | 141.8066
Path | P80 Montana Southeast | -600 | 600 | -127.7949 | 41 | 64 | 134.499 | Path | P80 Montana Southeast | -600 | 600 | -127.7949 | 41 | 64 | 134.499
Path | P16 Idaho-Sierra | -360 | 500 | 110.6732 | 22 | 0 | 121.68 | Path | P16 Idaho-Sierra | -360 | 500 | 110.6732 | 22 | 0 | 121.68
Nomogram | Path 22 | -99999 | 3113 | 550.6756 | 2 | 0 | 102.2371 | Nomogram | Path 22 | -99999 | 3113 | 550.6756 | 2 | 0 | 102.2371
Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 493.6041 | 28 | 0 | 83.1698 | Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 493.6041 | 28 | 0 | 83.1698
Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 162.079 | 1 | 0 | 83.0489 | Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 162.079 | 1 | 0 | 83.0489
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 14.2615 | 2 | 187 | 69.9574 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 14.2615 | 2 | 187 | 69.9574
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -20.0785 | 6 | 314 | 69.8862 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -20.0785 | 6 | 314 | 69.8862
Path | P22 Southwest of Four Corners | -2325 | 2325 | 404.268 | 5 | 0 | 58.6946 | Path | P22 Southwest of Four Corners | -2325 | 2325 | 404.268 | 5 | 0 | 58.6946
Nomogram | CA Path15 N2S-MidwayGen | -99999 | 3265 | -1140.1033 | 6 | 0 | 53.0105 | Nomogram | CA Path15 N2S-MidwayGen | -99999 | 3265 | -1140.1033 | 6 | 0 | 53.0105
Path | P03 Northwest-British Columbia | -3150 | 3000 | 509.7312 | 9 | 0 | 30.948 | Path | P03 Northwest-British Columbia | -3150 | 3000 | 509.7312 | 9 | 0 | 30.948
Path | P30 TOT 1A | -650 | 650 | -70.7531 | 4 | 1 | 29.4781 | Path | P30 TOT 1A | -650 | 650 | -70.7531 | 4 | 1 | 29.4781
Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -452.4415 | 0 | 54 | 21.9919 | Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -452.4415 | 0 | 54 | 21.9919
Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 38.096 | 3 | 0 | 20.0711 | Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 38.096 | 3 | 0 | 20.0711
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | -496.157 | 1 | 0 | 13.3688 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | -496.157 | 1 | 0 | 13.3688
Path | P11 West of Crossover | -2598 | 2598 | 1854.0164 | 11 | 0 | 10.179 | Path | P11 West of Crossover | -2598 | 2598 | 1854.0164 | 11 | 0 | 10.179
Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -119.8907 | 0 | 1 | 10.0495 | Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -119.8907 | 0 | 1 | 10.0495
Contingency | 3563-PG&E LCR NCNB LV Cat C | -120 | 120 | 48.7595 | 12 | 0 | 4.6805 | Contingency | 3563-PG&E LCR NCNB LV Cat C | -120 | 120 | 48.7595 | 12 | 0 | 4.6805
Path | P15 Midway-LosBanos | -3265 | 5400 | 1140.1033 | 0 | 1 | 0.18937 | Path | P15 Midway-LosBanos | -3265 | 5400 | 1140.1033 | 0 | 1 | 0.18937
[8 empty] | Path | 3111-cont 0 | -1503 | 1503 | -215.7447 | 0 | 184 | 22253.8614
[8 empty] | Path | 34576-cont 0 | -1139 | 1139 | 522.4003 | 191 | 0 | 521.7577
[8 empty] | Path | 2136-cont 0 | -796 | 796 | -481.2377 | 1 | 899 | 365.3123

## 2030 1 Regional
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Nomogram | CAISO_Plus_Renewables_Limit | -99999 | 2000 | -2949.8067 | 1253 | 0 | 281395.498 | Path | CAISO Zero Net Export | -99999 | 8000 | -2973.2939 | 270 | 0 | 209382.1782
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1026.1023 | 0 | 5415 | 178774.1947 | Path | z AZ Palo Verde East | -8010 | 8010 | 5508.5636 | 758 | 0 | 106636.2169
Path | P45 SDG&E-CFE | -800 | 408 | 79.1162 | 1263 | 2 | 107427.801 | Nomogram | BPA_PreferredRate | 0 | 3500 | 737.1727 | 5760 | 0 | 92372.6615
Nomogram | BPA_PreferredRate | 0 | 3500 | 761.1595 | 5922 | 0 | 78212.6028 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1041.5573 | 0 | 5648 | 87751.1966
Path | CAISO Zero Net Export | -99999 | 2000 | -3726.659 | 327 | 0 | 70617.3578 | Path | P01 Alberta-British Columbia | -1200 | 1000 | 204.9074 | 532 | 26 | 69055.5926
Nomogram | FreqResponse-3506 | -99999 | 0 | -51.6017 | 578 | 0 | 39954.48 | Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 255.2051 | 48 | 0 | 46395.4399
Path | P39 TOT 5 | -1680 | 1680 | 234.5724 | 13 | 0 | 32963.9023 | Path | P45 SDG&E-CFE | -800 | 408 | 34.2393 | 437 | 3 | 39257.0628
Path | P36 TOT 3 | -1680 | 1680 | 815.7521 | 42 | 0 | 29760.0583 | Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | 534.4674 | 3 | 0 | 35525.424
Path | P01 Alberta-British Columbia | -1200 | 1000 | 205.8018 | 395 | 5 | 24052.809 | Path | P15 Midway-LosBanos | -3265 | 5400 | 1235.1085 | 736 | 13 | 30536.9031
Path | z AZ Palo Verde East | -8010 | 8010 | 5271.2235 | 311 | 0 | 15710.3815 | Path | z WA North of Hanford | -2948 | 4100 | -789.9321 | 0 | 240 | 22046.4028
Path | P83 Montana Alberta Tie Line | -300 | 325 | 1.8869 | 179 | 92 | 6599.4271 | Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -355.2297 | 0 | 416 | 13475.744
Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 333.1007 | 13 | 0 | 6579.9513 | Path | P83 Montana Alberta Tie Line | -300 | 325 | -18.6092 | 258 | 329 | 12817.0223
Path | P31 TOT 2A | -690 | 690 | 108.4914 | 52 | 62 | 4093.5044 | Path | P36 TOT 3 | -1680 | 1680 | 1175.7744 | 924 | 0 | 12755.5445
Path | P26 Northern-Southern California | -3000 | 4000 | 881.1209 | 121 | 313 | 4014.574 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 171.3196 | 554 | 0 | 10676.2338
Path | P18 Montana-Idaho | -256 | 337 | 155.9341 | 174 | 0 | 3933.2743 | Path | xy AB-MT | -300 | 325 | -18.6092 | 103 | 150 | 8307.4758
Path | P15 Midway-LosBanos | -3265 | 5400 | 870.4604 | 221 | 4 | 3715.256 | Path | P18 Montana-Idaho | -256 | 337 | 152.5117 | 301 | 0 | 5112.7547
Path | 3111-cont 0 | -1503 | 1503 | -50.397 | 0 | 155 | 3097.166 | Path | P66 COI | -3675 | 4800 | 620.1039 | 1 | 217 | 5024.25
Nomogram | FreqResponse-25 | -99999 | 0 | -10.7759 | 690 | 0 | 2552.55 | Path | 3111-cont 0 | -1503 | 1503 | -102.2626 | 0 | 142 | 4990.9445
Path | z WA North of Hanford | -2948 | 4100 | -679.8181 | 0 | 59 | 1808.3946 | Path | P31 TOT 2A | -690 | 690 | -119.0008 | 42 | 749 | 4292.7253
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 95.6266 | 445 | 0 | 1217.8378 | Path | P39 TOT 5 | -1680 | 1680 | 695.2196 | 352 | 0 | 3507.3494
Path | P35 TOT 2C | -580 | 600 | 102.8684 | 317 | 468 | 747.785 | Path | P35 TOT 2C | -580 | 600 | 85.7671 | 792 | 901 | 3486.8579
Nomogram | FreqResponse-1 | -99999 | 0 | -0.055308 | 790 | 0 | 589.38 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 93.7045 | 1033 | 0 | 2904.9608
Path | xy AB-MT | -300 | 325 | 1.8869 | 133 | 78 | 583.3447 | Path | P65 Pacific DC Intertie (PDCI) | -3100 | 3220 | -106.2408 | 0 | 78 | 2551.0303
Path | P14 Idaho to Northwest | -2250 | 3400 | -267.1103 | 0 | 28 | 575.2777 | Path | P26 Northern-Southern California | -3000 | 4000 | 774.5538 | 210 | 48 | 2323.375
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 488.1789 | 139 | 0 | 554.1802 | Path | P14 Idaho to Northwest | -2250 | 3400 | -333.8593 | 0 | 65 | 1465.5532
Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -281.5051 | 0 | 30 | 496.988 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 445.9478 | 255 | 5 | 1053.5602
Nomogram | FreqResponse-197 | -99999 | 0 | -46.1648 | 217 | 0 | 491.4 | Path | xy COI plus PDCI | -6455 | 7900 | 513.8631 | 0 | 10 | 842.739
Path | P30 TOT 1A | -650 | 650 | 163.3843 | 6 | 1 | 330.7181 | Path | P76 Alturas Project | -300 | 300 | 93.05 | 968 | 290 | 648.6729
Path | P76 Alturas Project | -300 | 300 | 62.7648 | 427 | 272 | 321.3039 | Path | z CA PDCI South | -3100 | 2780 | -106.2408 | 9 | 3 | 634.3593
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 131.9233 | 30 | 0 | 310.9878 | Path | P24 PG&E-Sierra | -150 | 160 | 37.6317 | 1474 | 229 | 613.0022
Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -402.5108 | 0 | 41 | 298.1084 | Path | xy WA-BC East | -400 | 400 | 189.8669 | 830 | 11 | 582.3956
Path | P65 Pacific DC Intertie (PDCI) | -3100 | 3220 | -40.6039 | 0 | 15 | 235.0141 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 167.2687 | 0 | 85 | 581.4368
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 1.3125 | 178 | 330 | 224.0537 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 1.0645 | 334 | 783 | 447.5066
Path | P24 PG&E-Sierra | -150 | 160 | -1.5718 | 561 | 365 | 201.7337 | Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 254.6148 | 3 | 0 | 418.4555
Path | xy WA-BC East | -400 | 400 | 173.8523 | 426 | 10 | 122.6812 | Nomogram | COI 2 | -99999 | 4560 | 732.5742 | 40 | 0 | 373.7741
Nomogram | COI 2 | -99999 | 4560 | 1218.899 | 12 | 0 | 119.1528 | Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -583.6224 | 0 | 25 | 334.134
Path | z CA PDCI South | -3100 | 2780 | -40.6039 | 8 | 2 | 74.4183 | Nomogram | IPP DC | -99999 | 361 | 54.6029 | 158 | 0 | 328.4075
Nomogram | FreqResponse-128 | -99999 | 0 | -0.027854 | 10 | 0 | 70.68 | Path | P09 West of Broadview | -2573 | 2573 | 1922.3977 | 79 | 0 | 214.8532
Nomogram | FreqResponse-129 | -99999 | 0 | -0.024722 | 9 | 0 | 70.68 | Path | P40 TOT 7 | -890 | 890 | 383.0382 | 21 | 0 | 192.1608
Nomogram | COI 1 | -99999 | 6763 | 2267.4371 | 4 | 0 | 49.6675 | Path | 2136-cont 0 | -796 | 796 | -160.5423 | 0 | 535 | 180.4699
Path | P77 Crystal-Allen | -950 | 950 | 572.8176 | 492 | 96 | 37.7549 | Path | P77 Crystal-Allen | -950 | 950 | 131.5599 | 594 | 776 | 150.2178
Nomogram | IPP DC | -99999 | 361 | 79.2693 | 20 | 0 | 28.8175 | Path | P80 Montana Southeast | -600 | 600 | -88.0414 | 64 | 47 | 149.4252
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 163.944 | 0 | 13 | 28.0898 | Path | P75 Hemingway-Summer Lake | -1200 | 2400 | 72.0707 | 0 | 5 | 143.97
Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 37.0324 | 1 | 0 | 27.9409 | Path | P03 Northwest-British Columbia | -3150 | 3000 | 572.3184 | 15 | 0 | 121.23
Path | P09 West of Broadview | -2573 | 2573 | 1908.0979 | 11 | 0 | 26.6794 | Path | 34576-cont 0 | -1139 | 1139 | 194.7816 | 52 | 0 | 99.4768
Path | 2136-cont 0 | -796 | 796 | -54.1494 | 2 | 148 | 25.3733 | Path | P16 Idaho-Sierra | -360 | 500 | 91.1086 | 11 | 1 | 85.0245
Path | P16 Idaho-Sierra | -360 | 500 | 88.7123 | 6 | 2 | 23.7465 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -26.7928 | 3 | 374 | 75.1187
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 188.777 | 3 | 0 | 20.869 | Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 173.5947 | 45 | 0 | 74.6466
Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 115.8733 | 22 | 0 | 20.3038 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 10.1623 | 0 | 212 | 74.6183
Path | 34576-cont 0 | -1139 | 1139 | 133.2656 | 33 | 0 | 16.5326 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | 59.6662 | 10 | 0 | 58.5569
Path | P03 Northwest-British Columbia | -3150 | 3000 | 561.0192 | 4 | 0 | 14.199 | Nomogram | COI 1 | -99999 | 6763 | 1781.2676 | 5 | 0 | 47.7468
Path | P80 Montana Southeast | -600 | 600 | -159.8659 | 6 | 31 | 12.1902 | Path | P30 TOT 1A | -650 | 650 | -41.4087 | 10 | 3 | 41.7579
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -15.1509 | 7 | 55 | 11.0209 | Path | P19 Bridger West | -1250 | 2400 | 1569.0159 | 6 | 0 | 39.684
Path | P19 Bridger West | -1250 | 2400 | 1662.7615 | 3 | 0 | 9.6792 | Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 39.4854 | 2 | 0 | 27.6946
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 14.4117 | 0 | 50 | 7.8059 | Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -139.3554 | 0 | 63 | 25.6917
Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -96.5345 | 0 | 2 | 4.9572 | Path | P38 TOT 4B | -880 | 880 | 441.6516 | 5 | 0 | 5.9426
Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -36.7571 | 4 | 2 | 1.705 | Path | P11 West of Crossover | -2598 | 2598 | 1909.2505 | 6 | 0 | 3.7047
[8 empty] | Contingency | 3563-PG&E LCR NCNB LV Cat C | -120 | 120 | 48.1804 | 1 | 0 | 0.0648

## 2030 3 No Addl Renew
| Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$) |  | Path Name | Path Minimum Rating (MW) | Path Maximum Rating (MW) | Average Flow (MW) | Positive Flow Limited Hours | Negative Flow Limited Hours | Path Revenue (k$)
Data posted 6/14/2016 | [7 empty] | Data updated on 6/16/2016 (changes from 6/14 are highlighted in yellow)
Path | z Aeolus West | -2670 | 2670 | 1264.3916 | 1399 | 0 | 560956.3749 | Path | z AZ Palo Verde East | -8010 | 8010 | 5656.6394 | 1035 | 0 | 194701.2327
Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | -200.8612 | 0 | 1465 | 483949.6973 | Nomogram | BPA_PreferredRate | 0 | 3500 | 754.5319 | 5829 | 0 | 88265.4472
Path | z Aeolus South | -1700 | 1700 | -598.0075 | 0 | 1075 | 317803.268 | Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1040.563 | 0 | 5753 | 83563.0629
Path | P37 TOT 4A | -1775 | 1775 | -591.9928 | 0 | 1057 | 312437.39 | Path | P01 Alberta-British Columbia | -1200 | 1000 | 196.177 | 536 | 29 | 45315.3012
Path | z AZ Palo Verde East | -8010 | 8010 | 5779.5265 | 1260 | 0 | 273264.2579 | Path | CAISO Zero Net Export | -99999 | 8000 | -4294.7156 | 54 | 0 | 38070.0827
Nomogram | LDWP 25% LocalMinGen | -99999 | 999999 | 1016.7814 | 0 | 6272 | 199647.394 | Path | P45 SDG&E-CFE | -800 | 408 | 29.4878 | 408 | 4 | 21620.4623
Path | P01 Alberta-British Columbia | -1200 | 1000 | 276.9096 | 711 | 17 | 104538.9562 | Path | 3111-cont 0 | -1503 | 1503 | -185.1133 | 0 | 213 | 18292.4103
Path | P45 SDG&E-CFE | -800 | 408 | 41.1626 | 569 | 3 | 95963.8701 | Path | z WA North of Hanford | -2948 | 4100 | -736.6361 | 0 | 147 | 17022.2532
Path | P36 TOT 3 | -1680 | 1680 | 1264.9392 | 2321 | 0 | 54454.1256 | Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 235.8669 | 30 | 0 | 12941.9992
Nomogram | BPA_PreferredRate | 0 | 3500 | 590.1384 | 4430 | 0 | 35447.823 | Path | P48 Northern New Mexico (NM2) | -1970 | 1970 | 531.8856 | 1 | 0 | 11822.64
Path | CAISO Zero Net Export | -99999 | 8000 | -4746.9135 | 53 | 0 | 32383.7061 | Path | P26 Northern-Southern California | -3000 | 4000 | 332.4605 | 170 | 649 | 9683.165
Path | z WA North of Hanford | -2948 | 4100 | -687.256 | 0 | 172 | 30581.9064 | Path | P36 TOT 3 | -1680 | 1680 | 1070.805 | 688 | 0 | 9190.1174
Path | P83 Montana Alberta Tie Line | -300 | 325 | -31.0361 | 388 | 949 | 25898.9317 | Path | P83 Montana Alberta Tie Line | -300 | 325 | 14.2753 | 345 | 239 | 7288.2444
Path | P47 Southern New Mexico (NM1) | -1048 | 1048 | 99.7178 | 24 | 0 | 20181.6172 | Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | 42.0566 | 310 | 0 | 7211.7036
Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -355.7384 | 0 | 385 | 10567.337 | Path | P23 Four Corners 345/500 Qualified Path | -1000 | 1000 | -306.5374 | 0 | 208 | 6666.232
Path | P61 Lugo-Victorville 500 kV Line | -2400 | 900 | -21.7533 | 350 | 0 | 10060.5978 | Path | xy AB-MT | -300 | 325 | 14.2753 | 79 | 68 | 6208.2527
Path | P31 TOT 2A | -690 | 690 | -180.9004 | 35 | 1035 | 9867.0531 | Path | P31 TOT 2A | -690 | 690 | -107.2465 | 26 | 639 | 4065.0343
Path | P19 Bridger West | -2300 | 4100 | 2265.4174 | 189 | 0 | 8788.3377 | Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 103.5997 | 1168 | 0 | 3689.455
Path | P26 Northern-Southern California | -3000 | 4000 | 214.7716 | 95 | 481 | 7077.384 | Path | z CA PDCI South | -3100 | 2780 | -124.2438 | 6 | 110 | 3603.4243
Path | z CA PDCI South | -3100 | 2780 | -121.0998 | 8 | 96 | 6476.4075 | Path | P18 Montana-Idaho | -256 | 337 | 118.2382 | 203 | 0 | 3223.9755
Path | xy AB-MT | -300 | 325 | -31.0361 | 80 | 77 | 6158.3211 | Path | P35 TOT 2C | -580 | 600 | 99.8507 | 885 | 717 | 2671.098
Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -794.2201 | 0 | 159 | 4999.5185 | Path | P66 COI | -3675 | 4800 | 844.9906 | 1 | 111 | 2578.1461
Path | P29 Intermountain-Gonder 230 kV | -200 | 200 | 103.487 | 1316 | 0 | 4773.4526 | Path | P39 TOT 5 | -1680 | 1680 | 662.1303 | 128 | 0 | 1506.5954
Path | P66 COI | -3675 | 4800 | 1001.1482 | 17 | 132 | 4017.1021 | Contingency | 3105-CA500kV C1 L-1 LosBanos-Midway | -3464 | 3464 | -742.4743 | 0 | 65 | 1355.3489
Path | P35 TOT 2C | -580 | 600 | 124.2769 | 1356 | 821 | 3899.973 | Path | P76 Alturas Project | -300 | 300 | 126.7123 | 929 |  | 660.0009
Path | P18 Montana-Idaho | -256 | 337 | 112.2925 | 198 | 0 | 2976.4221 | Path | P24 PG&E-Sierra | -150 | 160 | 42.938 | 1371 | 273 | 588.0599
Nomogram | COI 2 | -99999 | 4560 | 1152.8337 | 199 | 0 | 2028.2652 | Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 400.4403 | 162 | 2 | 581.5408
Path | P38 TOT 4B | -880 | 880 | 475.9624 | 118 | 0 | 1510.5059 | Path | P14 Idaho to Northwest | -2250 | 3400 | 241.8361 | 0 | 23 | 512.55
Path | P49 East of Colorado River (EOR) | -10200 | 9900 | 5196.595 | 27 | 0 | 1163.8935 | Path | xy WA-BC East | -400 | 400 | 156.4532 | 563 | 24 | 443.812
Path | xy COI plus PDCI | -6455 | 7900 | 880.0484 | 0 | 13 | 1152.3724 | Nomogram | COI 2 | -99999 | 4560 | 991.1232 | 44 | 0 | 441.5722
Path | P09 West of Broadview | -2573 | 2573 | 1910.4558 | 167 | 0 | 1063.9587 | Path | P49 East of Colorado River (EOR) | -10200 | 9900 | 5274.3642 | 11 | 0 | 420.3738
Path | xy WA-BC East | -400 | 400 | 207.9843 | 1354 | 20 | 975.066 | Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 0.64717 | 307 | 742 | 413.1135
Path | P39 TOT 5 | -1680 | 1680 | 550.1622 | 57 | 0 | 914.3887 | Path | 34576-cont 0 | -1139 | 1139 | 388.4314 | 138 | 0 | 353.9363
Path | P76 Alturas Project | -300 | 300 | 132.2651 | 1197 | 303 | 903.2994 | Path | P37 TOT 4A | -1775 | 1775 | -240.7457 | 0 | 6 | 300.2998
Path | P24 PG&E-Sierra | -150 | 160 | 62.8165 | 1749 | 263 | 824.4502 | Path | 2136-cont 0 | -796 | 796 | -358.9436 | 2 | 734 | 295.3423
Path | P14 Idaho to Northwest | -2250 | 3400 | 277.8163 | 0 | 40 | 673.4295 | Nomogram | IPP DC | -99999 | 361 | 60.8886 | 227 | 0 | 255.9046
Path | P28 Intermountain-Mona 345 kV | -1200 | 1400 | 323.5749 | 119 | 9 | 622.8752 | Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 186.9882 | 0 | 49 | 203.2933
Path | P52 Silver Peak-Control 55 kV | -17 | 17 | 0.71957 | 319 | 878 | 480.518 | Path | P09 West of Broadview | -2573 | 2573 | 1967.8106 | 97 | 0 | 195.3267
Nomogram | IPP DC | -99999 | 361 | 41.1843 | 356 | 0 | 332.3056 | Path | P77 Crystal-Allen | -950 | 950 | 55.7262 | 629 | 983 | 170.3967
Path | P77 Crystal-Allen | -950 | 950 | 35.6674 | 805 | 1375 | 267.1258 | Path | P03 Northwest-British Columbia | -3150 | 3000 | 579.2379 | 19 | 0 | 167.181
Path | P32 Pavant-Gonder InterMtn-Gonder 230 kV | -235 | 440 | 184.6186 | 0 | 42 | 177.4652 | Path | xy COI plus PDCI | -6455 | 7900 | 720.7468 | 0 | 5 | 122.077
Nomogram | COI 1 | -99999 | 6763 | 2201.5349 | 9 | 0 | 141.8066 | Path | P16 Idaho-Sierra | -360 | 500 | 95.8491 | 12 | 0 | 117.825
Path | P80 Montana Southeast | -600 | 600 | -127.7949 | 41 | 64 | 134.499 | Path | P15 Midway-LosBanos | -3265 | 5400 | 1073.3722 | 0 | 12 | 113.1061
Path | P16 Idaho-Sierra | -360 | 500 | 110.6732 | 22 | 0 | 121.68 | Path | P30 TOT 1A | -650 | 650 | -48.5033 | 6 | 2 | 101.0731
Nomogram | Path 22 | -99999 | 3113 | 550.6756 | 2 | 0 | 102.2371 | Path | P80 Montana Southeast | -600 | 600 | -116.0304 | 45 | 28 | 96.4494
Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 493.6041 | 28 | 0 | 83.1698 | Nomogram | COI 1 | -99999 | 6763 | 2039.8244 | 5 | 0 | 78.3223
Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 162.079 | 1 | 0 | 83.0489 | Path | P40 TOT 7 | -890 | 890 | 326.869 | 13 | 0 | 67.1443
Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 14.2615 | 2 | 187 | 69.9574 | Nomogram | CA Path15 N2S-MidwayGen | -99999 | 3265 | -1073.3722 | 8 | 0 | 55.9523
Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -20.0785 | 6 | 314 | 69.8862 | Path | P60 Inyo-Control 115 kV Tie | -56 | 56 | -17.4054 | 4 | 221 | 48.5539
Path | P22 Southwest of Four Corners | -2325 | 2325 | 404.268 | 5 | 0 | 58.6946 | Contingency | 34576-CA500kV S5 L-2 APS N.Gila-ImperialValley | -1139 | 1139 | 361.8501 | 17 | 0 | 45.5497
Nomogram | CA Path15 N2S-MidwayGen | -99999 | 3265 | -1140.1033 | 6 | 0 | 53.0105 | Path | P22 Southwest of Four Corners | -2325 | 2325 | 604.3306 | 2 | 0 | 43.6333
Path | P03 Northwest-British Columbia | -3150 | 3000 | 509.7312 | 9 | 0 | 30.948 | Path | P25 PacifiCorp/PG&E 115 kV Interconnection | -45 | 100 | 17.321 | 0 | 137 | 42.3882
Path | P30 TOT 1A | -650 | 650 | -70.7531 | 4 | 1 | 29.4781 | Path | P38 TOT 4B | -880 | 880 | 465.4293 | 27 | 0 | 34.5022
Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -452.4415 | 0 | 54 | 21.9919 | Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | -398.0901 | 6 | 0 | 31.019
Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 38.096 | 3 | 0 | 20.0711 | Path | P46 West of Colorado River (WOR) | -11200 | 11800 | 5028.2656 | 2 | 0 | 24.9806
Nomogram | CA Path26 N2S with RAS | -99999 | 3450 | -496.157 | 1 | 0 | 13.3688 | Path | P75 Hemingway-Summer Lake | -1200 | 2400 | 331.6724 | 0 | 1 | 15.6864
Path | P11 West of Crossover | -2598 | 2598 | 1854.0164 | 11 | 0 | 10.179 | Contingency | 4915-PG&E LCR Fresno Wilson Cat B | -119.5 | 119.5 | 37.9412 | 1 | 0 | 14.185
Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -119.8907 | 0 | 1 | 10.0495 | Contingency | 2136-CA500kV S5 L-2 APS N.Gila-ImperialValley | -796 | 796 | -332.3623 | 0 | 44 | 13.4245
Contingency | 3563-PG&E LCR NCNB LV Cat C | -120 | 120 | 48.7595 | 12 | 0 | 4.6805 | Contingency | 2396-CA230kV S LAM3 L-1 SCE Sylmar-Pardee | -1195 | 1195 | 185.9496 | 1 | 0 | 12.8259
[8 empty] | Path | P11 West of Crossover | -2598 | 2598 | 1894.9314 | 7 | 0 | 4.3205
[8 empty] | Contingency | 2044-CA500kV S5 L-2 APS N.Gila-ImperialValley | -351 | 351 | -111.0878 | 0 | 1 | 2.9551
[8 empty] | Contingency | 3563-PG&E LCR NCNB LV Cat C | -120 | 120 | 48.92 | 6 | 0 | 1.1038