## Cost Details
All costs are $x1,000
2020 Proposed DCRT Generator Interconnection Unit Cost Guide |  |  |  |  | "Voltages" | 500 kV | Notes/Comments:
Revised as of: |  |  |  | 2020-01-28
Equipment Categories |  |  |  |  | Units |  | Note: DCRT Unit Costs for equipment at voltages 230 kV and below are estimated on an as-needed basis, and are not published on the CAISO website.
New Substation Equipment
|  | Complete Loop-in Substation, equipped with one line position to |  |  |  | 38116.2313 | Includes all necessary equipment, including operating buses, one double-breaker line position on a breaker-and-a-half (BAAH) configuration for gen-tie, one three-breaker line position on a BAAH configuration to loop transmission line (500kV), substation control building (MEER), and associated protective relays. Also includes base costs of site preparation, ground grid, fencing, and driveway. Does not include licensing or environmental mitigations.
terminate a single gen-tie
|  | Transformer Banks: |  |  |  |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. 230kV or 115kV sections of the substation to be estimated on a lump sum basis
|  |  | 500/230 kV 4-1 Phase |  | per unit | 42213.8696
|  |  | 500/230 kV 3-1 Phase |  | per unit | 33182.6748
|  |  | 500/115 kV 1-3 Phase |  | per unit | 16872.0256 | (500/230 kV = 1120 MVA)
(500/115 kV = 560 MVA)
Line Positions to terminate gen-ties and Transformer Bank positions
|  |  | Single Breaker (add third breaker to breaker and a half) |  | per unit | 5634.2526 | Position cost estimate includes cost of any related disconnect switches and protection equipment located within the position
|  |  | Breaker and a half (2CB) |  | per unit | 9043.7283
|  |  | Breaker and a half (3CB) |  | per unit | 12775.5163
|  |  | Double Breaker (2CB, double bus) |  | per unit | 8306.7359
|  |  | Operating / Transfer Bus |  | per unit | N/A
|  | Double Operating Bus Sections - 2 new buses, spanning 2 positions |  |  | per unit | 2695.5388 | Typical configuration for 500 kV, includes "pair" of N/S or E/W buses
|  | Double Operating Bus Sections - 2 bus extensions, spanning 2 positions |  |  | per unit | 1510.8606 | Used in substation expansion
|  | Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  |  | per unit | N/A | Used in substation expansion
|  | Sectionalizing Breaker |  |  | per unit | N/A
|  | Shunt Capacitors |  |  | per unit | 20994.0384 | Includes cost of CB
| Miscellaneous Equipment (see comments) | [5 empty] | These items are rarely required for
|  | Bus Tie (1CB) |  |  | lump sum |  | high-voltage substations. If required,
|  | Shunt Reactors |  |  | lump sum |  | would be estimated as a lump sum.
|  | Phase Shifter |  |  | lump sum
|  | Ground Bank |  |  | lump sum
|  | Series Capacitors |  |  | lump sum
|  | Static VAR Compensator (SVC) |  |  | lump sum
|  | Tertiary Reactors (1 reactor, 1 bay) |  |  | lump sum
| Gas Insulated Substation (in lieu of open air construction) |  |  |  | lump sum |  | Not typical, would be estimated as a
Lump sum, if GIS required
Replacement Substation Equipment
|  | Line drops - 3 phases |  |  | per unit | 2624.2331
|  | Circuit Breakers (including replacement of foundation) |  |  | per unit | N/A
|  | Circuit Breakers (without TRV caps) |  |  | per unit | 2100.8718
|  | Transient recovery voltage capacitors (set of 3, separate from CBs) |  |  | per unit | N/A
|  | Disconnect switches (incl. steel structures and foundations) |  |  | per unit | 670.615
|  | Line protection relays (other end of line) |  |  | per set | 436.6879
|  | Wave Trap - 1 phase only |  |  | per unit | 172.1008
|  | Wave Trap removal |  |  | per unit | 387.2268
New Protection Equipment
|  | New SPS |  |  | lump sum |  | Costs vary widely, will be lump sum
|  | SPS Relays |  |  | lump sum |  | Costs vary widely, will be lump sum
|  | Additional set of bushing current transformers (3) at existing CBs |  |  | lump sum |  | Not separately estimated, but rolled into cost of SPS
Telecommunications Infrastructure
|  |  | Telecommunications infrastructure for new substations |  | per unit | 3456.2514 | Substations require complete communications rooms; 500kV cost includes microwave systems at substations for DCRT Network use only.
|  |  | Rack for telecommunication equipment (CRIAR) |  | per unit | 38.9644 | For lightwave, channel bank & related equipment in comm rooms at end of each fiber optic cable.
|  |  | Prefabricated communications building |  | per unit | 656.077 | Used at DCRT subs when no bldgs are available and only Telecom equipment is needed.
|  |  | Lightwave |  | per unit | 107.4155 | Terminal Equipment at end of fiber optic cables to manage optical signals.
|  |  | Channel bank |  | per unit | 49.4954 | Multiplexer interface between lightwave & the protection relays & SCADA equipment
|  |  | Digital Access Cross Connects |  | per unit | 166.3887 | Used at 500kV Subs to automate management of protection circuits.
|  |  | Cross Connect |  | per unit | 4.2124 | Engineered connections between comm ports of Telecom equipment
|  |  | Terminal equipment interface for T1 from local telco |  | per unit | 53.7077 | Terminal equipment for RTU connected to IC leased T1 for communications
|  |  | Fiber optic cable on existing poles |  | per mile | 104.2562 | FO Cable on a new 500 kV T/L is included in transmission line cost per mile estimate.
|  |  | Fiber optic cable on new poles |  | per mile | 141.1145
New HV Transmission Line
|  | Double Circuit, Strung on both sides, Lattice Tower |  |  | per mile | 9879.855 | Unit cost per mile shown is based on
|  | Double Circuit, Strung on one side, Lattice Tower |  |  | per mile | 8267.1544 | flat land/rural setting. Additional factors
|  | Single Circuit, Lattice Tower |  |  | per mile | 4821.6742 | applied for hilly (1.5X), mountainous (2.0X),
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  |  | per mile | 11599.1735 | and forested (3.0X) terrain (see factors tab)
|  | Double Circuit, Strung on one side, Tubular Steel Pole |  |  | per mile | *** | Factors also apply for suburban (2.0X)
|  | Single Circuit, Tubular Steel Pole |  |  | per mile | 6128.6271 | or urban (3.0X) population density.
*** Not recommended by DCRT Transmission Engineering
|  | Wood poles |  |  | per mile | N/A
| Removal of HV Transmission Line (complete tear down) | [5 empty] | Cost of removal only, assume any rebuild
|  | Double Circuit |  |  | per mile | 1690.2758 | would use "new transmission line" from
|  | Single Circuit |  |  | per mile | 1163.7293 | section above. Will include similar factors
as new transmission line
Reconductor/Upgrade Transmission Line
|  | Double Circuit, Strung on both sides, Lattice Tower |  |  | lump sum |  | Costs vary widely depending on
|  | Double Circuit, Strung on one side, Lattice Tower |  |  | lump sum |  | number of structures that require
|  | Single Circuit, Lattice Tower |  |  | lump sum |  | upgrade. As a result, will be estimated
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  |  | lump sum |  | as a lump sum.
|  | Double Circuit, Strung on one side, Tubular Steel Pole |  |  | lump sum
|  | Single Circuit, Tubular Steel Pole |  |  | lump sum
Metering
|  | Upgrade of existing RTUs |  |  | lump sum |  | Cost varies widely, will be lump sum
| Lump Sum costs below are in addition to per-unit or lump-sum costs listed above: | [5 empty] | Lump-sum costs are not published on CAISO website, but are included in Phase I cost estimates
| Engineering costs |  |  |  | lump sum |  | These costs are generally included
in the per-unit cost of equipment.
However, if any identified incremental
costs exceed the per-unit amount, they
will be estimated as a lump sum.
| Capitalized Licensing and Permitting Costs, including |  |  |  | lump sum |  | As best estimated at time of Phase I
| mitigation measures, FAA permits, etc. | [5 empty] | study
| Civil work: Site Preparation including site grading, ground grid, | [5 empty] | Civil, general facilities, MEER buildings, and any other facilities that are unique to a given project are lump sums
| and walls/fencing/containment |  |  |  | lump sum
| General Facilities: station light & power, backup generator, |  |  |  | lump sum
station utilities (water, gas, etc. if manned substation)
| Substation Control (MEER) Buildings |  |  |  | lump sum |  | Includes cost of batteries, DC power supply, cable trays
| Incremental cost for transmission line crossings (roads, |  |  |  | lump sum |  | Number of crossings are highly variable.
| streams, rail, highway, other T\L) | [5 empty] | As a result, will be estimated as a lump sum
| Land cost for substations and T/L ROW |  |  |  | lump sum |  | Land costs are highly variable.
As a result, will be estimated as a lump sum
| Incremental cost of soil/geotechnical mitigation measures |  |  |  | lump sum |  | Unable to perform detailed geotechnical
analysis of land in Phase I study, but
any known geotech mitigation measures
will be estimated as a lump sum
| Incremental environmental monitoring and mitigations |  |  |  | lump sum
| Corporate Overheads (A&G, P&B, and AFUDC) |  |  |  | lump sum |  | Unit costs shown above do not include
| Income Tax Component of Contribution (ITCC) |  |  |  | lump sum |  | A&G, P&B, AFUDC, or ITCC.

## Substation Notes & Assumptions
#REF!
Substation Notes and Assumptions
As of January 2020
Assumptions:
General labor overtime: based on 6-10 work schedule.
General contingency factor: 35% - DCRT Standard Contingency Policy used for preliminary project estimating based on AACE guidelines, and used in previous regulatory filings.
Unit costs include costs to procure materials, installation, engineering, project management costs, home office costs, and contingency.
Unit costs exclude allocated corporate overhead, including P&B, A&G, and AFUDC (these will be added to total cost estimates).
Unit costs exclude generator's responsibility for Income Tax Component of Contribution (ITCC), (these will be added to total cost estimates, if required).
Unit costs exclude environmental monitoring and mitigations.
Unit costs exclude Licensing.
Unit cost are given without the benefit of any preliminary & final engineering. Unforeseen conflicts and/or scope will increase costs. These unit costs do not include: right-of-way & easements requirements, environmental engineering/mitigation, GO 131-D engineering /permitting, other permitting, associated DCRT/3rd Party under-build work, etc. A signed Interconnection Agreement is required before final design/engineering can start. Construction will not commence until all of the above conditions have been addressed.

## BulkTrans Factors & Assumptions
#REF!
Bulk Transmission (500 kV) Factors for use in developing cost estimates in Phase I Generator Interconnection Studies
As of January 2020
Simplified example on how to apply factors:
[10 empty] | $ millions | Apply Factor | Delta
| Hypothetical baseline cost per mile for Double Circuit 220 kV line (strung one side) using Lattice Towers: | [8 empty] | 2
Known characteristics of proposed transmission line ROW at Phase I study:
|  | Will be constructed in mountainous terrain | [7 empty] | 2 | 2.0 x 2.0 =4 | 2
No population density issues
|  | High wind-prone area (but not icy) | [7 empty] | 1.35 | 2.0 x 1.35 =2.7 | 0.7
|  |  | Total Delta (summation of applied factor) | [8 empty] | 2.7
|  |  | Estimated cost per mile | [8 empty] | 2
|  |  | Estimated cost per mile including applied factors ($ million/ mile) | [8 empty] | 4.7
|  | Factor Types: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | flat |  |  | hilly |  | mountain |  | forest
|  |  | Population density |  | rural |  | desert | suburban |  | urban/metro
|  |  | Weather study (increase in |  | 1/2" ice, or 20# wind |  |  | 1" ice, 6# wind |  | > 2" ice, 6# wind
structural steel amount and foundation volume)
|  | Factor Amounts: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  | 2.0X to 3.0X
|  |  | Population density |  |  | 1.00X to 1.10X |  |  | 1.33X |  | 1.67X
|  |  | Weather study |  |  | 1.35X |  |  | 1.45X |  | 1.60X
|  |  | Factor Type | Explanation of Factor issues and Factor multipliers
|  |  | Terrain | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
|  |  | Population density | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
|  |  | Weather study | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure types or an increased number of structures to reduce the span lengths.
Other assumptions underlying unit cost guide:
Assumptions:
General labor overtime: based on 6-10 work schedule.
General contingency factor: 35% - DCRT Standard Contingency Policy used for preliminary project estimating based on AACE guidelines, and used in previous regulatory filings.
Owner's Representative Fee for EPC Construction: 10% of the total project cost.
Unit costs include costs to procure materials, installation, engineering, project management costs, home office costs, and contingency.
Unit costs exclude allocated corporate overhead, including P&B, A&G, and AFUDC (these will be added to total cost estimates).
Unit costs exclude generator's responsibility for Income Tax Component of Contribution (ITCC), (these will be added to total cost estimates, if required).
Unit costs exclude environmental monitoring and mitigations.
Unit cost are given w/out the benefit of any preliminary & final engineering. Unforeseen conflicts and/or scope will increase costs. These unit costs do not include: right-of-way & easements requirements, environmental engineering/mitigation, GO 131-D engineering /permitting, other permitting, associated DCRT/3rd Party under-build work, etc. A signed Interconnection Agreement is required before final design/engineering can start. Construction will not commence until all of the above conditions have been addressed.
Transmission line cost per mile assumes conventional construction.
Cost per mile of T\L requiring helicopter construction (or deconstruction) will have higher than published per-unit cost, the labor component of helicopter construction is incrementally higher, which is not included in the per-unit cost.
Cost of teardown of existing lines includes temporary bypass line (also referred to as a "shoe-fly") costs.

## Telecom Assumptions
#REF!
Telecommunication Elements
Telecommunications Infrastructure Assumptions:
Unit cost estimates are without the benefit of any preliminary & final engineering.
General contingency factor: 35% - DCRT Standard Contingency Policy used for preliminary project estimating based on AACE guidelines, and used in previous regulatory filings.
Delays in an IC's project may result in unavailability of telecommunications facilities originally assumed to be available in the study.
The IC is responsible for the installing the required communications paths, from the generator to the POCO, including the diverse path if required. DCRT will own and install the FO terminal equipment.
If diverse routing of FO cable is required for power line protection, FO cable on the power line poles and underground within the same Right-Of-Way (ROW) is considered in compliance with current WECC guidelines.
DCRT Telecommunications infrastructure, including FO, microwave path and tower, and satellite, is not available as an option to the IC for its gen-tie communications requirements.
Prefabricated buildings assume ground conditions and location do not trigger abnormal mitigation measures.

## Escalation Rates & Factors
#REF!
ESCALATION OVERVIEW :
Current DCRT Unit Cost Guide as posted on the CAISO website is in 2020 Constant Dollars.
DCRT’s cost estimating is done in 2020 constant dollars and then escalated over the years during which the project will be constructed, arriving at project costs in 2020 Constant Dollars Escalated to OD Year.
Current escalation rates used to arrive at escalated dollars are derived as follows:
► 2020-2028 - Q3 2018 IHS Global Insight Forecast of Transmission Capital escalation for the Pacific region (JUEPT@PCF)
► 2029, 2020 - 3-year average escalation rate (2025-2028)
DEFINITIONS :
Project Cost in 2020 Constant Dollars represents the cost of the Project if all costs were paid for in 2020.
Project Cost Escalated to OD Year represents the cost of the Project if all costs were paid for in the OD Year.
| Mathematical formula: Constant Dollars Escalated to OD Year |  |  |  |  | = Cost in Constant Dollars x Escalation Factor to OD year
CURRENT DCRT ESCALATION RATES :
|  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| Escalation Rate | 2.441% | 2.35% | 2.084% | 2.207% | 2.19% | 2.221% | 2.18% | 2.251% | 1.999% | 2.143% | 2.143%
| Escalation Factors | 1 | 1.0235 | 1.0448 | 1.0679 | 1.0913 | 1.1155 | 1.1398 | 1.1655 | 1.1888 | 1.2143 | 1.2403