## Cost Details
All costs are $x1,000
2020 Final GridLiance Generator Interconnection Unit Cost Guide |  |  |  | "Voltages" |  | 138 kV | 230 kV | 500 kV | Notes/Comments:
Revised as of: January 2020
Equipment Categories |  |  |  | Units
New Substation Equipment
|  | Complete 3-CB ring bus Substation, equipped with one line position to |  |  |  |  | 7326 | 15347 | Includes all necessary substation equipment, including operating buses, three breaker ring bus laid out in a breaker-and-a-half configuration (BAAH) to loop transmission line (230 and 500kV), substation control building, and associated protective relays. Also includes base costs of site preparation, ground grid, fencing, and driveway. Does not include telecom, licensing or environmental mitigations.
terminate a single gen-tie with as many as (2) outgoing lines.
New Substation Equipment
|  | Transformer Banks: | [6 empty] | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. Includes disconnects and additonal relaying.
|  |  | 230/138 kV 1-3 phase | per unit |  |  | N/A | N/A
|  |  | 500/230 kV 4-1 phase | per unit |  |  | N/A | 12180 | 500/230 kV = 1120 MVA normal rating
|  | Line Positions to terminate gen-ties and Transformer Bank positions | [6 empty] | Position cost estimate includes cost
|  |  | Single Breaker (add third breaker to breaker and a half) | per unit |  |  | 716 | 2811 | of any related disconnect switches
|  |  | Breaker and a half (2CB) | per unit |  | N/A | 1056 | 3897 | and protection equipment located within
|  |  | Breaker and a half (3CB) | per unit |  |  | 1772 | 6708 | the position.
|  | Sectionalizing Breaker |  | lump sum |  | lump sum | lump sum | lump sum | Not typical, would be estimated as a Lump sum.
|  | Shunt Capacitors |  | lump sum |  | lump sum | lump sum | lump sum | Not typical, would be estimated as a Lump sum.
| Miscellaneous Equipment (see comments) | [7 empty] | If required these items will be estimated as a lump sum.
|  | Bus Tie (1CB) |  | lump sum |  | lump sum | lump sum | lump sum
|  | Shunt Reactors |  | lump sum |  | lump sum | lump sum | lump sum
|  | Phase Shifter |  | lump sum |  | lump sum | lump sum | lump sum
|  | Ground Bank |  | lump sum |  | lump sum | lump sum | lump sum
|  | Series Capacitors |  | lump sum |  | lump sum | lump sum | lump sum
|  | Static VAR Compensator (SVC) |  | lump sum |  | lump sum | lump sum | lump sum
|  | Tertiary Reactors (1 reactor, 1 bay) |  | lump sum |  | lump sum | lump sum | lump sum
| Gas Insulated Substation (in lieu of open air construction) |  |  | lump sum |  | lump sum | lump sum | lump sum | Not typical, would be estimated as a Lump sum.
Replacement Substation Equipment
|  | Circuit Breakers |  | per unit |  |  | 188 | 768 | Prices listed are for a single item. 230 kV circuit breakers are
|  | Disconnect switches (incl. steel structures and foundations) |  | per unit |  |  | 76 | 159 | single 3 phase units. 500 kV circuit breakers are single 1
|  | Line protection relays (other end of line) |  | per set |  |  | 56 | 56 | phase units. Switches and wave traps are single 1 phase
|  | Wave Trap - 1 phase only |  | per unit |  |  | 60 | 83 | units. Line protection relays are a complete line protection panel
New Protection Equipment
|  | New SPS |  | lump sum |  | lump sum | lump sum | lump sum | Costs vary widely, will be estimated as needed.
|  | SPS Relays |  | lump sum |  | lump sum | lump sum | lump sum
|  | Additional set of bushing current transformers (3) at existing CBs |  | lump sum |  | lump sum | lump sum | lump sum
Information Technology (IT) Equipment
IT interface equipment - Control Rooms
|  |  | Communication rack placed in existing B station MEER bldg |  | per set | Lump Sum | Lump Sum | Lump Sum | Will be estimated as needed.
|  |  | Comm. Rack with own environmental enclosure |  | per set | Lump Sum | Lump Sum | Lump Sum
|  |  | Full Comm. package for AA or A stations |  | per set | Lump Sum | Lump Sum | Lump Sum
|  |  | Prefab communications building |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | 48V DC power supply for comm. equipment |  | per set | Lump Sum | Lump Sum | Lump Sum
|  |  | 100' self-supporting comm. tower (3 legs) |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | 120' self-supporting comm. tower (4 legs) |  | per unit | Lump Sum | Lump Sum | Lump Sum
IT interface equipment - miscellaneous equipment
|  |  | Lightwave terminal |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | Microwave terminal and dish antennas |  | per set | Lump Sum | Lump Sum | Lump Sum
|  |  | Dehydrator for microwave antennas |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | Channel bank |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | Digital Access Cross Connect (DACS) |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | Network synchronization equipment (BITS clock) |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | Large router for network access to work bases |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | Small router for equipment monitoring, "data beyond SCADA" |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | T1 cross connect |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | Fiber to Telco connection (high voltage protected) |  | per unit | Lump Sum | Lump Sum | Lump Sum
|  |  | Satellite Terminal for "RTU only" locations |  | per unit
IT interface equipment - T/L
|  |  | Fiber optic cable on existing poles |  | per mile |  | 65.8 | N/A
|  |  | Fiber optic cable on new poles |  | per mile |  | N/A | N/A
New HV Transmission Line
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | per mile |  |  | 1459 | N/A | Assumes no environmental, permitting or ROW acquisition.
|  | Double Circuit Capable, Strung on one side, Tubular Steel Pole |  | per mile |  |  | 1138 | N/A
|  | Single Circuit, Tubular Steel Pole |  | per mile |  |  | 801 | N/A
|  | Double Circuit, Strung on both sides, Lattice Tower |  | per mile |  |  | N/A | 3829
|  | Double Circuit Capable, Strung on one side, Lattice Tower |  | per mile |  |  | N/A | 3305
|  | Single Circuit, Lattice Tower |  | per mile |  |  | N/A | 1705
|  | Wood poles |  | per mile |  |  | 428 | N/A
|  | Light Duty steel poles |  | per mile |  |  | 414 | N/A
Removal of HV Transmission Line (complete tear down)
|  | Double Circuit |  | per mile |  |  | 193 | N/A | Assumes removal of old poles, conductor, and OHGW.
|  | Single Circuit |  | per mile |  |  | 143 | N/A
Reconductor/Upgrade Transmission Line
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | per mile |  |  | 785 | N/A | Assumes removal of existing conductor and installation of new.
|  | Single Circuit, Tubular Steel Pole |  | per mile |  |  | 550 | N/A
Metering
|  | Upgrade of existing RTUs |  | lump sum |  | lump sum | lump sum | lump sum
|  | GLW Meter at Gen Site |  |  |  | lump sum | lump sum | lump sum
|  | GLW RTU at Gen Site for EMS telemetry and RTSCADA |  |  |  | lump sum | lump sum | lump sum
|  | GLW Pre-parallel inspection, compliance review for gen site |  |  |  | lump sum | lump sum | lump sum
Lump Sum costs below are in addition to per-unit or lump-sum costs listed above:
| Engineering costs |  |  | lump sum |  | lump sum | lump sum | lump sum | Will be estimated as needed.
| Capitalized Licensing and Permitting Costs, including |  |  | lump sum |  | lump sum | lump sum | lump sum
mitigation measures, FAA permits, etc.
| Civil work: Site Preparation including site grading, ground grid, |  |  |  |  | lump sum | lump sum | lump sum
| and walls/fencing/containment |  |  | lump sum
| General Facilities: station light & power, backup generator, |  |  | lump sum |  | lump sum | lump sum | lump sum
station utilities (water, gas, etc. if manned substation)
| Substation Control (MEER) Buildings |  |  | lump sum |  | lump sum | lump sum | lump sum
| Incremental cost for transmission line crossings (roads, |  |  | lump sum |  | lump sum | lump sum | lump sum
streams, rail, highway, other T\L)
| Land cost for substations and T/L ROW |  |  | lump sum |  | lump sum | lump sum | lump sum
| Incremental cost of soil/geotechnical mitigation measures |  |  | lump sum |  | lump sum | lump sum | lump sum
| Incremental environmental monitoring and mitigations |  |  | lump sum |  | lump sum | lump sum | lump sum
| Corporate Overheads (A&G, P&B, and AFUDC) |  |  | lump sum |  | lump sum | lump sum | lump sum
| Income Tax Component of Contribution (ITCC) |  |  | lump sum |  | lump sum | lump sum | lump sum

## BulkTrans Factors & Assumptions
Bulk Transmission (230 kV) Factors for use in developing cost estimates in Phase I Generator Interconnection Studies
As of January 2020
Simplified example on how to apply factors:
[10 empty] | $ millions | Apply Factor | Delta
| Hypothetical baseline cost per mile for Double Circuit 220 kV line (strung one side) using Lattice Towers: | [8 empty] | 2
Known characteristics of proposed transmission line ROW at Phase I study:
|  | Will be constructed in mountainous terrain | [7 empty] | 2 | 2.0 x 2.0 =4 | 2
No population density issues
|  | High wind-prone area (but not icy) | [7 empty] | 1.35 | 2.0 x 1.35 =2.7 | 0.7
|  |  | Total Delta (summation of applied factor) | [8 empty] | 2.7
|  |  | Estimated cost per mile | [8 empty] | 2
|  |  | Estimated cost per mile including applied factors ($ million/ mile) | [8 empty] | 4.7
|  | Factor Types: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | flat |  |  | hilly |  | mountain |  | forest
|  |  | Population density |  | rural |  | desert | suburban |  | urban/metro
|  |  | Weather study (increase in |  | 1/2" ice, or 20# wind |  |  | 1" ice, 6# wind |  | > 2" ice, 6# wind
structural steel amount and foundation volume)
|  | Factor Amounts: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  | 2.0X to 3.0X
|  |  | Population density |  |  | 1.00X to 1.10X |  |  | 1.33X |  | 1.67X
|  |  | Weather study |  |  | 1.35X |  |  | 1.45X |  | 1.60X
|  |  | Factor Type | Explanation of Factor issues and Factor multipliers
|  |  | Terrain | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
|  |  | Population density | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
|  |  | Weather study | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure types or an increased number of structures to reduce the span lengths.
Other assumptions underlying unit cost guide:
Assumption

## Escalation Rates & Factors
ESCALATION OVERVIEW :
GLW cost estimating is done in 2020 constant dollars and then escalated over the years during which the project will be
constructed, arriving at project costs in 2020 Constant Dollars Escalated to OD Year.
DEFINITIONS :
Project Cost in 2020 Constant Dollars represents the cost of the Project if all costs were paid for in 2020.
Project Cost Escalated to OD Year represents the cost of the Project if all costs were paid for in the OD Year.
Mathematical formula: Constant Dollars Escalated to OD Year | [5 empty] | = Cost in Constant Dollars + Escalation to OD Year
= Cost in Constant Dollars x Escalation Factor
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Escalation Rate | 2.489% | 1.748% | 1.746% | 2.14% | 2.32% | 2.299% | 2.299% | 2.388% | 2.388% | 2.106% | 2.294%
Escalation Factors | 1 | 1.0175 | 1.0352 | 1.0574 | 1.0819 | 1.1068 | 1.1323 | 1.1593 | 1.187 | 1.212 | 1.2398