## PGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Expected In-Service Jul 2022 TDF | Expected In-Service Oct 2022 TDF | Notes
C9P2-F17 | Panoche 115 kV circuit breakers 152 overstress | Replace Panoche 115 kV circuit breaker 152 and associated switches/relays | PG&E | C9 | Reliability | SCD overstress | Removed | [5 empty] | (blank)
19rsmt-3 | Schindler 70kV Bus Normal & Outage Overload | Upgrade Schindler 70 kV Bus to 1113 kcmil AAC | PG&E | RA-19 | Reliability | Bus Flow | Not Triggered | [5 empty] | (blank)
C13P1-KPN02 | Midway Substation 230 kV bus and 27 circuit breakers overstress | Install 2 x 16 ohm series bus reactors between Midway Substation 230 kV bus sections D and E (16 ohm parallel / 8 ohm net) | PG&E | C13 | Reliability | SCD overstress | Not Triggered |  |  |  | (blank) |  | Q4 Notes: not triggered
20rsmt-3 | Midway 230 kV Bus Section E overload mitigation | Replace limiting conductor and/or fittings on Bus Section E to achieve 3372 A min. rating | PG&E | RA-20 | Reliability | Bus Flow | In-Service |  |  | 1905-07-13 | Q3-2022 | Q3-2022 | Q4 Notes: In-Service
21rsmt-4 | Monta Vista 115 kV circuit breaker 1322 overstress | Replace Monta Vista 115 kV circuit breaker 1322 | PG&E | RA-21 | Reliability | SCD overstress | In-Service | Q4-2021 |  | 1905-07-13 | Q4-2021 | Q4-2021 | (blank)
C11P2-FC01 | Midway 500kV CB's 722 Overstress | Midway Sub: Replace 500kV CB's 722, SW's and Relays | PG&E | C11 | Reliability | SCD overstress | In-Service | Q3-2022 |  | 1905-07-13 | Q3-2022 | Q3-2022 | Q4 Notes: In-Service
C11P2-FP01 | Midway 500 kV circuit breakers 732, 802, 832 and 842 overstress | Replace Midway 500 kV circuit breakers 732, 802, 832 and 842 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Service | Q4-2022 |  | 1905-07-13 | Q3-2022 | Q3-2022 | Q4 Notes: In-Service
C12P1-NPN02 | Lodi Substation 60 kV circuit breakers 12 and 22 overstress | (blank) | PG&E | C12 | Reliability | SCD overstress | In-Service | Q3-2020 |  |  | Q2-2022 | Q2-2022 | (blank)
C12P2-GRNU3 | Midway Substation 500 kV CB 712 overstress | Replace Midway Substation 500 kV CB 712 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Service | Q4-2022 |  | 1905-07-13 | Q1-2022 | Q1-2022 | (blank)
C12P2-KC01 | Midway Substation 500kV CB 722 Overload mitigation | Replace Midway 500 kV CB 722 to achieve 3600 A emergency rating | PG&E | C12 | Reliability | Bus Flow | In-Service | Q4-2022 |  | 1905-07-13 | Q3-2022 | Q3-2022 | Q4 Notes: In-Service
C9P2-N09 | Re-conductor Stockton A-Weber #3 60 kV Line (Stockton A-Hazelton Jct) | Re-conductor 0.9 mi of Stockton A-Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC. | PG&E | C9 | Deliverability | Re-conductor | In-Service | Q1-2022 |  | 1905-07-10 | Q1-2022 | Q1-2022 | (blank)
20rsmt-7a | Tesla 500 kV circuit breaker 632 overstress | Replace Tesla 500 kV circuit breaker 632 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Service | Q4-2021 |  |  | Q4-2021 | Q4-2021 | (blank)
22rsmt-3 | Metcalf 230 kV Substation Circuit Breaker #No 292 Upgrade | Upgrade Metcalf Circuit Breaker #292 due to overstress issues | PG&E | (blank) | Capacity | (blank) | In-Service |  | TBD | 1905-07-14 | Q4-2025 | Q3-2022 | Q4 Notes: In-Service
C12P2-LDNU3 | Bellota-Riverbank-Melones Sw Sta 115 kV Line 115 kV Line Reconductor | Reconductor a total of 17 miles of Bellota-Riverbank-Melones SW STA 115 kV Line with 477 ACSS | PG&E | C12 | Deliverability | Re-conductor | Initiating |  |  | 1905-07-13 | Q4-2027 | Q4-2027 | Q4 Notes: Scoping
C12P2-LDNU1 | Ripon-Manteca 115 kV Line Reconductor | Reconductor Ripon-Manteca 115 kV line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total) | PG&E | C12 | Deliverability | Re-conductor | Initiating |  |  | 1905-07-13 | Q4-2027 | Q4-2027 | (blank)
C12P2-LDNU2 | Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line Reconductor | Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV line 25.23 miles section of various conductors from 018/115-043/277 | PG&E | C12 | Deliverability | Re-conductor | Initiating |  |  | 1905-07-13 | Q4-2027 | Q4-2027 | (blank)
C12P2-LDNU4 | Stanislaus-Melones SW STA-Riverbank Jct Sw Sta 115 kV Line Reconductor | Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/043 | PG&E | C12 | Deliverability | Re-conductor | Initiating |  |  | 1905-07-13 | Q4-2027 | Q4-2027 | (blank)
C12P1-NPT04 | Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 overstress | Replace Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | Initiating | Q3-2023 |  | 1905-07-13 | Q4-2024 | Q1-2025 | Q4 Notes: Work reprioritization.
22rsmt-4 | New 230 kV switching station to loop Dos Amigos – Panoche # 3 230 kV | Build a new 2 bay 230 kV BAAH switching station to loop in the Dos Amigos – Panoche # 3 230 kV Line requiring access road, land and land rights acquisition and permitting, remote end protection upgrades, and OPGW/fiber telecommunication work | PG&E | RA-22 | Deliverability | New Station | Initiating |  |  |  | (blank) | Q4-2028 | Q4 Notes: 2022 Reassessment determined new Dos-Amigos-Panoche #3 Switching Station to be looped in with scope to remove Dos Amigos PP dependencies.
20rsmt-4 | Metcalf 115kV breakers Overstress (almost all breakers) (Reactors) | Install 2 x 5.3 ohm reactors at Metcalf 115 kV between bus sections D and E | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | Q4-2024 |  | 1905-07-12 | Q3-2025 | Q4-2025 | Q4 Notes: Design change from 115kV CB overstress replacement to Transformer Reactor Installs on 230kV
20rsmt-6 | 20RSMTRAS-02 (Reliability) to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | 20RSMTRAS-02 RAS to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | PG&E | RA-20 | Reliability | RAS (Reliability) | In-Flight | Q2-2023 |  | 1905-07-12 | Q4-2023 | Q4-2023 | Q4 Notes: Material on Order
21rsmt-1 | Henrietta Substation 70kV CBs 12 and 72 Overstress | Henrietta Sub: Replace 70kV CB 12 & 72 and switches. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | Q2-2025 |  | 1905-07-13 | Q1-2025 | Q3-2026 | Q4 Notes: Work reprioritization.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 4 - incl CB182) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | Q1-2027 |  | 1905-07-13 | Q4-2025 | Q4-2027 | Q4 Notes: Work reprioritization.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 1) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | Q3-2021 |  | 1905-07-13 | Q2-2023 | Q4-2024 | Q4 Notes: Work reprioritization.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 3 - incl CB262) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | Q1-2026 |  | 1905-07-13 | Q4-2024 | Q4-2026 | Q4 Notes: Work reprioritization.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 2 - incl CB282) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | Q2-2025 |  | 1905-07-13 | Q4-2023 | Q4-2025 | Q4 Notes: Work reprioritization.
21rsmt-SCD-23 | El Cerrito G 115kV CB 112, 142, 132 Overstress | Replace Overstressed Circuit Breakers | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | Q1-2024 |  |  | Q3-2024 | Q4-2025 | Q4 Notes: Work reprioritization.
C11P2-NP01 | Contra Costa 230kV SW's 601, 603 overload | Contra Costa PP: Replace 230kV SW's 601 & 603 and jumpers. | PG&E | C11 | Reliability | Bus Flow | In-Flight |  |  | 1905-07-13 | Q3-2025 | Q2-2025 | (blank)
C11P2-NP02 | Contra Costa 230kV Bus Sections D, E and F and circuit breaker 820 overload | Contra Costa PP: Reconductor Bus Sections D, E and F. Replace circuit breaker 820. | PG&E | C11 | Reliability | Bus Flow | In-Flight |  |  | 1905-07-13 | Q3-2025 | Q2-2025 | (blank)
C11P2-NR01 | Cottonwood Substation 230 kV circuit breakers 232, 242 overstress | Replace Cottonwood Substation 230 kV circuit breakers 232, 242 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Flight | Q1-2025 |  | 1905-07-14 | Q2-2024 | Q3-2025 | Q4 Notes: Work reprioritization.
C12P1-GPT01 | Ames Distribution 115 kV circuit breaker 132 overstress | Replace Ames Distribution 115 kV circuit breaker 132 | PG&E | C12 | Reliability | SCD overstress | In-Flight | Q4-2025 |  | 1905-07-11 | Q3-2024 | Q1-2026 | Q4 Notes: Work reprioritization.
C12P1-NPT01 | Gold Hill Substation 115 kV circuit breakers 142 and 172 overstress | Replace Gold Hill Substation 115 kV circuit breakers 142 and 172 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | Q2-2024 |  | 1905-07-13 | Q4-2023 | Q3-2025 | Q4 Notes: Work reprioritization. Q2 2025 CB 142. Q3 2025 CB172
C12P2-GRNU2 | Gates Substation 230 kV Bus Overstress | Install series bus reactors between Gates Substation 230 kV bus sections E and F | PG&E | C12 | Reliability | SCD overstress | In-Flight | Q1-2024 |  | 1905-07-14 | Q4-2025 | Q1-2025 | Q4 Notes: Schedule Improvement. Subject to change through the design process.
C12P2-PNU-02 | Gates 230 kV circuit breakers 352, 362 and 372 overstress mitigation (Cap Banks) | Replace Gates 230 kV circuit breakers 352, 362 and 372 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Flight | Q4-2022 |  | 1905-07-14 | Q1-2023 | Q2-2023 | (blank)
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 overstress | Replace Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 | PG&E | C13 | Reliability | SCD overstress | In-Flight | Q4-2024 |  | 1905-07-10 | Q2-2025 | Q1-2026 | Q4 Notes: Work reprioritization. Q4 2022 Interim Solution removes the overstress condition until CBs replaced.
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | PG&E | C13 | Reliability | SCD overstress | In-Flight | Q4-2022 |  | 1905-07-10 | Q4-2022 | Q4-2022 | (blank)
C8P2-15 | Cottonwood Substation 230 kV Circuit Breaker 522 and 542 Overstress | Cottonwood Substation 230 kV CB Overstress: Replace CB 522 & 542 (rated @ 34.5KA, overstress close-in fault is 35,179A or 2%, 679A). | PG&E | C8 | Reliability | SCD overstress | In-Flight | Q1-2023 |  | 1905-07-10 | Q3-2023 | Q3-2024 | Q4 Notes: Long Lead Time delay
C9P2-F13-F15 | Gates 230kV Bus Section E and CB 312, 322, 2102, 2202 overload mitigation (BAAH) | Gates Substation 230 kV circuit breakers 312, 322, 2102, 2202 overload – convert bus section E to BAAH and move Panoche-Gates #1 and #2 230 kV lines and Q1117/Q1120/Q1139/Q1242/Q1243 into bus section E | PG&E | C9 | Reliability | Bus Flow | In-Flight | Q3-2021 |  | 1905-07-11 | Q2-2023 | Q1-2023 | (blank)
(blank) | Morro Bay MPAC | New 230kV MPAC building relocates 230kV equipment from existing Control Building | PG&E | n/a | Reliability | MPAC | In-Flight | Q4-2025 |  |  | (blank) | Q1-2027 | Q4 Notes: Work reprioritization impacting EGI projects depending on DTT and Point Of Interconnection at Morro Bay
(blank) | Tesla MPAC | New 230kV MPAC building relocates 230kV equipment from existing Control Building | PG&E | n/a | Reliability | MPAC | In-Flight | Q2-2024 |  |  | (blank) | Q4-2024 | Q4 Notes: Work reprioritization impacting EGI projects depending on DTT and Point Of Interconnection at Morro Bay
C11P2-ND03 | North Dublin-Cayetano 230 kV Line | Reconductor North Dublin-Cayetano 230 kV Line 2.63 miles OH Line & 2.82 UG cable with new UG cable 797 MVA/2000 A | PG&E | C11 | Deliverability | Re-conductor | In-Flight | Q4-2024 | Q3-2023 | 1905-07-13 | Q4-2025 | Q1-2025 | Q4 Notes: Schedule Improvement. Subject to change through the design process. Tracking to 30% Design complete by Dec 2022
21rsmt-5 | Palo Alto 115 kV circuit breakers 412 and 442 overstress | Replace Palo Alto 115 kV circuit breakers 412 and 442 with 63 kA interrupting capability | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | Q4-2026 |  | 1905-07-13 | Q2-2026 | Q4-2027 | Q4 Notes: Work reprioritization.
C8P2-10 | QC8RAS-02 SPS (Deliverability Triggered RNU) | QC8SPS-02 SPS to modify the existing Hatchet Ridge SPS to trip Q1106 200 MW wind and Hatchet Ridge 102 MW wind for thermal overloads on the Q1106 SS-Cottonwood, Carberry SS-Round Mountain or Pit #3-Carberry SS 230 kV Lines. | PG&E | C8 | Deliverability | RAS (Deliverability) | In-Flight | Q1-2023 |  | 1905-07-09 | Q3-2023 |  | Q4 Notes: This work is being delayed due to triggering project schedule changes.
C8P2-3 | QC8RAS-08 RAS (Deliverability Triggered RNU) | QC8RAS-08 RAS to trip Generation offline for outage AND overload of either Gates 500/230 kV Transformer Bank 11 or 12 | PG&E | C8 | Deliverability | RAS (Deliverability) | In-Flight |  |  | 1905-07-09 | Q4-2023 | Q2-2024 | Q4 Notes: Sequencing aligning with Gates 500kV STATCOM activities
C8P2-1 | Re-conductor Borden-Gregg #1 230 kV Line | Re-conductor 6.25 mi Borden-Gregg #1 230 kV Line with 1113 ACSS and upgrade equipment to 2000 A minimum (this is the existing Borden-Gregg 230 kV Line) | PG&E | C8 | Deliverability | Re-conductor | In-Flight | Q3-2025 | Q1-2023 | 1905-07-09 | Q1-2026 | Q1-2026 | (blank)
C9P1-F12 | Re-conductor Borden-Gregg #2 230 kV Line | Re-conductor 6.25 mi Borden-Gregg #2 230 kV Line with 1113 ACSS | PG&E | C9 | Deliverability | Re-conductor | In-Flight | Q1-2025 | Q1-2023 | 1905-07-09 | Q2-2025 | Q2-2025 | (blank)
C9P1-F11 | Re-conductor Dos Amigos PP-Panoche #3 230 kV Line | Re-conductor 23.63 mi Dos Amigos PP-Panoche #3 230 kV Line with 795 ACSS | PG&E | C9 | Deliverability | Re-conductor | In-Flight | Q3-2024 |  | 1905-07-09 | Q2-2025 | Q2-2025 | Q4 Notes: 2022 Reassessment determined new Dos-Amigos-Panoche #3 Switching Station to be looped in with scope to remove Dos Amigos PP dependencies.
C11P2-ND01 | Re-conductor Fulton-Hopland 60 kV Line (Fitch Mountain Tap-Geysers Jct) | Re-conductor Fulton-Hopland 60 kV Line (Fitch Mountain Tap 009/005A-Geysers Jct 016/004) ~7 mi total length with 715 AAC | PG&E | C11 | Deliverability | Re-conductor | In-Flight | Q2-2025 | Q4-2023 | 1905-07-10 | Q4-2027 | Q4-2025 | Q4 Notes: Scoping
C9P2-N02 | Re-conductor Fulton-Hopland 60 kV Line (Geysers Jct-Cloverdale Jct-Hopland) | Re-conductor 24.21 mi Fulton-Hopland 60 kV Line (Geysers Jct 016/003A-Cloverdale Jct 026/002-Hopland) with 715 AAC and upgrade any limiting equipment | PG&E | C9 | Deliverability | Re-conductor | In-Flight | Q2-2025 | Q4-2023 | 1905-07-11 | Q4-2027 | Q4-2025 | Q4 Notes: Scoping
C8P2-6 | Re-conductor Los Banos-Q779 SS #1 230 kV Line | Re-conductor 4.5 mi Los Banos-Padre Flat SS #1 230 kV Line with 1113 ACSS and upgrade equipment to 1900 A. | PG&E | C8 | Deliverability | Re-conductor | In-Flight | Q4-2022 |  | 1905-07-09 | Q1-2023 | Q4-2022 | (blank)
C8P1-35 | Re-conductor Los Banos-Quinto SS 230 kV Line | Re-conductor 6.11 mi Quinto Sw Sta-Los Banos 230 kV Line with super bundled 795 ACSS | PG&E | C8 | Deliverability | Re-conductor | In-Flight | Q1-2022 |  | 1905-07-09 | Q2-2023 | Q2-2023 | Q4 Notes: Materials Received
C8P1-34 | Re-conductor Padre Flat SS-Panoche #1 230 kV Line | Re-conductor 32.59 mi Q779/Padre Flat SS-Panoche #1 230 kV Line with 795 ACSS | PG&E | C8 | Deliverability | Re-conductor | In-Flight | Q3-2023 | Q4-2022 | 1905-07-09 | Q2-2024 | Q2-2024 | (blank)
C12P1-NPT03 | Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 overstress | Replace Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | Q2-2021 |  | 1905-07-12 | Q4-2023 | Q2-2024 | Q4 Notes: Work reprioritization.
20rsmt-5 | Tesla 500 kV circuit breaker 612 overstress | Replace Tesla Substation 500 kV CB 612 and associated switches/relays | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | Q2-2024 |  | 1905-07-12 | Q3-2024 | Q3-2024 | (blank)
20rsmt-7b | Tesla 500 kV circuit breakers 542 and 642 overstress | Replace Tesla 500 kV circuit breakers 542 and 642 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | Q1-2024 |  | 1905-07-12 | Q2-2024 | Q3-2024 | (blank)
C12P1-GCR01 | Moraga 115 kV circuit breakers 582, 612, 622, 642 and 712 overstress | Replace Moraga 115 kV circuit breakers 582, 612, 622, 642 and 712 | PG&E | C12 | Reliability | SCD overstress | Not Triggered | Q2-2029 |  |  | Q4-2028 | Q4-2029 | Q4 Notes: Work reprioritization.

## SCE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Construction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Estimated In-service Date July 2022 TDF | Current Estimated In-service Date | Comments
SCE-C8P2-POS-C11 | 220 kV line position at Colorado River Substation. | 220 kV line position at Colorado River Substation | SCE | C11 Phase II | CANU-IR | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Recommending removal of project as not applicable to the TDF scope
SCE-C3C4P2-SCD | Vincent CB Upgrades | Upgrade Vincent 500kV CBs | SCE | C3&4 Phase II | RNU | SCD Over Stress | Cancelled | N/A | N/A | N/A | N/A | N/A | N/A | Project replaced by new project PIN8455 identified via ATRA
SCE-PreC12-SCD-Vincent-C12 | Vincent 500kV SCD (Install seven (7) sets of 500 kV TRV) |  | SCE | C12 Phase II | CANU-GR | SCD Over Stress | Cancelled | N/A | N/A | N/A | N/A | N/A | N/A | Project replaced by new project PIN8455 identified via ATRA
SCE-TCP2-E-R1 | Colorado River Substation Expansion - Reliability | Expand Colorado River substation and install Colorado River 1AA bank | SCE | TC Phase II | RNU | Capacity Increase | In-service Nov-21 | N/A | N/A | 2010-12-01 | N/A | In-service Nov-21 | In-service Nov-21 | Trigger Year based on GIA date.
SCE-TCP2-E-R5 | Colorado River Corridor RAS - CR Transformers | Develop a SPS to trip 500 MW TC2 generation at the Colorado River 500/220 kV Substation to mitigate the overload by on one AA bank for the loss of another AA bank (T‐1 contingency) | SCE | TC Phase II | RNU | RAS/CRAS | In-service May-22 | 2021-05-01 | N/A | 2018-01-01 | 2021-12-01 | In-service May-22 | In-service May-22 | Trigger Year based on GIA date.
SCE-C3C4P2-E-D1 | Red Bluff 2AA | Install Red Bluff 500/230kV bank No. 2 | SCE | C3&4 Phase II | DNU | Capacity Increase | In-service May-22 | 2021-02-01 | N/A | 2014-10-01 | 2021-10-01 | In-service May-22 | In-service May-22 | Trigger Year based on GIA date.
SCE-C8P2-E-CR-M | West of Colorado River CRAS -Include monitoring infrastructure relays to monitor the Red Bluff 2nd AA bank | West of Colorado River CRAS -Include monitoring infrastructure relays to monitor the Red Bluff 2nd AA bank | SCE | C8 Phase II | RNU | RAS/CRAS | In-service May-22 | 2021-03-01 | N/A | 2018-12-01 | 2021-08-01 | In-service May-22 | In-service May-22 | Project need was postponed from original ISD due to delays from projects in the triggering queue. Trigger Year based on GIA date.
SCE-C11P2-NOL-R3 | Upgrade Roadway 115kV Operating/Transfer Bus | Upgrade Roadway 115 kV Operating/Transfer Bus with 1590 kcmil ACSR conductor or equivalent. | SCE | C11 Phase II | GRNU | Substation Expansion | In-service Jun-22 | 2022-04-01 | N/A | 2020-11-01 | 2022-10-01 | In-service Jun-22 | In-service Jun-22 | Trigger Year based on GIA date.
SCE-C11P2-EOP-R1 | Lugo - Victorville CRAS - monitoring infrastructure | Infrastructure to convert the Lugo - Victorville RAS to centralized RAS platform | SCE | C11 Phase II | GRNU | RAS/CRAS | Design | 2024-06-30 | N/A | 2019-11-01 | 2024-06-01 | 2025-06-01 | 2025-06-30 | Trigger Year based on the date of the QC11 Phase 2 report.
SCE-C10P2-E-R3 | West of Colorado River CRAS Inland/Devers Extension - monitoring infrastructure | Infrastructure to convert the formally referred to as the New Devers RAS and the Inland RAS to centralized RAS platform | SCE | C10 Phase II | RNU | RAS/CRAS | Construction | 2021-01-01 | N/A | 2018-12-01 | 2021-10-01 | 2023-03-01 | 2023-03-30 | Mar-23 is for Inland/Devers Extension CRAS monitoring equipment & Aug-25 is for the Alberhill modification to the CRAS. Trigger Year based on GIA date.
SCE-C11P2-N-L1 | Pardee – Pastoria- Warne 220 kV T/L rating increase | Upgrade terminal equipment and fix ground clearance for Pardee – Pastoria- Warne 230kV line | SCE | C11 Phase II | LDNU | Capacity Increase | Design | 2023-01-31 | N/A | 2020-07-01 | 2022-10-15 | 2023-06-01 | 2023-12-31 | Project delayed from original ISD due to delays in triggering queue projects.
SCE-C9P2-N-R1 | Whirlwind AA Bank CRAS Monitoring Infrastructure | Implement Whirlwind AA Bank CRAS - monitoring infrastructure | SCE | 2018 Reassessment | GRNU | RAS/CRAS | Design | 2022-10-31 | N/A | 2020-07-01 | 2022-11-01 | 2023-02-01 | 2023-06-30 | Trigger Year based on 2020 Reassessment.
SCE-2021RA-E-R6 | West of Colorado River CRAS Palo Verde Extension | Include Palo Verde sub in WOCR CRAS | SCE | 2021 Reassessment | RNU | RAS/CRAS | Cancelled | N/A | N/A | 2019-12-01 | 2023-12-01 | 2023-12-01 | N/A | Trigger Year based on Upgrade Facility Agreement.
SCE-C9C10-N | Windhub AA Bank cRAS - monitoring infrastructure | Windhub AA Bank cRAS - monitoring infrastructure | SCE | 2021 Reassessment | GRNU | RAS/CRAS | Construction | 2022-06-01 | N/A | 2021-08-01 | 2022-11-01 | 2023-02-01 | 2023-03-31 | Trigger Year based on 2021 Reassessment
SCE-TCP2-EOP-R4 | Lugo - Victorville RAS | Trip generation for Eldorado area 500kV line outages. | SCE | TC Phase II | RNU | RAS/CRAS | Permitting | 2022-12-01 | N/A | 2011-09-01 | 2020-12-01 | 2023-05-01 | 2023-12-31 | Trigger Year based on GIA. Additional working areas caused SCE to refile application
SCE-C9P2-NOL-R1 | New North of Lugo RAS - Backbone Portion | New North of Lugo RAS combining HDPP RAS and Calcite RAS | SCE | C9 Phase II | RNU | RAS/CRAS | Design | 2024-06-30 | N/A | 2017-11-01 | 2024-06-01 | 2025-06-01 | 2025-06-30 | Trigger Year based on Letter Agreement.
SCE-C12P2-N-R3 | Moorpark CRAS: monitoring infrastructure | New Moorpark CRAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | 2023-12-01 | N/A | 2021-07-01 | 2024-07-01 | 2024-07-01 | 2024-07-31 | Trigger year based on GIA.
SCE-C12P2-N-R2 | Tehachapi CRAS: monitoring infrastructure addition | Add N-1 to RAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | 2023-10-01 | N/A | 2021-02-01 | 2024-09-01 | 2024-09-01 | 2025-04-30 | Trigger year based on GIA. Schedule adjusted to meet earliest generation in-service date
SCE-C72021-EOP | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | SCE | 2021 Reassessment | RNU | RAS/CRAS | Design | 2024-06-01 | N/A | 2021-08-01 | 2025-06-01 | 2025-06-01 | 2025-06-30 | Trigger Year based on 2021 Reassessment report date.
SCE-C11P2-E-R1 | West of Colorado Rivers CRAS - Inland/Devers Extension – additional remote monitoring | Additional infrastructure to convert the formally known Inland Empire RAS to centralized RAS platform | SCE | C11 Phase II | GRNU | RAS/CRAS | Design | Pending | N/A | 2018-12-01 | 2025-08-01 | 2027-04-01 | 2027-04-30 | Contingent on Alberhill licensing schedule. Trigger Year based on GIA date.
SCE-C11P2-E-R1-C12 | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub |  | SCE | C12 Phase II | PNU | RAS/CRAS | On Hold | Pending | N/A | 2020-03-01 | 2026-10-01 | 2026-10-01 | 2027-06-30 | Trigger Year based on Riverside Transmission Reliability Project CPUC CPCN approval date.
PIN8455 | Vincent 500 kV Circuit Breaker Upgrade | ATRA: Upgrade 3 500 kV CB, and install 4 TRV Capacitor to increase breaker rating | SCE | ATRA 2021 | SCE | SCD Over Stress | Cancelled | N/A | N/A | 2021-12-01 | 2023-12-01 | 2023-12-01 | N/A | Project cancelled due to circuit breaker re-rate
PIN8449 | Whirlwind 230 kV Circuit Breaker Upgrade | ATRA: Install 2 TRV to upgrade breaker rating | SCE | ATRA 2021 | SCE | SCD Over Stress | Cancelled | N/A | N/A | 2021-12-01 | 2023-12-01 | 2023-12-01 | N/A | Project cancelled due to circuit breaker re-rate
PIN8450 | Vista 230 kV Circuit Breaker Upgrade | ATRA: Upgrade one 230 kV circuit breaker | SCE | ATRA 2021 | SCE | SCD Over Stress | Cancelled | N/A | N/A | 2021-12-01 | 2023-12-01 | 2023-12-01 | N/A | Project cancelled due to circuit breaker re-rate
PIN8454 | Antelope 230 kV Circuit Breaker Upgrade | ATRA: Replace 2 Circuit breakers | SCE | ATRA 2021 | SCE | SCD Over Stress | Cancelled | N/A | N/A | 2021-12-01 | 2023-12-01 | 2023-12-01 | N/A | Project cancelled due to circuit breaker re-rate
TBD | South of Vincent CRAS | Add lines south of Vincent to the Tehachapi CRAS | SCE | C13 Phase II | RNU | RAS/CRAS | Initiation | Pending | Pending | 2021-12-31 | 2026-04-30 | New | 2026-04-30 | Trigger Year based on GIA date.
TBD | Calcite Substation | New four position 220 kV switchrack | SCE | Serial LGIP | GRNU | New Substation | Permitting | Pending | Pending | 2020-11-30 | 2024-01-31 | New | TBD | Trigger Year based on GIA date.

## SDGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Estimated In-service Date July 2022 TDF | Current Estimated In-service Date | Comments
SDGE-EXISTING-RNU-01 | Imperial Valley Existing/Modified RAS' | Imperial Valley Existing/Modified RAS' | SDGE |  | PNU |  | Operational |  |  |  |  | Operational
SDGE-EXISTING-RNU-7.1 | Existing Miguel BK 80 / 81 | Existing Miguel BK 80 / 81 | SDGE |  | PNU |  | Operational |  |  |  |  | Operational
SDGE-EXISTING-RNU-02 | Existing Otay Mesa RASs | Existing Otay Mesa RASs | SDGE |  | PNU |  | Operational |  |  |  |  | Operational
SDGE-EXISTING-RNU-04 | Existing ECO/BUE anti-islanding scheme for radial generators | Existing ECO/BUE anti-islanding scheme for radial generators | SDGE |  | PNU |  | Operational |  |  |  |  | Operational
SDGE-C11-PHII-RNU-02 | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | SDGE | C11 Phase II | PNU | Reliability | In construction |  | N/A | N/A | 2022-06-01 | In service | In service | Placed in service on 6/18/22
SDGE-C07-PHI-RNU-01 | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | SDGE | C7 Phase I | PNU | Reliability | In design |  | N/A | N/A | 2023-06-01 | 2023-06-01 | 2023-06-01 | New CEC RAS - will mitigate the overload of 23006 for the loss of 23010 AND 23002; protect TL23011B from overloading for loss of 23003; and protect 23003 from overloading for the loss of TL23011. On track for Jun-2023 ISD
SDGE-C08-PHII-RNU-04 | Participate in the proposed RAS to protect TL23003 & TL23011 Encina to San Luis Rey 230 kV lines (Proposed grouping RAS to protect Encina/Pen/San Luis Rey 230kV Lines) | Proposed RAS to Protect TL23003 Encina - San Luis Rey 230 kV line | SDGE | C8 Phase II | PNU
SDGE-PRE-AMEND-RNU-01.2 | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | SDGE |  | CANU-GR

## GLW-VEA
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Estimated In-service Date July TDF 2022 | Current Estimated In-service Date | Comments
VEA-C6P2-EOP-R5 | VEA Vista RAS | VEA Vista RAS: Install a new RAS to protect Jackass Flats - Mercury Switch 138 kV line under contingency conditions | VEA | C6 Phase II | RNU
VEA-C6P2-EOP-R5 | VEA Vista RAS | VEA Vista RAS: Install a new RAS to protect Jackass Flats - Mercury Switch 138 kV line under contingency conditions | VEA | C6 Phase II | RNU | Thermal | Cancelled | N/A | N/A | N/A | N/A | N/A | N/A | IC choose to re-build Jackass Flats - Mercury Switch line in place of Vista RAS. Completed June-21.
VEA-C8P2-VEA-R2 | Innovation RAS | Install a new Innovation RAS | GLW | C8 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-11-22 | 2022-11-22 | Supply chain issues pushed out the project outside the outage windows. As a result, a new outage plan was developed and the new anticipated in-service date is November 2022
VEA-C9P2-EOP-R3 | Innovation RAS (VEA-GLW portion) | New Innovation RAS (include Desert View RAS from QC8) to trip generation under N-1 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-11-22 | 2022-11-22 | Supply chain issues pushed out the project outside the outage windows. As a result, a new outage plan was developed and the new anticipated in-service date is November 2022
VEA-C9P2-EOP-R4 | Sloan Canyon RAS (fka Bob RAS - VEA-GLW portion) | New Sloan Canyon RAS to trip generation under N-1 and N-2 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-11-22 | 2022-11-22 | Supply chain issues pushed out the project outside the outage windows. As a result, a new outage plan was developed and the new anticipated in-service date is November 2022
GLW-2021-EOP-L1 | Trout Canyon - Sloan Canyon 230kV line upgrade | Trout Canyon - Sloan Canyon 230kV line upgrade | GLW | 2021 Reassessment | LDNU |  |  |  |  | N/A | 2025-12-31 | 2025-12-31 | 2025-12-31