## Data Specification
|  | RC Operating Procedure Attachment |  | Procedure No. | RC0120A
|  |  |  | Version No. | 6.4
|  |  |  | Effective Date | 2024-04-01
RC West IRO-010 Data Specification |  |  |  | Distribution Restriction: None
Section | Category | Request Number | Responsible Party | Data Item | Data Transfer Method | Data Update Frequency | Data Request Effective Date | Related NERC Standards (including but not limited to) | CAISO Guidance Document
1 | Real-time Network Measurement Data | 1.1 | Transmission Operator | Real-time status points for all BES equipment and other non-BES equipment that impact the BES | ICCP | By exception | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.2 | Transmission Operator | Real-time MW measurements, or ampere if MW not available, for all BES equipment and other non-BES equipment that impact the BES | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.3 | Transmission Operator | Real-time Mvar measurements for all BES equipment and other non-BES equipment that impact the BES | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.4 | Transmission Operator | Voltage measurements for all busses associated with BES equipment and other busses associated with non-BES equipment that impact the BES | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.5 | Transmission Operator | Designated WECC Transfer Path data for paths listed in RC0120, section regarding data requests 5.7 – 5.9 1) Actual MW 2) Scheduled MW, Total Transfer Capability (TTC) | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.6 | Transmission Operator | LTC tap position measurements for LTCs with high side voltage > 100 kV | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.7 | Transmission Operator | Phase shifter phase tap position | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.8 | Transmission Operator | MW/Mvar measurements for measured loads. These loads may be equivalent representations of your distribution system. | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.9 | Transmission Operator | RAS Arming Status for all schemes that have an impact to the BES. An armed RAS implies that it is 1) In service and 2) Ready to perform an action (trip a unit for example) if a specific condition occurs on the power system. | ICCP (preferred, if available) or phone notification to the Reliability Coordinator System Operator upon status change | ICCP – 10 sec, or if ICCP unavailable then Phone Notification – as soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.1 | Transmission Operator | RAS in-service status for all schemes that have an impact to the BES | ICCP (preferred, if available) or phone notification to the Reliability Coordinator System Operator upon status change | ICCP – 10 sec, or if ICCP unavailable then Phone Notification – as soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.11 | Transmission Operator | RAS associated analog arming values (e.g. Amp, MW, Mvar). | ICCP (preferred, if available) or phone notification to the Reliability Coordinator System Operator upon status change | ICCP – 10 sec, or if ICCP unavailable then Phone Notification – as soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.13 | Transmission Operator | Dynamic line and transformer ratings that vary with real-time system or ambient conditions, as applicable to FERC 881 | ICCP | At least hourly or on demand with temperature changes | 2025-07-01
1 | Real-time Network Measurement Data | 1.14 | Transmission Operator | Any TOP-provided stability limitation that the RC, in collaboration with the TOP, determines to require submission in Real-time. | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
1 | Real-time Network Measurement Data | 1.15 | Transmission Operator | Real-time status points for RC identified PMU installations on the WISP network consisting of measurement and communication equipment, if applicable | PMU | 30 samples per second | 2020-01-01 | IRO-002-7 D.A.7.2.
2 | Real-time Balancing Authority Data | 2.1 | Balancing Authority | Instantaneous BA Area Load | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.2 | Balancing Authority | BA Net Actual Interchange (as used in ACE calculation) | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.3 | Balancing Authority | BA Net Scheduled Interchange (as used in ACE calculation) | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.4 | Balancing Authority | BA Instantaneous ACE that is used for NERC reporting requirements | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.5 | Balancing Authority | BAAL high and low limits instantaneous, or if unable then one minute average values | ICCP | 10 sec for instantaneous or 1 min | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.6 | Balancing Authority | System frequency at multiple locations within the BA as requested by the RC | PMU (preferred, if available) or ICCP | PMU - 30 samples per second or if via ICCP - 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.7 | Balancing Authority | BA Scheduled frequency | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.8 | Balancing Authority | BA Area (BAA) Contingency Reserve obligation (as defined in the NERC Glossary and WECC Regional Standards) or, if the BAA is part of a Reserve Sharing Group (RSG), the BAA's allocated obligation as defined by the RSG. 1) Total Required, 2) Total Actual Available, 3) Spinning Required, 4) Spinning Actual Available | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.9 | Balancing Authority | BA Area Actual Generation Total | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.1 | Balancing Authority | Actual Most Severe Single Contingency (MSSC) of your Balancing Authority. This value should not be a static PMax of the largest generator, rather the actual MW output. This is NOT a request for the RSG MSSC. | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.11 | Balancing Authority or Generator Operator | Real-time status points (UCON status point designating unit is or is not connected to the network) for BES connected and BES impacting units 10 MW or greater, or those units with automatic voltage control or black start capability | ICCP | By exception | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.12 | Balancing Authority | All BES connected and BES impacting generators with SCADA, 10 MW or greater - real-time net MW output | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.13 | Balancing Authority | All BES connected and BES impacting generators with SCADA, 10 MW or greater - real-time net Mvar output | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.14 | Balancing Authority | Dynamic Schedule real-time dynamic signal used in ACE calculation for each dynamic schedule. This is not the anticipated energy on the tag, rather a real-time calculation of MWs associated with the Dynamic Schedule. | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.15 | Balancing Authority | Pseudo tie real-time dynamic signal. This is a real-time calculation of MWs associated with each pseudo tie used in ACE calculation. Note: This is not an alternate method for inclusion in congestion management procedures pursuant to INT-004-3.1. | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.16 | Balancing Authority | Balancing Authority total wind MW output. This is a single value - summation of all wind generation currently online. This value should represent wind generation at the BES level. | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.17 | Balancing Authority | Balancing Authority total solar MW output. This is a single value - summation of all solar generation currently online. This value should represent solar generation at the BES level. | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.18 | Balancing Authority | ATEC component of ACE | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.19 | Balancing Authority | BA frequency bias if a dynamic bias is used | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.2 | Balancing Authority | Meter error component of ACE | ICCP | 10 sec | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.21 | Balancing Authority | Actual change in status of BES generating unit Automatic Voltage Regulators (AVR), BES Power System Stabilizers (PSS) or BES alternative voltage controlling device lasting for 30 minutes or longer | ICCP (preferred, if available) or phone notification to the Reliability Coordinator System Operator | As soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
2 | Real-time Balancing Authority Data | 2.22 | Balancing Authority | Balancing Authority total storage MW output. This is a single value - summation of all storage production and consumption online. This value should represent storage at the BES level. | ICCP | 10 sec | 2021-01-01
2 | Real-time Balancing Authority Data | 2.23 | Balancing Authority | Balancing Authority total storage State of Charge. This is a single value - summation of the current MWh available within all storage. This value should represent storage at the BES level. | ICCP | 10 sec | 2021-01-01
2 | Real-time Balancing Authority Data | 2.24 | Balancing Authority | Balancing Authority gross storage charging MW. This is a single value - summation of all storage consumption online. This value should represent storage at the BES level. | ICCP | 10 sec | 2024-01-01
2 | Real-time Balancing Authority Data | 2.25 | Balancing Authority | All BES connected and BES impacting storage generators with SCADA - real-time State of Charge | ICCP | 10 sec | 2024-08-01
2 | Real-time Balancing Authority Data | 2.26 | Balancing Authority | All BES connected and BES impacting hybrid (more than one resource type) generators with SCADA - real-time MW and State of Charge for each component of the hybrid resource, if applicable | ICCP | 10 sec | 2024-08-01
3 | Forecast Data | 3.2 | Balancing Authority | Hourly Total Contingency Reserve forecast of the BA Area (BAA) for the next calendar day, or, if the BAA is part of a Reserve Sharing Group (RSG), the BAA's forecast allocated obligation for the next calendar day as defined by the RSG. 1) Contingency Reserve Availability 2) Contingency Reserve Requirement | EIDE | Daily submission by 10 AM Pacific Prevailing Time | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | TOP-002-5 | RC EIDE Interface Specification
3 | Forecast Data | 3.3 | Balancing Authority | Hourly BAA load forecast. Required each day for the current day through the next four calendar days, not to exceed 7 days. | ALFS/ EIDE | Daily submission by 9:45 AM Pacific Prevailing Time | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | TOP-002-5 | RC ALFS Interface Specification RC EIDE Interface Specification
3 | Forecast Data | 3.4 | Balancing Authority | Hourly BAA load forecast. Required each hour for the next 4 hours. | ALFS/ EIDE | If changed, hourly submission received 10 min prior to the hour | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | TOP-002-5 | RC ALFS Interface Specification RC EIDE Interface Specification
3 | Forecast Data | 3.5 | Balancing Authority | Hourly Resource Dispatch MW for all BAA generation that qualifies per the BES definition and any non-BES generation (As determined the RC) that are necessary to support the accuracy of Operational Planning Analyses and to determine SOL exceedance on BES Facilities. Required each day for the next four calendar days, not to exceed 7 days. | BSAP/ RC-BSAP/ EIDE | Daily submission by 10 AM Pacific Prevailing Time | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | TOP-002-5 | RC Base Schedule Interface Specification Web Services RC EIDE Interface Specification
3 | Forecast Data | 3.8 | Balancing Authority | Hourly Resource Dispatch MW for all BAA generation that qualifies per the BES definition and any non-BES generation (as determined by the BA and RC) that is necessary to support the accuracy of Operational Planning Analyses and to determine SOL exceedance on BES Facilities. Required each hour for the next four hours. | BSAP/ RC-BSAP/ EIDE | If changed, hourly submission received 10 min prior to the hour | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | TOP-002-5 | RC Base Schedule Interface Specification Web Services RC EIDE Interface Specification
4 | Documentation and Procedures | 4.1 | Balancing Authority and Transmission Operator | Emergency Operations Plans | 1) For RC review - upload to RC Portal > Plan Review Submissions library or email procedurecontrol@caiso.com 2) After RC review - upload to BA/TOP Procedures library | Anytime the plan is updated | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | EOP-011-2 IRO-010-4
4 | Documentation and Procedures | 4.2 | Transmission Operator | Restoration Plans | 1) For RC review - upload to RC Portal > Plan Review Submissions library or email procedurecontrol@caiso.com 2) After RC review - upload to BA/TOP Procedures library | Annually and/or anytime the plan is updated | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | EOP-005-3
4 | Documentation and Procedures | 4.3 | Transmission Operator | Under voltage and under frequency load shed Plans | Upload to RC Portal > BA/ TOP Procedures library | Anytime the plan is updated | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | PRC-006-WECC-CRT-3
4 | Documentation and Procedures | 4.4 | Transmission Operator | Path procedures (for WECC Paths listed in RC0120, section regarding data requests 5.7 – 5.9 that impact SOL/IROL, neighboring RCs) | Upload to RC Portal > BA/ TOP Procedures library | Anytime the plan is updated | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
4 | Documentation and Procedures | 4.5 | Transmission Operator | Geomagnetic Disturbance Operating Procedures | 1) For RC review - upload to RC Portal > Plan Review Submissions library or email procedurecontrol@caiso.com 2) After RC review - upload to BA/TOP Procedures library | Anytime the plan is updated | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | EOP-010-1
4 | Documentation and Procedures | 4.6 | Balancing Authority and Transmission Operator | Area specific Operating Plans, Procedures or Processes for mitigating SOLs, IROLs or other stability limitations | Upload to RC Portal > BA/ TOP Procedures library | Anytime the plan is updated | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
4 | Documentation and Procedures | 4.7 | Balancing Authority and Transmission Operator | Loss of Control Center Functionality procedures, which may include protocols for evacuation, back up communications and back up control center. Note: These documents should not include CIP sensitive materials. | Upload to RC Portal > BA/ TOP Procedures library | Anytime the plan is updated | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | EOP-008-2
4 | Documentation and Procedures | 4.8 | Balancing Authority and Transmission Operator | Other Plans, Procedures, Protocols or Process documents as requested by the RC, including fire/weather mitigation and/or regulatory limitations that could cause inability to follow Operating Instructions. | Upload to RC Portal > BA/ TOP Procedures library | Anytime the plan is updated | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
4 | Documentation and Procedures | 4.9 | Transmission Operator | System voltage limits and stability limitations. These documents include: Voltage Limit Tables, Transient Stability Limit Tables, Credible Multiple Contingency Lists, and Regionally Critical Multiple Contingencies.​​​​​​ | 1) Upload to RIMS 2) Share with TOPs via RC Portal > SOL Methodology library | Consistent with SOL Methodology | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | FAC-014-3 R3
4 | Documentation and Procedures | 4.1 | Transmission Operator | List of BES exceptions, which should include the list of facilities that are “Not in the normal bright line 100kV” in accordance with NERC’s BES definition and guidelines. The list should include all facilities < 100 kV that are considered BES as well as the list of all facilities > 100 kV that are considered NOT BES. | 1) Upload to RIMS 2) Share with TOPs via RC Portal > TOP-003 Reference Data library | One initial list; updates as necessary to reflect any changes to the list | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-002-7
5 | Scheduled and Unscheduled Outage Information | 5.1 | Balancing Authority and Transmission Operator | For Outages identified prior to Real-time/ Same-day study window - forced generation and transmission outages, 30 minutes or more in duration, on Facilities/equipment identified in the In-Scope Outage Categories section of the CAISO Outage Coordination Process | webOMS, even if submitted after the fact (via user interface or API) | As soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.2 | Balancing Authority | For Outages identified prior to Real-time/ Same-day study window - any planned individual generating unit, or based on plant configuration, derate of > 50 MW reduction of available capacity (30 minutes or more in duration) shall be submitted per the instructions of the webOMS Manual and per the Short-Range Study Window Process Outage Submission Timeline | webOMS via user interface or API | In accordance with the Short-Range Submittal Timeline specified in the CAISO Outage Coordination Process | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.3 | Balancing Authority | For Outages identified prior to Real-time/ Same-day study window - any generating unit, or based on plant configuration, derate of > 50 MW reduction of available capacity (other than planned derates, and 30 minutes or more in duration), shall be submitted per the instructions of the webOMS Manual | webOMS via user interface or API | As soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.4 | Balancing Authority | For Outages identified prior to Real-time/ Same-day study window - any Forced generating unit, or based on plant configuration, derate of > 50 MW reduction of available capacity (30 minutes or more in duration) | webOMS, even if submitted after the fact (via user interface or API) | As soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.5 | Balancing Authority | For Outages identified prior to Real-time/ Same-day study window - any planned Automatic Voltage Regulator (AVR) or Power System Stabilizer (PSS) outage (30 minutes or more in duration) on a BES facility | webOMS via user interface or API | In accordance with the Short-Range Submittal Timeline specified in the CAISO Outage Coordination Process | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.6 | Balancing Authority | For Outages identified prior to Real-time/ Same-day study window - any Automatic Voltage Regulator (AVR) or Power System Stabilizer (PSS) outage (other than planned outages, and 30 minutes or more in duration) on a BES facility | webOMS via user interface or API | As soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.7 | Transmission Operator | For Outages identified prior to Real-time/ Same-day study window - Total Transfer Capability (TTC) values for WECC Paths that impact SOL, IROLs, neighboring RCs adjusted to account for planned outages or operating conditions. See path listing in RC0120 - Guidelines for IRO-010 RC Data Specification and Collection. | PLC via User Interface | In accordance with the Short-Range Submittal Timeline specified in the CAISO Outage Coordination Process | 2019-11-01 | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.8 | Transmission Operator | For Outages identified prior to Real-time/ Same-day study window - Total Transfer Capability (TTC) values for WECC Paths that impact SOL, IROLs, neighboring RCs adjusted to account for unplanned outages or operating conditions. See path listing in RC0120 - Guidelines for IRO-010 RC Data Specification and Collection. | PLC via User Interface | As soon as practicable | 2019-11-01 | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.9 | Transmission Operator | For Outages identified prior to Real-time/ Same-day study window - Total Transfer Capability (TTC) adjustments for WECC Paths that impact SOL/IROL, neighboring RCs due to a Forced outage. See path listing in RC0120 - Guidelines for IRO-010 RC Data Specification and Collection. | PLC via User Interface | As soon as practicable | 2019-11-01 | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.1 | Balancing Authority and Transmission Operator | For Outages identified prior to Real-time/ Same-day study window - planned outages of telemetering and control equipment of 30 minutes or more in duration, with potential impacts to SE results, SOLs, IROLs, RAS visibility, or could lead to loss of visibility for an area, or communication channels impacting system protection that may result in EMS alarms. | webOMS via user interface or API | As soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1, TOP-001-6 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.11 | Balancing Authority and Transmission Operator | For Outages identified prior to Real-time/ Same-day study window - unplanned telemetering and control equipment outages of 30 minutes or more in duration, with potential impacts to SE results, SOLs, IROLs, RAS visibility, or could lead to loss of visibility for an area, or communication channels impacting system protection that may result in EMS alarms. | webOMS (via user interface or API); include Grid Messaging System (GMS) if impacts adjacent entities | As soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1, TOP-001-6 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.13 | Transmission Operator | Operational Planning Analysis and Operating Plan(s) for next-day operations | Upload to RC Portal > Entity Studies library Operating Plan(s) to webOMS outage cards as applicable | When Operational Planning Analysis is completed and when Operating Plans have been identified | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | TOP-002-5 | CAISO Operational Planning Analysis document, RC 0620
5 | Scheduled and Unscheduled Outage Information | 5.15 | Balancing Authority | Deliverability capability constraints for capacity and energy reserve requirements shall be communicated to the RC | Upload to RC Portal > Entity Studies library | When next-day studies identify constraints | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | TOP-002-5 | CAISO Operational Planning Analysis document, RC 0620
5 | Scheduled and Unscheduled Outage Information | 5.16 | Transmission Operator | For Outages identified prior to OPA and Real-time timeframes - any planned Transmission outages on Facilities/equipment identified in the In-Scope Outage Categories section of the CAISO Outage Coordination Process. | webOMS via user interface or API | As soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.17 | Balancing Authority | For Outages in real-time - any forced or urgent generation unit derate of 50 MW reduction or greater of available capacity, 30 minutes or more in duration | webOMS, even if submitted after the fact (via user interface or API) | As soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.18 | Balancing Authority | For Outages in real-time - any forced or urgent generation unit connected to BES >= 20 MVA gross nameplate rating or >=75 MVA facility aggregate rating, 30 minutes or more in duration | webOMS, even if submitted after the fact (via user interface or API) | As soon as practicable; with as much advanced notice as possible. | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
5 | Scheduled and Unscheduled Outage Information | 5.19 | Balancing Authority | For Outages in real-time - any forced Black Start certified unit, 30 minutes or more in duration | webOMS, even if submitted after the fact (via user interface or API) | As soon as practicable | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live | IRO-017-1 | CAISO Outage Coordination Process, RC 0630 WebOMS User Manual, RC 0630A
6 | Power System Modeling Information | 6.1 | Transmission Operator or Balancing Authority | Network topology changes (additions, changes, removals) for generation, transmission, and load equipment and facilities plus ICCP SCADA mapping | CIM file or equivalent file(s) with sufficient model details uploaded to RIMS; if modeling method may impact SE solution (i.e. double modeling), submit required switch positions via WebOMS until facility is placed into service | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-01-01 |  | RIMS User Guide Modeling Submission Checklist WebOMS User Manual, RC 0630A
6 | Power System Modeling Information | 6.8.1 | Transmission Operator or Balancing Authority | Generator attributes: gross and net MW maximum and reactive capability curves (if no curve available, Mvar minimum and maximum required); List of units normally on AVR- a list shall include voltage set point(s) with High and Low range representing voltage regulation criteria. | SGIT or GRDT (EIM Customers) for resource attributes – refer to RIMS User Guide | 10 business days for existing resources | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live |  | RIMS User Guide, Modeling Submission Checklist
6 | Power System Modeling Information | 6.8.2 | Transmission Operator or Balancing Authority | Generating unit(s) minimum: 1. Design temperature; or 2. Historical operating temperature; or 3. Current cold weather performance temperature determined by an engineering analysis. Extreme Cold Weather Temperature (ECWT), if known All temperatures will be communicated in degrees Fahrenheit (F). If Generator Cold Weather Critical Component freeze protection measures will be implemented prior to upcoming winter season Net Winter Capacity (MW), with scenarios defined in NERC Alert 3 | Extreme Weather Template to RIMS | 10 business days for existing resources In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library for new resources | 2023-12-01 | EOP-011-2 IRO-010-4 | RIMS User Guide, Modeling Submission Checklist
6 | Power System Modeling Information | 6.10.1 | Transmission Operator | Seasonal Facility Ratings and overload relay trip settings (including time-delay) on those Facilities (transformers and transmission lines) that are part of Bulk Electric System and their overload trip settings are below 125% of the highest Facility rating. | CIM file or equivalent file with sufficient model details, plus RC Data Gathering Template for additional ratings - uploaded to RIMS; if between model builds then submit via equipment rating change in webOMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library; if between model builds then same day via webOMS | 2020-01-01 | FAC-008-3 R7, R8 PRC-023-5 FAC-014-3 R3 | RIMS User Guide, Modeling Submission Checklist, WebOMS User Manual, RC 0630A
6 | Power System Modeling Information | 6.10.2 | Transmission Operator | Dynamic Facility Ratings on those Facilities (transformers and transmission lines) that are part of Bulk Electric System, as applicable to FERC 881 | FERC 881 Dynamic MVA ICCP Template uploaded to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2025-07-01 |  | RIMS User Guide, Modeling Submission Checklist
6 | Power System Modeling Information | 6.11 | Transmission Operator or Balancing Authority | List of all transmission and generation ICCP object ID data available for the entity's area. Also include SCADA definition relating to each object ID. | RC Portal > TOP-003 Reference library | Initial provision and then as changes to the points list occur | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
6 | Power System Modeling Information | 6.12 | Transmission Operator or Balancing Authority | Dated BES system one-line diagrams and RC requested Non-BES system one-line diagrams | RC Portal > TOP-003 Reference library | Initial provision and then whenever changes occur | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live
6 | Power System Modeling Information | 6.13 | Transmission Operator or Balancing Authority | Longitude and latitude for each substation with voltage levels > 100 kV or with total plant generation >= 50 MW | Shapefile or RC Data Gathering Template uploaded to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-01-01 |  | RIMS User Guide, Modeling Submission Checklist
6 | Power System Modeling Information | 6.14 | Transmission Operator or Balancing Authority | Line routing for all lines 100 kV and above | Shapefile or RC Data Gathering Template uploaded to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-01-01 |  | RIMS User Guide, Modeling Submission Checklist
6 | Power System Modeling Information | 6.15 | Transmission Operator or Balancing Authority | List of shunt devices normally on AVR. These shunts are those that can automatically connect/disconnect at a specified voltage set point without operator intervention. The list shall include the voltage set point(s) and any time delays prior to automatic switching. | CIM file or Shunt Equipment Data Template uploaded to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-01-01 |  | RIMS User Guide, Modeling Submission Checklist
6 | Power System Modeling Information | 6.16 | Balancing Authority | List of all pseudo ties and jointly owned units by the owner BA. List of all Dynamic Schedules by the owner BA as requested by the RC. | JOU and Dynamic Transfer Template uploaded to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2021-04-01 |  | RIMS User Guide, Modeling Submission Checklist
6 | Power System Modeling Information | 6.17 | Transmission Operator or Balancing Authority | List of all normally open circuit breakers, disconnects and switches that control the connectivity of transmission branch elements and Facilities; list shall include unique status for all applicable seasons. The list is applicable to BES Facilities/elements and non-BES Facilities/elements that impact the BES (see Note 1), and non-BES Facilities/elements specifically requested by the RC. Examples of applicable switching devices include those associated with: * Transmission lines * Transformers * Series Compensation * Station bus switches including auxiliary buses and bus tie switches Examples of non-applicable devices include: Shunt devices | CIM file or RC Data Gathering Template uploaded to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-01-01 |  | RIMS User Guide, Modeling Submission Checklist
6 | Power System Modeling Information | 6.18 | Transmission Operator | RAS scheme information for all schemes or at the discretion of the RC. This requires logic diagrams and documentation on the function of each RAS. | RC Portal > BA/TOP Procedures library | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-01-01 | IRO-002-7 PRC-012-2
6 | Power System Modeling Information | 6.19 | Transmission Operator or Balancing Authority | Description and modeling information for all non-RAS automatic post-contingency actions based on certain parameters such as under voltage or overloaded facilities. This may include, but is not limited to, certain generator run-back schemes or under voltage facility tripping schemes. | Upload to RC Portal > BA/TOP Procedures library | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-01-01
6 | Power System Modeling Information | 6.23 | Transmission Operator or Balancing Authority | Equipment Long Name to Resource Description Framework (RDFID) mapping | CIM file or RC Data Gathering Template uploaded to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-01-01 |  | RIMS User Guide, Modeling Submission Checklist
6 | Power System Modeling Information | 6.24 | Transmission Operator or Balancing Authority | Contingency definition additions, modifications, and deletions | Contingency Definition Template uploaded to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library 10 business days for existing resources | 2020-01-01 |  | RIMS User Guide, Modeling Submission Checklist
6 | Power System Modeling Information | 6.25 | Transmission Operator or Balancing Authority | Dynamic Model for Transient Stability Analysis in the same GE PSLF format that is being submitted to WECC base case development. Additionally, include mapping between the EMS model and the GE PSLF dynamic model. | Upload to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-09-11 | MOD-032-1 MOD-033-2
6 | Power System Modeling Information | 6.26 | Transmission Operator or Balancing Authority | EMS screenshot of the RAS display used by TOP or BA System Operators showing the RAS points, if available. | Upload to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-09-11
6 | Power System Modeling Information | 6.27 | Transmission Operator or Balancing Authority | RAS information outlined in RC0690. | See RC0690 | See RC0690 | 2021-01-01 | PRC-012-2 | RC0690 RC0690A
7 | Other Operational Information | 7.6 | Balancing Authority and Transmission Operator | See RC Operating Procedure RC0130 Notification Requirements for Real-time Events for full list of requirements. This procedure addresses real-time transmission and balancing area events and outages identified in the OPA or Real-time timeframes that require immediate notification to the RC operator by phone, the Grid Messaging System (GMS) and/or CAISO Outage Management System (OMS). | See RC0130 | See RC0130 | Shadow Ops 5/1/19 for 7/1/19 go-live; Shadow Ops 9/1/19 for 11/1/19 go-live |  | RC0130 Notification Requirements for Real-Time Events

## Exceptions
|  | RC Operating Procedure Attachment |  | Procedure No. | RC0120A
|  |  |  | Version No. | 6.4
|  |  |  | Effective Date | 2024-04-01
RC West IRO-010 Data Specification |  |  |  | Distribution Restriction: None
Category | Request Number | Entity | Exclusion and Agreement Rationale
Real-time Network Measurement Data | All | RDNG | WASN submits on behalf of RDNG.
Real-time Network Measurement Data | 1.1 - 1.4 | TBC | Per the agreement between TBC and the CAISO, the CAISO shall transmit all applicable real-time measurement data to the RC on TBC’s behalf.
Real-time Network Measurement Data | 1.2 | LST | Not applicable to LST area.
Real-time Network Measurement Data | 1.4 | LST | Not applicable to LST area.
Real-time Network Measurement Data | 1.5 | All except BPA, CAISO, IPCO, LADWP, NEVP, NWMT, PAC | All except the entities listed are not a WECC Path operator.
Real-time Network Measurement Data | 1.6 | HHWP, LST, TBC | TBC’s Transformer tap changers are only used to regulate the 180.5 kV voltage for the HVDC Converter System, not the 230 kV and 115 kV buses in Pittsburg and Potrero, respectively as used in typical AC systems.
Real-time Network Measurement Data | 1.7 | HHWP, LST, TBC | TBC does not have phase shifter tap positions.
Real-time Network Measurement Data | 1.8 | AVRN, GRID, GWA, WWA, LST, TBC | These entities do not have load.
Real-time Network Measurement Data | 1.9, 1.10, 1.11 | AEPC, AVRN, BANC, CHPD, DOPD, GCPD, GWA, HHWP, LST, MID, RDNG, SCL, SNPD, SVP, TBC, TIDC, TPWR, TSGT, VEA, WWA | These entities do not own or operate a Remedial Action Scheme.
Real-time Network Measurement Data | 1.13 | Various | Entities have provided this information but is pending CAISO implementation, if applicable.
Real-time Network Measurement Data | 1.14 | HHWP, LST, RDNG, TBC | These entities do not have any stability limitations.
Real-time Balancing Authority Data | 2.1 | AVRN, GRID, GWA, WWA | These entities do not have load.
Forecast Data | 3.3, 3.4 | AVRN, GRID, GWA, WWA | These entities do not have load.
Documentation and Procedures | 4.1 | MATL | MATL does not have an emergency plan.
Documentation and Procedures | 4.3 | LST, TBC | LST and TBC do not have UVLS or UFLS.
Documentation and Procedures | 4.4 | All except BPA, CAISO, IPCO, LADWP, NEVP, NWMT, PAC | All except the entities listed are not a WECC Path operator.
Documentation and Procedures | 4.5 | RDNG | Any applicable RDNG equipment is included in WASN GMD procedure.
Documentation and Procedures | 4.6 | LST | LST does not have stability limitations.
Documentation and Procedures | 4.9 | AEPCO, LST, MATL, SCL | AEPCO is in CAISO OP3100B. MATL is provided by NWMT. LST is provided by HZWT.
Documentation and Procedures | 4.10 | PSEI, SCL | No BES exceptions to be posted.
Scheduled and Forced Outage Information | All | BANC | BANC will delegate to their SCs the BA approval on generation outages. From a TOP standpoint, the SC is the TOP.
Scheduled and Forced Outage Information | All | AVA, PNM | Created ACL groups for delegating submission of generation outages to their GOPs.
Scheduled and Forced Outage Information | All | RDNG | RDNG submits to webOMS via SMUD applications.
Scheduled and Forced Outage Information | 5.7 - 5.9 | All except BPA, CAISO, IPCO, LADWP, NEVP, NWMT, PAC | All except the entities listed are not a WECC Path operator.
Scheduled and Forced Outage Information | 5.13 | AEPCO | CAISO will provide information on behalf of AEPCO.
Power System Modeling Information | All | LST | LST is provided by HZWT.
Power System Modeling Information | 6.11 | TBC | CAISO will provide information on behalf of TBC.
Power System Modeling Information | 6.15 | AEPCO, BANC, CHPD, HHWP, MATL, PSEI, RDNG, SNPD, TBC, VEA | These entities do not have shunt devices.
Power System Modeling Information | 6.17 | MATL | These entities do not have a list of normally open CB, switches, and disconnects.
Power System Modeling Information | 6.18, 6.26, 6.27 | AEPC, AVRN, BANC, CHPD, DOPD, GCPD, GWA, HHWP, LST, MID, RDNG, SCL, SNPD, SVP, TBC, TIDC, TPWR, TSGT, WWA | These entities do not own or operate RAS.
Power System Modeling Information | 6.19 | HHWP, TBC, VEA | These entities do not own or operate non-RAS automatic post-contingency devices.

## Version History
|  | RC Operating Procedure Attachment | Procedure No. | RC0120A
|  |  | Version No. | 6.4
|  |  | Effective Date | 2024-04-01
RC West IRO-010 Data Specification |  | Distribution Restriction: None
Operationally Affected Parties
Shared with the Public and RC West BAs and TOPs.
Version History
Version Number | Changes |  | Effective Date
1 | Approved by Steering Committee Comparison to Peak Data Specification: New req #s - 4.7 and 4.8 - split from 4.6 in order to make requirements more explicit, 5.16 - gap in Peak's data spec, 6.21 - split from 6.10 to make requirements more explicit, 7.6 - replaces current requirements with cross reference to real time notification procedure; Retired req #s: 3.1, 3.6, 3.7, 3.9 - 3.12, 7.1 - 7.5 Updated req #s - updated data items for clarification - 1.14, 2.5, 2.11 - 2.13, all section 3 items, 4.4, 4.6, 5.1 - 5.4, 5.7 - 5.11, 6.10, 6.12, 6.17, 6.18; updated transfer methods - 1.9, 1.11, 2.6, all sections 3, 4, 5, 6; updated data frequency - 2.6, 3.3, 3.4, 3.8, 5.2, 5.5, 5.7, 5.10, 6.1, 6.2, 6.10, 6.11, 6.12 Updates to reqs 5.1 - 5.11 to add language "For Outages identified prior to Real-time/ Same-day study window", update to 5.9 to remove Notification to RCSO, update to 5.16 to add "for Outages identified prior to OPA and Real-time timeframes" and updates to 5.1, 5.4, 5.9 to remove phone and GMS from Data Transfer Method; and 7.6 to add "Outages identified in the OPA or Real-time timeframes" |  | 2019-01-23
2 | See yellow highlights throughout document: Section 1 - 1.9, 1.11 - updated frequency to match 1.10; Section 3 - 3.2 – Updated Data Item to clarify requirements, also citing EIDE Interface Specification for guidance; 3.5 – Updated Data Item to change “Commitment” to “Dispatch”, Data transfer method - added BSAP; 3.8 - Data transfer method - added BSAP; Section 4 - 4.1 – 4.8 – clarified specific RC Portal libraries for document uploads; Section 5 - 5.13 – 5.15 - clarified specific RC Portal libraries for document uploads; Section 6 - throughout clarified upload locations and templates if applicable; 6.22 – new item List of BES exceptions; 6.23 - new item Equipment Long Names to RDFID mapping |  | 2019-07-01
2.1 | URGENT CHANGE for 11/1 - See yellow highlights in document: Section 5 - 5.7-5.9 - Changed submission method from webOMS to PLC, effective date of 11/1/2019, and CAISO guidance documents to include RC0630, RC0630A, and RC0130. Added West (RC West) to title to be consistent with RC0120B. |  | 2019-11-01
3 | Section 1 - Added request 1.15. Section 4 – Expanded 4.7 to clarify this requirement should not include CIP sensitive materials. Replaced 6.21, 6.22 with 4.9, 4.10. Changed data transfer method of 4.9. Section 5 - Updated 5.10 data transfer frequency to "as soon as practicable" and included "30 minutes or more in duration" to the description; Consolidated 5.14 into 5.13; Clarified CAISO guidance document on entire section. Removed COS references. Section 6 - Consolidated 6.2-6.7 and 6.9 into 6.1. Updated the data update frequency, effective date, and CAISO guidance document for 6.1, 6.8.1, 6.10, 6.13-6.17, 6.20, 6.23. Updated data update frequency for 6.11. Expanded 6.12 to construction diagrams, updated data transfer method and data update frequency. Removed state and city from 6.13. Combined 6.20 into 6.10. Changed responsible party for 6.1, 6.11-15, 6.17, and 6.23. Updated data frequency for 6.18 and 6.19. Added request 6.24. Errata Change: Reviewed changes with Data Exchange Working Group. |  | 2020-01-01
4 | Section 4 - Updated applicable NERC standards on item 4.9 Section 6 - Added request 6.25, 6.26, and 6.27. Clarified data transfer method for requests 6.13-6.17, 6.23, and 6.24. Reviewed changes with the Data Exchange Working Group and Operations Planning Working Group on 4/16/20 and on 6/4/20. Errata Change: Annual Review. |  | 2020-06-26
4.1 | Section 2 - Added requests 2.22 and 2.23. Section 6 - Updated 6.1 data transfer method and CAISO guidance document to include webOMS for instances such as double modeling. Added tab for exceptions to data requests. Minor format and grammar edits. |  | 2020-11-02
5 | Annual Review: Added exceptions to data requests. Modified language in request 6.16. Reviewed changes with the Data Exchange Working Group on 3/9/21. Updated NERC Standards referenced in Data Specification tab. |  | 2021-04-01
5.1 | Added and clarified exceptions to data request. |  | 2021-11-01
5.2 | Annual Review: Added exceptions to data requests. |  | 2022-05-03
6 | Annual Review: Removed exceptions to data request. Clarified RDFID in 6.23. Added data request 6.8.2 from discussions with DEWG on 9/7/22 and Joint Cold Weather Task Force. Added data requests 5.17, 5.18, and 5.19 for items communicated in real-time via webOMS that were previously listed in RC0130. Removed RC0130 reference from outage data requests 5.1, 5.4, and 5.9 prior to real-time / OPA process. Minor format and grammar edits. (Published as future effective for 4/01/23) |  | 2023-04-01
6.1 | Publishing these changes as current update and future change will be published as version 6.2 and effective 4/01/23 (To follow). Annual Review: Removed exceptions to data request. Clarified RDFID in 6.23. Section 4: Updated data transfer method on 4.9 and 4.10 to match SOL methodology. Added data requests 5.17, 5.18, and 5.19 for items communicated in real-time via webOMS that were previously listed in RC0130. Removed RC0130 reference from outage data requests 5.1, 5.4, and 5.9 prior to real-time / OPA process. Minor format and grammar edits. |  | 2023-01-24
6.2 | Added data request 6.8.2 from discussions with DEWG on 9/7/22 and Joint Cold Weather Task Force. Updated NERC Standard EOP-011 reference. Updated remaining instances of ISO and CISO to CAISO, and minor format and grammar edits. |  | 2023-04-01
6.3 | Updated data request 6.8.2 from discussions with DEWG on 9/13/23 and Joint Cold Weather Task Force, per NERC Alert 3. Added a note to 6.8.2 In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library for new resources. Updated data requests 1.13 and 6.10.2 in preparation of FERC Order 881 on dynamic ratings. Updated template name for request 6.15. Added request 2.24 based on feedback regarding battery storage ICCP data. 10/17/23 - Errata Change: Updated 6.10.1 for RC Data Gathering Template, System Voltage Limits and Stability Limits Template change due to FAC-11, FAC-14 Standard change which has impact on the RC SOL methodology. The effective start date of the new templates is 12/27/23, which will be modeled with a production date of April 2024. |  | 2023-10-12
6.4 | Annual Review: Request 1.5 and 4.4 - Updated language for clarity; Added new data request items 2.25 for storage resources and 2.26 for hybrid resources. Request 4.10 - Updated to add also sharing the list of BES exceptions with neighboring TOPs within RC Portal; Requests 4.9 and 6.10.1 – updated FAC-014-3 R3 references. Added to Exceptions tab – see yellow highlights. |  | 2024-04-01