## menu
All costs are $x1,000
SCE Generation Interconnection Unit Cost Guide - as of 4-1-09 |  |  |  | "Voltages" | 230 kV | 500 kV | Notes/Comments:
Equipment Categories |  |  |  | Units |  |  | Unit costs for equipment at lower voltages (33 kV, 66 kV, 115 kV, etc.) will be estimated on an as-needed basis
New Substation Equipment
|  | Complete Loop-in Substation, equipped with one line position |  |  | 21800 | 40200 | Includes all necessary equipment, including the
|  | to terminate a single gen-tie |  |  |  |  | operating buses, one double-breaker line position
on a breaker-and-a-half (BAAH) configuration
for the gen-tie, one three-breaker line position
on a BAAH configuration to loop in the
transmission line, substation control building
(MEER), and protection relays. Also includes
base costs of site preparation, grounding grid,
fencing, and driveway.
|  | Transformer Banks: |  |  |  |  | Unit cost of transformer banks
|  |  | 500/230 kV 4-1 Phase | per unit |  | 41000 | reflects cost of the highest MVA
|  |  | 500/230 kV 3-1 Phase | per unit |  | 31500 | rated transformer for the given
|  |  | 500/115 kV 1-3 Phase | per unit |  | 16100 | voltage
|  |  | 230/115 kV | per unit | 8200
|  |  | 230/66 kV | per unit | 7700
|  | Line Positions to terminate gen-ties and Transformer Bank positions |  |  |  |  | Position cost estimate includes cost
|  |  | Single Breaker (add third breaker to breaker and a half) | per unit | 1500 | 6200 | of any related disconnect switches
|  |  | Breaker and a half (2CB) | per unit | 2800 | 7500 | and protection equipment located within
|  |  | Breaker and a half (3CB) | per unit | 3800 | 12100 | the position
|  |  | Double Breaker (2CB, double bus) | per unit | 2500
|  | Double Operating Bus Sections - 2 new buses, spanning 2 positions |  | per unit | 700 | 2100 | typical configuration for 500 kV, includes "pair" of North/South or East/West buses
|  | Double Operating Bus Sections - 2 new buses, spanning 4 positions |  | per unit | 800 |  | typical configuration for 230 kV, includes "pair" of North/South or East/West buses
|  | Double Operating Bus Sections - 2 bus extensions, spanning 2 positions |  | per unit | 500 | 1600 | used in substation expansion
|  | Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  | per unit | 600 |  | used in substation expansion
|  | Sectionalizing Breaker |  | per unit | 1000 | 3100 | includes cost of position
|  | Shunt Capacitors |  | per unit | 4200 | 26000 | includes cost of CB
Miscellaneous Equipment (see comments)
|  | Bus Tie (1CB) |  | site specific |  |  | These items are rarely required for
|  | Shunt Reactors |  | site specific |  |  | high-voltage substations. If required,
|  | Phase Shifter |  | site specific |  |  | would be estimated as a lump sum.
|  | Ground Bank |  | site specific
|  | Series Capacitors |  | site specific
|  | Static VAR Compensator (SVC) |  | site specific
|  | Tertiary Reactors (1 reactor, 1 bay) |  | site specific
| Gas Insulated Substation (GIS, in lieu of open air construction) |  |  | site specific |  |  | not typical, would be estimated as a
lump sum, if GIS required
Replacement Substation Equipment
|  | Line drops - 3 phases |  | per unit | 110 | 220 | Any site-specific, or other non-typical
|  | Circuit Breakers (including replacement of foundation) |  | per unit | 620 | 2200 | equipment would be estimated as a lump sum
|  | Circuit Breakers (without TRV caps) |  | per unit | 520 | 2000
|  | Transient recovery voltage capacitors (set of 3, separate from CBs) |  | per unit | 150 | 200
|  | Disconnect switches (incl. steel structures and foundations) |  | per unit | 250 | 500
|  | Line protection relays (other end of line) |  | per set | 180 | 250
|  | Wave Trap - 1 phase only |  | per unit | 70 | 120
|  | Wave Trap removal |  | per unit | 40 | 230
New Protection Equipment
|  | New SPS |  | site specific |  |  | costs vary widely, will be lump sum estimate
|  | SPS Relays |  | site specific |  |  | costs vary widely, will be lump sum estimate
Information Technology (IT) Equipment
IT interface equipment - Control Rooms
|  |  | Full Telecomm. package for AA or A stations | per set | 110 | 110 | excludes battery room, cable trays, power supply (in MEER bldg cost)
|  |  | Prefab communications building | per unit | 390 | 390 | If needed to build from scratch
|  |  | 48V DC power supply for comm. equipment | per set | 100 | 100 | excludes batteries (in MEER bldg cost)
|  |  | 100' self-supporting comm. tower (3 legs) | per unit | 370 | 370
|  |  | 120' self-supporting comm. tower (4 legs) | per unit | 450 | 450 | any towers over 120' will be lump sum estimates due to high permit costs
IT interface equipment - miscellaneous equipment
|  |  | Lightwave terminal | per unit | 140 | 140 | one needed for each comm. system connected (SPS requirement)
|  |  | Microwave terminal and dish antennas | per set | 340 | 340 | one set typically needed for each end of path, includes cost of FCC license
|  |  | Dehydrator for microwave antennas | per unit | 12 | 12
|  |  | Channel bank | per unit | 40 | 40 | also referred to as a multiplexer
|  |  | Digital Access Cross Connect (DACS) | per unit | 190 | 190
|  |  | Network synchronization equipment (BITS clock) | per unit | 80 | 80
|  |  | Large router for network access to work bases | per unit | 140 | 140 | Selection of large or small router
|  |  | Small router for equipment monitoring, "data beyond SCADA" | per unit | 30 | 30 | depends on amount of substation automation and data requirements
|  |  | T1 cross connect | per unit | 4 | 4 | Interconnects new facility to existing network
|  |  | Fiber to Telco connection (high voltage protected) | per unit | 90 | 90 | for subs requiring local phone service
IT interface equipment - T/L
|  |  | Fiber optic cable on existing poles | per mile | 70 | 70 | Fiber optic cable on new T/L included in
|  |  | Fiber optic cable on new poles | per mile | 90 | 90 | transmission line cost per mile
New Transmission Line
|  | Double Circuit, Strung on both sides, Lattice Tower |  | per mile | 2500 | 5000 | Unit cost per mile shown is based on
|  | Double Circuit, Strung on one side, Lattice Tower |  | per mile | 2000 | 4500 | flat land/rural setting. Additional factors apply
|  | Single Circuit, Lattice Tower |  | per mile | 1500 | 2600 | for hilly (1.35X-1.5X), mountainous (2.0X),
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | per mile | 6100 |  | and forested (3.0X) terrain (see factors tab)
|  | Double Circuit, Strung on one side, Tubular Steel Pole |  | per mile | *** |  | Factors also apply for suburban (1.33X)
|  | Single Circuit, Tubular Steel Pole |  | per mile | 5000 |  | or urban (1.67X) population density.
*** Not recommended by SCE Trans. Engineers
| Removal of Transmission Line (complete tear down) | [5 empty] | Cost of removal only, assume any rebuild
|  | Double Circuit |  | per mile | 1000 |  | would use "new transmission line" from
|  | Single Circuit |  | per mile | 500 | 1000 | section above. Will include similar factors
as new transmission line
Reconductor/Upgrade Transmission Line
|  | Double Circuit, Strung on both sides, Lattice Tower |  | site specific |  |  | Costs vary widely depending on
|  | Double Circuit, Strung on one side, Lattice Tower |  | site specific |  |  | number of structures that require
|  | Single Circuit, Lattice Tower |  | site specific |  |  | upgrade. As a result, will be estimated
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | site specific |  |  | as a lump sum.
|  | Double Circuit, Strung on one side, Tubular Steel Pole |  | site specific
|  | Single Circuit, Tubular Steel Pole |  | site specific
Metering
|  | Upgrade of existing RTUs |  | site specific |  |  | Cost varies widely, will be estimated as a
lump sum
Lump Sum costs, in addition to per-unit or lump-sum costs listed above: | [6 empty] | Lump-sum costs are not published on CAISO website, but are included in Phase I cost estimates
| Engineering costs |  |  | site specific |  |  | Engineering and Project Management costs
| Project Management costs (EPC, home office, owners agent) |  |  | site specific |  |  | are included in the per-unit cost of equipment.
However, if any site specific incremental
costs exceed the per-unit amount, they
will be estimated as a lump sum.
| Capitalized Licensing and Permitting Costs, including |  |  | site specific |  |  | As best estimated at time of Phase I
| mitigation measures, FAA permits, etc. | [5 empty] | study
| Civil work: Site Preparation including site grading, ground grid, | [5 empty] | Civil, general facilities, MEER buildings,
| and walls/fencing/containment |  |  | site specific |  |  | and any other facilities that are unique to
a given project are lump sums
| General Facilities: station light & power, backup generator, |  |  | site specific
station utilities (water, gas, etc. if manned substation)
| Substation Control (MEER) Buildings |  |  | site specific |  |  | Includes cost of batteries, DC power supply, cable trays
| Incremental cost for transmission line crossings (roads, |  |  | site specific |  |  | Number of crossings are highly variable and site
| streams, rail, highway, other T\L) | [5 empty] | specific. As a result, will be estimated
as a lump sum
| Land cost for substations and T/L ROW |  |  | site specific |  |  | Land costs are highly variable and site specific.
As a result, will be estimated as a lump sum
| Incremental cost of soil/geotechnical mitigation measures |  |  | lump sum |  |  | Unable to perform detailed geotechnical
analysis of land in Phase I study, but
any known geotech mitigation measures
will be estimated as a lump sum
| Corporate Overheads (A&G, P&B, and AFUDC) | [5 empty] | Per-unit costs shown do not include
| Income Tax Component of Contribution (ITCC) | [5 empty] | A&G, P&B, AFUDC, or ITCC. If required
such items will be added to the total
cost estimate as a lump sum
Escalation:
| Annual Escalation Rates |  |  | rate |  |  | Unit costs are shown in 2008 constant
dollars. Each Phase I cost estimate will include escalation rates for future periods, based on good engineering judgment and indices used in industry practice, such as Handy Whitman indices.
Additional assumptions are listed on the accompanying "factors" tab
Acronyms List:
AA substation: denotes high-voltage side of transformation is 500 kV
A substation: denotes high-voltage side of transformation is 230 kV
ACSR: Aluminum Conductor Steel Reinforced, commonly used conductor
AFUDC: Allowance for Funds Used During Construction
A&G: Administrative and General expenses
BAAH: Breaker-and-a-half configuration
BITS: Building Integrated Timing Supply, timekeeping for network
CB: Circuit breaker
DACS: Digital Access Cross Connect
DC: Direct current
EPC: Engineer, Procure & Construct
FAA: Federal Aviation Administration
FCC: Federal Communications Commission
IT: Information Technology and telecommunications equipment
ITCC: Income Tax Component of Contribution
kV: Kilovolts
MEER: Mechanical Electrical Equipment Room where substation control equipment resides
MVA: Million (Mega) Volt Amperes
ROW: Right-of-way
RTU: Remote Terminal Unit
SCADA: Supervisory Control and Data Acquisition system
SPS: Special Protection System
SVC: Static VAR Compensator
T\L: Transmission line
TRV: Transient Recovery Voltage
VAR: Volt Ampere Reactive

## factors
SCE Unit Cost Guide
Factors for use in developing cost estimates in Phase I GIPR studies
As of April 1, 2009
Simplified example on how to apply factors:
$ millions
Hypothetical baseline cost per mile for Double Circuit 220 kV line (strung one side) using Lattice Towers: | [8 empty] | 2
Known characteristics of proposed transmission line ROW at time of Phase I study:
| Will be constructed in mountainous terrain | [7 empty] | 2.0X
| No known population density issues | [7 empty] | 1.0X
| Known high wind-prone area (but not icy) | [7 empty] | 1.35X
|  |  | Estimated cost per mile | [5 empty] | 5.4
|  | Factor Type: |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain | flat |  |  | hilly |  | mountain |  | forest
|  |  | Population density | rural |  | desert | suburban |  | urban/metro
|  |  | Weather study (increase in | 1/2" ice, or 20# wind |  |  | 1" ice, 6# wind |  | > 2" ice, 6# wind
structural steel amount and foundation volume)
|  | Factor Amounts: |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  | 2.0X to 3.0X
|  |  | Population density |  | 1.00X to 1.10X |  |  | 1.33X |  | 1.67X
|  |  | Weather study |  | 1.00X to 1.35X |  |  | 1.45X |  | 1.60X
Other assumptions underlying unit cost guide:
Unit costs denominated in 2008 constant dollars, when used in cost estimates, the unit costs will be subject to escalation
General labor overtime rate: 50%
General contingency factor: 35%
Unit costs include costs to procure materials, installation, engineering, project management costs, home office costs, and contingency
Unit costs exclude allocated corporate overhead, including P&B, A&B, and AFUDC (will be added to total cost estimates)
Unit costs exclude generator's responsibility for Income Tax Component of Contribution (ITCC), (some items in the unit cost guide include components
that are network facilities, and components that are interconnection facilities. ITCC applies to those components that are considered
interconnection facilities, and would be additive to the amount shown in the per-unit cost).
For example, in the first item under substation equipment, the 220 kV loop-in substation, of the $21,800,000 unit cost, $750,000 is considered
interconnection facilities to which ITCC would be applied and added to the total cost, while the remaining $21,050,000 is
considered network facilities with no ITCC applied.
Unit cost guide assumes facilities are constructed by SCE or SCE-controlled contractors, and facilities are owned by SCE
Cost of removal of facilities excludes any credit for salvage value. If applicable, SCE will estimate a salvage value credit for removed facilities, but
the credit will be included as a lump sum, where and when appropriate.
Transmission line cost per mile assumes conventional construction
Cost per mile of T\L requiring helicopter construction (or deconstruction) will have higher than published per-unit cost,
as cost of helicopter construction is imbedded in labor component
Cost of teardown of existing lines includes temporary bypass line (also referred to as a "shoe-fly") costs
Towers assumption for single-circuit 220 kV construction:
4.25 towers/mile, 68,785 lbs. of steel/mile for lattice towers strung with 2B-1590kcmil ACSR conductor
3.8 towers/mile, 56,905 lbs. of steel/mile - for suspension structures
0.45 towers/mile, 10,880 lbs. of steel/mile - for dead-end structures