## menu
Costs are in 2009 Dollars (x1000)
|  |  |  | "Voltages" | 69 kV | 138 kV | 230 kV | 500 kV | Notes/Comments:
Equipment Categories |  |  |  | Units
New Substation Equipment
|  | Transformer Banks: | [6 empty] | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage a steel deadend structure and protection
|  |  | 500/230 kV 4-1 Phase | per unit |  |  |  | 47267.415
|  |  | 500/230 kV 3-1 Phase | per unit |  |  |  | 37018.215
|  |  | 500/138 kV 1-3 Phase | per unit
|  |  | 230/138 kV | per unit |  |  | 10075.455
|  |  | 230/69 kV | per unit |  |  | 7901.01
|  |  | 138/69kV | per unit |  | 6812.91
|  | Line Positions to terminate gen-ties and Transformer Bank positions | [6 empty] | Position cost estimate includes cost of any related disconnect switches and protection equipment located in the position
|  |  | Single Breaker | per unit | 522.99 | 679.185 | 2069.145 | 3832.92
|  |  | Breaker and a half (2CB) | per unit |  |  | 4140.045 | 7909.785
|  |  | Double Breaker (3CB) | per unit | 865.215 | 1451.385 | 4471.74 | 9570.015
|  | Double Bus sections - 2 buses spanning 2 positions |  | per unit | 905.58 | 1226.745 | 786.24 | 2113.02 | typical configuration for 500 kV
|  | Double Bus sections - 2 buses spanning 4 positions |  | per unit | 1690.065 | 2541.24 | 2102.49 | 3957.525 | typical configuration for 230 kV
|  | Series Capacitors |  | site specific |  |  |  |  | not typical, would be estimated as
lump sum, if required
|  | Shunt Capacitors |  | per unit | 796.77 | 879.255 | 3259.035 |  | includes cost of CB and disconnect
| Miscellaneous Equipment (see comments) | [7 empty] | Costs provided here are for typical SDG&E substation items.
Bus Tie (1CB)
Shunt Reactors
Phase Shifter
Ground Bank
|  | Bank Protection |  | per unit | 510.705 | 510.705 | 510.705 | 510.705
|  | Tie Line Protection |  | per unit | 470.34 | 470.34 | 470.34 | 470.34
|  | Bus Protection |  | per unit | 528.255 | 528.255 | 528.255 | 528.255
| Gas Insulated Substation (in lieu of open air construction, which is typical) |  |  | site specific |  |  |  |  | Not typical, would be estimated as site specific, if required
Replacement Substation Equipment
|  | Circuit Breakers (including replacement of foundation) |  | per unit | 200.07 | 280.8 | 584.415 | 1779.57
|  | Circuit Breakers (without TRV caps) |  | per unit
|  | Transient recovery voltage capacitors (set of 3, separate from CBs) |  | per unit
|  | Disconnect switches (incl. steel structures and foundations) |  | per unit | 121.095 | 168.48 | 173.745 | 568.62
New Protection Equipment
|  | New SPS |  | site specific |  |  |  |  | New protection equipment is greatly dependent upon geographic location with respect to existing facilities. Costs will be provided in Phase 1.
|  | SPS Relays |  | site specific
|  | Additional set of bushing current transformers (3) at existing CBs |  | site specific
IT interface equipment - substation
|  |  | Fiber | per sub |  |  |  |  | To be provided in Phase 1.
|  |  | Microwave | per sub
|  |  | Phone Line | per sub
|  | IT interface equipment - T/L | [6 empty] | To be provided in Phase 1.
|  |  | Fiber | per mile
|  |  | Microwave | per mile
|  |  | Phone Line | per mile
New Transmission Line
|  | Single Circuit, Lattice Tower |  | per mile |  |  |  | 6051.5499 | 230kV assumes: Single Circuit is 2 cond./phase (Split phase or bundled), Dbl. Circuit is 2 cond./phase each circuit. 138kV = 230kV less OHGW. Anchor bolted steel pole construction approx. = for all voltages.
|  | Single Circuit, Anchor-bolted Steel Pole |  | per mile |  | 4839.8869 | 4932.5999
|  | Double Circuit, Anchor-bolted Steel Pole |  | per mile |  | 5944.4504 | 6051.5499
|  | Single Circuit Wood Equivalent Steel Pole |  | per mile | 1890.6544 | 2020.1329
|  | Double Circuit Wood Equivalent Steel Pole |  | per mile | 2683.5104
Rebuild Transmission Line (complete tear down and replace)
|  | Single Circuit, Anchor-bolted Steel Pole |  | per mile |  |  | 5971.6249 |  | Rebuild costs = New construction plus the removals.
|  | Double Circuit, Anchor-bolted Steel Pole |  | per mile |  |  | 7090.5749
|  | Single Circuit Wood Equivalent Steel Pole |  | per mile | 2157.6039 | 2226.3394
|  | Double Circuit Wood Equivalent Steel Pole |  | per mile | 3014.3999
Reconductor/Upgrade Transmission Line
|  | Single Circuit, Anchor-bolted Steel Pole |  | site specific |  |  |  |  | Cost varies depending on the number of structures to be replaced and requirements for temporary line construction. Estimates will be provided on a site specific basis.
|  | Double Circuit, Anchor-bolted Steel Pole |  | site specific
|  | Single Circuit Wood Equivalent Steel Pole |  | site specific
|  | Double Circuit Wood Equivalent Steel Pole |  | site specific
Metering
|  | Upgrade of existing RTUs |  | site specific |  |  |  |  | Cost can vary widely, will be determined on a site specific basis.
Site specific costs in addition to per-unit costs listed above:
| Engineering costs |  |  | site specific |  |  |  |  | Engineering costs are included in per-unit costs provided above, additional engineering could be required depending on the complexity of regulatory / licensing requirements. Civil Work: both engineering and construction is not included in unit costs because of the extreme variability of sites. Substation control building costs vary greatly depending on whether a new facility is required or if an existing facility has the capability to receive additional equipment.
| Environmental / Regulatory Licensing Costs, Permitting |  |  | site specific
| Civil work: Site Preparation including Substation site grading, ground grid installation, walls/fencing/containment, geotechnical analysis and access road and structure work pad design and construction. |  |  | site specific
| Land Purchase costs |  |  | site specific
| Substation Control Buildings |  |  | site specific
Escalation:
| Annual Escalation Rate (10 yrs 2009-2017) |  |  | rate |  |  |  |  | These unit cost are in 2009 dollars. Each Phase 1 cost estimate will use escalation rates for future periods based on good engineering judgment and indices used in industry practice such as Handy-Whitman.
contemplates using Handy-Whitman Index of Public Utilities
| Cost | as baseline escalation rate
Note on G64: bnanning:
Note on G65: bnanning:
Note on G72: bnanning:

## factors
SDG&E Preliminary Draft Unit Cost Guide
Factors for use in developing cost estimates in Phase I GIPR studies
As of January 2009
Simplified example on how to apply factors:
$ millions
Hypothetical baseline cost per mile for Double Circuit 230 kV line using Anchor Bolted Steel Poles: | [5 empty] | 1
Known characteristics of proposed transmission line ROW:
| Mountainous terrain: Some Helicopter Operation |  |  |  | X | 1.3
| With high environmental mitigation: |  |  |  | X | 1.3
|  | Fully loaded cost per mile for this given project |  |  |  | 1.69
|  | Factor Type: |  | Low Impact factors: | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain | flat | hilly |  |  | rugged / mountain
|  |  | Environmental | low mitigation | med mitigation |  | high mitigation
|  |  | Location | urban/metro | suburban |  |  | rural / remote
|  | Factor Amount: |  | Low Impact factors: | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain | flat 1.0 | hilly 1.2 |  |  | rugged / mountain 1.3
|  |  | Environmental | low mitigation 1.0 | med mitigation 1.2 |  | high mitigation 1.3
|  |  | Location | urban/metro 1.0 | suburban 1.1 |  |  | rural / remote 1.3
Assumptions underlying unit cost guide:
Overtime for labor is not included in the unit cost estimates.
Outage coordination caused delays or restrictions are not included in the unit cost estimates.
General contingency factor: 35% included in the Unit Costs
Transmission line cost per mile assumes standard SDG&E construction.