## Rev 4.0
RARF GLOSSARY (applies to RARF Ver 4.0)
Tab | Resource Type Affected | Labels | Field | Definition / Details | RARF Guide Reference | Purpose
General Information
General Information | ALL |  | This submittal is for | Select: New Site, Revision, Addition of unit(s), or Deletion of unit(s) | RARF Guide: Section 4.0 | Identification
General Information |  |  | Date Form Completed | Enter date in the format: MM/DD/YYYY
General Information |  |  | Resource Entity Submitting Form | Enter the name of the Resource Entity who represents the load. This must be the same entity name that filed as a Resource Entity on the Standard Form Agreement. The Protocols require that a Load Acting as a Resource must complete and submit an Application
General Information |  |  | Resource Entity DUNS # | Enter the Market Participant unique identifier as registered with ERCOT for Resource Entity above [DUNS number or DUNS number plus 4.
General Information |  |  | Primary Contact | Enter the Primary Contact person - Site or facility contact for Generation Resources - Resource Entity contact for Load Resources who can address ERCOT questions regarding RARF submittal.
Site Information
Site Information | GEN, CC, WIND |  | Resource Site Name | Resource site or main facility name (i.e.. CEDAR BAYOU PLANT) | RARF Guide: Section 4.0 | Identification
Site Information |  |  | Resource Site Code | Code for Resource Site (i.e.. Cedar Bayou Plant it is CBY) -- Determined jointly with ERCOT
Site Information |  |  | Site In-Service Date | Site In-Service Date is the date when plant or unit was commissioned
Site Information |  |  | Site Stop Service Date | Site Stop-Service Date is the date when plant or unit will be decommissioned or blank if not known
Site Information |  |  | Congestion Management Zone for 2003: | This information can be found in the ERCOT Data Dictionary. For newer units, please contact ERCOT.
Site Information |  |  | Resource ID | Enter Resource ID , if known, as determined by ERCOT; can be obtained from the RID extract.
Site Information |  | Y/N | Resource owned by NOIE? (Y/N) | Indicate NOIE Ownership of resource
Site Information |  | Y/N | Is Resource behind a NOIE Settlement Meter Point? (Y,N) | For resources that are connected to the grid behind NOIE settlement meter points
Site Information |  |  | Number of EPS Primary meters | Enter the total number of primary EPS meters associated with this site.
Site Information |  | Y/N | Gen. Load Splitting (Y or N) | Is resource load split between multiple ESI IDs? Complete only if Units represent Split-Generation behind the EPS meter or if load is split across TDSPs.
Site Information |  |  | ESI ID | Enter the site ESI ID
Site Information |  | Y/N | ERCOT Read (Y or N) | Are the meters read (polled) by ERCOT? If N, please ensure the Resource ID is filled in above.
Site Information |  |  | TDSP Providing Service To Resource | Enter the name of the TDSP that provides transmission or distribution service to the site.
Site Information |  |  | TDSP DUNS Number | Enter the TDSP DUNS number.
Site Information |  |  | If the Gen Site Load is split among multiple ESI IDs:
Site Information |  | % | Fixed Load Splitting % | If the Gen Site Load is split among multiple ESI IDs, enter the fixed percentage (Ex: for 35% enter: 35.0 )
Site Information |  |  | Competitive Retailer | If the Gen Site Load is split among multiple ESI IDs, enter the Load Serving entity associated with that ESI ID
Site Information |  |  | Competitive Retailer DUNS # | If the Gen Site Load is split among multiple ESI IDs, enter the Load Serving Entity DUNS number associated with that ESI ID
Site Information |  |  | TDSP Providing Service | Enter the name of the TDSP that provides distribution service to the site.
Site Information |  |  | TDSP DUNS Number | Enter the TDSP DUNS number.
Unit Information
Unit Information | GEN, CC, WIND |  | Unit Name | Code for name of generator unit (e.g.. Cedar Bayou Plant Gen 1 is "CBYG1") from http://www.ercot.com/gridinfo/generation/Resource_Site_Name_to_Mnemonic_Dictionary.xls | RARF Guide: Section 5.0 | Identification
Unit Information |  |  | Resource Name (Unit Code/Mnemonic) | Concatenated mnemonic of Resource Site Code and Unit name (e.g.. CBY_CBYG1) from http://www.ercot.com/gridinfo/generation/Resource_Site_Name_to_Mnemonic_Dictionary.xls
Unit Information |  |  | PUC Registration Number (NEW!) | P.U.C. Subst. R. 25.109, Registration of Power Generation Companies (PGCs) and Self-Generators
Unit Information |  |  | ERCOT Interconnection Project Number (NEW!) | INR #, Generation Interconnection Request - only needed for new interconnections
Unit Information |  |  | NERC Number (NEW!) | Enter NERC ID#.
Unit Information |  |  | Unit Start Date | In-Service Date in MM/DD/YYYY. If full date is not known, enter the year YYYY. |  | Planning
Unit Information |  |  | Unit End Date | Retirement Date in YYYY format. Leave blank if unknown. |  | Planning
Unit Information |  |  | Physical Unit Type | CA -- Combined cycle steam part (includes steam part of integrated coal gasification combined cycle) |  | Reporting, Settlements
Unit Information |  |  |  | CC -- Combined cycle total unit (use only for plants/generators that are in planning stage, for which specific generator details cannot be provided)
Unit Information |  |  |  | CE -- Compressed air energy storage
Unit Information |  |  |  | CS -- Combined cycle single shaft (combustion turbine and steam turbine share a single generator)
Unit Information |  |  |  | CT -- Combined cycle combustion turbine part (includes comb. turbine part of integrated coal gasification combined cycle)
Unit Information |  |  |  | FC -- Fuel Cell
Unit Information |  |  |  | GT -- Combustion (gas) turbine (includes jet engine design)
Unit Information |  |  |  | HY -- Hydraulic turbine (includes turbines associated with delivery of water by pipeline
Unit Information |  |  |  | IC -- Internal combustion (diesel, piston) engine
Unit Information |  |  |  | NA -- Unknown at this time (planned units only)
Unit Information |  |  |  | OT -- Other
Unit Information |  |  |  | PS -- Hydraulic Turbine - Reversible (pumped storage)
Unit Information |  |  |  | PV -- Photovoltaic
Unit Information |  |  |  | ST -- Steam Turbine including nuclear, geothermal and solar. Does not include combined cycle.
Unit Information |  |  |  | WT -- Wind Turbine
Unit Information | GEN, CC |  | Primary Fuel Type | AB -- Agriculture Byproducts (bagasse, straw, energy crops) |  | Reporting, Settlements, Operations
Unit Information |  |  |  | BFG -- Blast-Furnace Gas
Unit Information |  |  |  | BIT -- Bituminous Coal
Unit Information |  |  |  | BL -- Black liquor
Unit Information |  |  |  | DFO -- Distillate Fuel Oil (diesel, No1 fuel oil, No 2 fuel oil, No 4 fuel oil)
Unit Information |  |  |  | GEO -- Geothermal
Unit Information |  |  |  | JF -- Jet Fuel
Unit Information |  |  |  | KER -- Kerosene
Unit Information |  |  |  | LFG -- Landfill Gas
Unit Information |  |  |  | LIG -- Lignite
Unit Information |  |  |  | MSW -- Municipal Solid Waste (refuse)
Unit Information |  |  |  | NA -- Not Applicable
Unit Information |  |  |  | NG -- Natural Gas
Unit Information |  |  |  | NUC -- Nuclear (uranium, plutonium, thorium)
Unit Information |  |  |  | OBG -- Other - Biomass Gas (methane, digester gas)
Unit Information |  |  |  | OBL -- Other - Biomass Liquids (ethanol, fish oil, waste alcohol, other gases)
Unit Information |  |  |  | OBS -- Other - Biomass Solids (animal manure/waster, medical waste, paper pellets, paper derived fuel)
Unit Information |  |  |  | OG -- Other - Gas (butane, coal processes, coke-oven coal, methanol, refinery gas)
Unit Information |  |  |  | OO -- Other - Oil (butane, crude, liquid byproducts, oil waste, propane)
Unit Information |  |  |  | OTH -- Other (batteries, chemicals, hydrogen pitch sulfur, misc technologies)
Unit Information |  |  |  | PC -- Petroleum Coke
Unit Information |  |  |  | PG -- Propane
Unit Information |  |  |  | RFO -- Residual Fuel Oil (No 5 and No 6 fuel oil)
Unit Information |  |  |  | STM -- Steam from other units
Unit Information |  |  |  | SLW -- Sludge Waste
Unit Information |  |  |  | SUB -- Sub-bituminous Coal
Unit Information |  |  |  | SUN -- Solar (photovoltaic, thermal)
Unit Information |  |  |  | TDF -- Tires
Unit Information |  |  |  | T -- Tidal
Unit Information |  |  |  | WAT -- Water (conventional, pumped storage)
Unit Information |  |  |  | WDL -- Wood/Wood Waste - Liquids (red liquor, sludge wood spent sulfite liquor, other liquors)
Unit Information |  |  |  | WDS -- Wood/Wood Waste - Solids (peat, railroad ties, utility poles, wood chips, other solids)
Unit Information |  |  |  | WH -- Waste heat (residual steam)
Unit Information |  |  |  | WND -- Wind
Unit Information |  |  |  | WOC -- Waste / Other Coal
Unit Information |  |  | Secondary Fuel Type | Same data entry elements as primary fuel type, but for secondary or start-up fuel. |  | Reporting, Settlements, Operations
Unit Information |  |  | Fuel Transportation Type | CV -- Conveyor |  | Reporting, Operations
Unit Information |  |  |  | PL -- Pipeline
Unit Information |  |  |  | RR -- Railroad
Unit Information |  |  |  | TK -- Truck
Unit Information |  |  |  | NA -- Not Applicable
Unit Information | GEN, CC, WIND | Y/N | Renewable | Is the unit a certified renewable energy credit generator? See Protocol Section 14.9. |  | Reporting
Unit Information |  | Y/N | Renewable/Offset | REC offset generators that produce generation to cover offsets they have been approved to provide
Unit Information |  |  | Resource Category | Nuclear |  | Settlements
Unit Information |  |  |  | Hydro
Unit Information |  |  |  | Coal and Lignite
Unit Information |  |  |  | Combined Cycle ≤ 90 MW*
Unit Information |  |  |  | Combined Cycle > 90 MW*
Unit Information |  |  |  | Gas Steam - Supercritical Boiler
Unit Information |  |  |  | Gas Steam - Reheat Boiler
Unit Information |  |  |  | Gas Steam - Non-reheat or Boiler without air-preheater
Unit Information |  |  |  | Simple Cycle ≤ 90 MW
Unit Information |  |  |  | Simple Cycle > 90 MW
Unit Information |  |  |  | Diesel
Unit Information |  |  |  | Renewable
Unit Information |  | Y/N | Qualifying facility | A qualifying co-generation facility or qualifying small power production facility under regulatory qualification criteria as defined in PURPA, 16 USC §796(18)(B) and §796(17)(C). |  | PURPA
Unit Information |  | MVA | Name Plate Rating | Name Plate MVA Rating of this unit at its rated Power Factor. |  | Planning, Operations
Unit Information |  | MW | Real Power Rating | Maximum rated MW at rated Power Factor.
Unit Information |  | MVAR | Reactive Power Rating | Maximum MVAR at rated Power Factor
Unit Information | GEN, CC | MW | Turbine Rating | Maximum gross designed MW of the turbine
Unit Information | GEN, CC, WIND | KV | Unit Generating Voltage | Terminal voltage of generating unit
Unit Information | CC |  | Unit Information -- Additional Combined Cycle Data -- CC Train Details
Unit Information |  |  | Name of Combined Cycle Train | Train name assigned by ERCOT |  | Identification
Unit Information |  |  | Mnemonic for Combined Cycle Train | Determined jointly with ERCOT for new units. Typically the GenSite= 8 char, Train id = 4 char, Configuration id = 3 char, (ex."GENSITE_CC1_1") |  | Identification
Unit Information |  | Y/N | Is train augmented with Duct Burner(s)? | Indicate whether Duct Burner(s) augmentation is in service |  | Planning, Operations
Unit Information |  | Y/N | Is train augmented with Evap Cooler(s)? | Indicate whether Evap Cooler(s) augmentation is in service |  | Planning, Operations
Unit Information |  | Y/N | Is train augmented with Chiller(s)? | Indicate whether Chiller(s) augmentation is in service |  | Planning, Operations
Unit Information |  | Y/N | Other augmentation? | Indicate whether other augmentation is in service |  | Planning, Operations
Unit Information | WIND |  | Unit Information -- Additional Wind Resource Data
Unit Information |  | Y/N | Eligible for McCamey Flowgate Rights (MCFRIs)? | New Nodal Field- see Section 7.7 for Cong. Mgmt. in McCamey Area for details |  | Planning, Operations
Unit Information |  | decimal degrees | Latitude of center of Wind Farm | New Nodal field- used for Wind Generation Forecasting
Unit Information |  | decimal degrees | Longitude of center of Wind Farm | New Nodal field- used for Wind Generation Forecasting
Unit Information |  | meters | Average Height above ground of Turbine Hub | New Nodal field- used for Wind Generation Forecasting
Unit Information |  | decimal degrees | Latitude of Meteorological Tower | New Nodal field- used for Wind Generation Forecasting
Unit Information |  | decimal degrees | Longitude of Meteorological Tower | New Nodal field- used for Wind Generation Forecasting
Unit Information |  | meters | Height of Meteorological Instrumentation | New Nodal field- used for Wind Generation Forecasting
Unit Information |  |  | Unit Information -- Wind Turbine Details - Turbine Information by Model Group
Unit Information |  |  | Group # - Type of Turbine (Manufacturer/Model) | From name-plate or manufacturer data sheet |  | Planning, Operations
Unit Information |  | MW | Group # - MW Rating for this model of Turbine | From name-plate or manufacturer data sheet
Unit Information |  |  | Group # - Number of this type of Turbine | Count of wind turbines in this group
Parameters
Parameters | GEN, CC, CFG, WIND | MW | High Reasonability Limit | New Nodal field per protocol 3.7.1- An "Out-of-Bounds" value chosen by RE and used by ERCOT to alarm/reject data exceeding the value. | RARF Guide Sections 6.1, 6.2, 6.3 | Protocol 3.7.1
Parameters |  | MW | Low Reasonability Limit | New Nodal field per protocol 3.7.1- An "Out-of-Bounds" value chosen by RE and used by ERCOT to alarm/reject data exceeding the value. |  | Protocol 3.7.1
Parameters |  | MW/min | High Reasonability Ramp Rate Limit | New Nodal field- An "Out-of-Bounds" value chosen by RE and used by ERCOT to alarm/reject data exceeding the value. |  | Protocol 3.7.1
Parameters |  | MW/min | Low Reasonability Ramp Rate Limit | New Nodal field- An "Out-of-Bounds" value chosen by RE and used by ERCOT to alarm/reject data exceeding the value. |  | Protocol 3.7.1
Parameters |  | MW | Seasonal Net Max Sustainable Rating | Seasonal - Spring, Summer, Fall, Winter; Used for Planning as well as Mitigated Offer Cap in calculating the capacity factor of the resource. Winter months are December, January, and February; Spring months are March, April, and May; Summer months are June, July, and August; Fall months are September, October, and November. These are not the HSL/LSL or HEL/LEL values. |  | Protocol 4.4.9.4.1; Protocol 3. 7.1
Parameters |  | MW | Seasonal Net Min Sustainable Rating
Parameters |  | MW | Seasonal Net Max Emergency Rating
Parameters |  | MW | Seasonal Net Min Emergency Rating
Operational Parameters
Operational Parameters | GEN, WIND, CFG | hours | Minimum On Line Time | The minimum number of consecutive hours the Resource must be On-Line before being shut down. Field was previously called Minimum Up Time on zonal GARF | RARF Guide Section 7.1 Nodal Protocols 3.7.1 | Operations, Settlements
Operational Parameters |  | hours | Minimum Off Line Time | The minimum number of consecutive hours the Resource must be Off-Line before being restarted. Field was previously called Minimum Down Time on Zonal GARF.
Operational Parameters |  | hours | Hot Start Time | The time, in hours, from the ERCOT notice to the Resource breaker-closing, for a Resource in its hot-temperature state. New nodal value from Protocols 3.7.1- Resource Parameter Criteria Hot, Cold, Intermediate start times are not additive.
Operational Parameters |  | hours | Intermediate Start Time | The time interval, in hours, from the ERCOT notice to the Resource breaker-closing, for a Resource in its intermediate temperature state. New nodal value from Protocols 3.7.1- Resource Parameter Criteria Hot, Cold, Intermediate start times are not additive.
Operational Parameters |  | hours | Cold Start Time | The time interval, in hours, from the ERCOT notice to the Resource breaker-closing, for a Resource in its cold-temperature state. New nodal value from Protocols 3.7.1- Resource Parameter Criteria Hot, Cold, Intermediate start times are not additive.
Operational Parameters |  |  | Max Weekly Starts | The maximum number of times a Resource can be started in seven consecutive days under normal operating conditions. New nodal value from Protocols 3.7.1- Resource Parameter Criteria
Operational Parameters |  | hours | Max On Line Time | The maximum number of consecutive hours a Resource can run before it needs to be shut down. New nodal value from Protocols 3.7.1- Resource Parameter Criteria
Operational Parameters |  |  | Max Daily Starts | The maximum number of times a Resource can be started in a 24 hour period under normal operating conditions. New nodal value from Protocols 3.7.1- Resource Parameter Criteria
Operational Parameters |  | MWh | Max Weekly Energy | The maximum amount of energy, in MWh, a Resource can produce in seven consecutive days. New nodal value from Protocols 3.7.1- Resource Parameter Criteria
Operational Parameters |  | hours | Hot-to-Intermediate Time | The time, in hours, after shutdown that a hot-temperature-state Resource takes to cool down to intermediate-temperature state. New nodal value from Protocols 3.7.1- Resource Parameter Criteria
Operational Parameters |  | hours | Intermediate-to-Cold Time | The time, in hours, after shutdown that an intermediate-temperature-state Resource takes to cool down to cold-temperature state. New nodal value from Protocols 3.7.1- Resource Parameter Criteria
Operational Parameters |  |  | Normal Ramp Rate Curve. Enter up to ten points. Upward MW1-10 (MW1/Low to MW10/High end of curve) | Normal Ramp Rate curve in protocols is for curve to span from Low Sustainable Limit to High Sustainable Limit. Since HSL/LSL are subject to daily changes, extending the curve to High/Low Reasonability Limits for registration purposes is recommended. The curve is reflected in ERCOT systems as steps. The curve is not interpolated between points.
Operational Parameters |  | MW | MW1 (MW1/Low MW point to MW10/High MW end of curve) | Ramp Rate curve is a pairing (MW Output vs. Ramp Rate). Enter MW value here
Operational Parameters |  | MW/min | Normal Upward RampRate1 | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level .
Operational Parameters |  | MW/min | Normal Downward RampRate1 | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level .
Operational Parameters |  |  | Emergency Ramp Rate Curve. Enter up to ten points. Upward MW1-10 (MW1/Low to MW10/High end of curve) | Emergency Ramp Rate curve in protocols is for curve to span from Low Emergency Limit to High Emergency Limit. Since HEL/LEL are subject to daily changes, extending the curve to High/Low Reasonability Limits for registration purposes is recommended. The curve is reflected in ERCOT systems as steps. The curve is not interpolated between points.
Operational Parameters |  | MW | MW1 (MW1/Low MW point to MW10/High MW end of curve) | Ramp Rate curve is a pairing (MW Output vs. Ramp Rate). Enter MW value here
Operational Parameters |  | MW/min | Upward RampRate1 | Enter Rate at which resource can increase MW output in MW/minute for the given output level .
Operational Parameters |  | MW/min | Downward RampRate1 | Enter Rate at which resource can decrease MW output in MW/minute for the given output level .
Reactive Capability
Reactive Capability | GEN, CC, WIND | MW | MW1 | Reactive Capability curve - point on curve of MW output for this unit, MW1 | RARF Guide: Section 8.1 | Planning, Operations
Reactive Capability |  | MVAR | Lagging MVAR limit associated with MW1 output | Unit's Lagging reactive power output capability associated with its MW1 output, in MVAR.
Reactive Capability |  | MVAR | Leading MVAR limit associated with MW1 output | Unit's Leading reactive power output capability associated with its MW1 output, in MVAR; input as negative number
Reactive Capability |  | MW | MW2 | Reactive Capability curve - point on curve of MW output for this unit, MW2
Reactive Capability |  | MVAR | Lagging MVAR limit associated with MW2 output | Unit's Lagging reactive power output capability associated with its MW2 output, in MVAR.
Reactive Capability |  | MVAR | Leading MVAR limit associated with MW2 output | Unit's Leading reactive power output capability associated with its MW2 output, in MVAR; input as negative number
Reactive Capability |  | MW | MW3 | Reactive Capability curve - point on curve of MW output for this unit, MW3
Reactive Capability |  | MVAR | Lagging MVAR limit associated with MW3 output | Unit's Lagging reactive power output capability associated with its MW3 output, in MVAR.
Reactive Capability |  | MVAR | Leading MVAR limit associated with MW3 output | Unit's Leading reactive power output capability associated with its MW3 output, in MVAR; input as negative number
Reactive Capability |  | MW | MW4 | Reactive Capability curve - point on curve of MW output for this unit, MW4
Reactive Capability |  | MVAR | Lagging MVAR limit associated with MW4 output | Unit's Lagging reactive power output capability associated with its MW4 output, in MVAR.
Reactive Capability |  | MVAR | Leading MVAR limit associated with MW4 output | Unit's Leading reactive power output capability associated with its MW4 output, in MVAR; input as negative number
Reactive Capability |  | MW | MW5 - Unity Power Factor | From the Reactive Capability curve - the MW output at Unity Power Factor (zero MVAR)
Reactive Capability | GEN, CC | PSI | If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies | From manufacturer Reactive Capability Curve or data sheet.
Reactive Capability | GEN, CC, WIND | MVAR | Net Maximum Leading Operating Capability (MVAR) | Enter the maximum lagging MVARs that can be produced. Obtained from manufacturer Reactive Capability Curve or data sheet; input as negative number
Reactive Capability |  | MVAR | Net Maximum Lagging Operating Capability (MVAR) | From manufacturer Reactive Capability Curve or data sheet.
Reactive Capability |  | Y/N | Manufacturer's Capability Curve submitted? | Has a recent curve been submitted to ERCOT? If not, please submit.
Reactive Capability | WIND | Y/N | Reactive Standard? | Does the Wind unit meet the reactive standard?
GSU Transformer
GSU Transformer | ALL GEN RES |  | Step-Up Transformer Name from the ERCOT Operations & Planning Database (all data in 100MVA base) | Name of Transformer. Should match existing model. Please find the transformer name from the ERCOT Branch Data file. | RARF Guide Section 9.1 | Network Modeling
GSU Transformer |  |  | Unit(s) associated with this transformer | Identify which unit(s) use this transformer.
GSU Transformer |  |  | Provide kV Base | Base KV for impedances
GSU Transformer |  | KV | High Voltage Limit (no-load) | Voltage of the high side (transmission or secondary side) of this step up transformer under no-load conditions.
GSU Transformer |  | KV | Low Voltage Limit (no-load) | Voltage of the low side (generator or primary side) of this step up transformer under no-load conditions
GSU Transformer |  |  | High Voltage Connection - Wye or Delta | Is high voltage side Wye or Delta connected?
GSU Transformer |  |  | Low Voltage Connection - Wye or Delta | Is low voltage side Wye or Delta connected?
GSU Transformer |  | p.u. | Series Resistance | Per ANSI/IEEE Std: Impedance is the ratio of the phasor equivalent of a steady-state sine-wave voltage or voltage-like quantity (driving force) to the phasor equivalent of a steady-state sine-wave current or current-like quantity (response). The real part of the impedance is the resistance. The imaginary part is the reactance. All are measured in Ohms.
GSU Transformer |  | p.u. | Series Reactance
GSU Transformer |  | p.u. | Shunt Magnetizing Conductance | Per ANSI/IEEE Std: Admittance is the reciprocal of impedance. Admittance is ratio of the phasor equivalent of a steady-state sine-wave current or current-like quantity (response) to the phasor equivalent of the corresponding voltage or voltage-like quantity (driving force). The real part is the conductance and the imaginary part is the susceptence. All are measured in mhos (reciprocal ohms).
GSU Transformer |  | p.u. | Shunt Magnetizing Susceptance
GSU Transformer |  | MVA | Normal Rating MVA | Per ERCOT Operating Guides, Section 3: Normal Rating or Continuous Rating: Represents the continuous MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature. The Transmission Facility can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.
GSU Transformer |  | MVA | Emergency Rating MVA | Per ERCOT Operating Guides, Section 3: Emergency Rating: Represents the two (2) hour MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature. The Transmission Facility can operate at this rating for two (2) hours without violation of NESC clearances or equipment failure.
GSU Transformer |  | MVA | Loadshed Rating MVA | Per Operating Guides, Section 3:Loadshed Rating or Fifteen Minute Rating: Represents the fifteen (15) minute MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature and with a step increase from a prior loading of ninety percent (90%) of the Continuous Rating. The Transmission Facility can operate at this rating for fifteen (15) minutes, assuming its pre-contingency loading was ninety percent (90%) of the Continuous Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure. This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.
GSU Transformer |  | Y/N | Load Tap Changer (Y/N) | Is this a LTC transformer? Per ANSI/IEEE Std: LTC (or load-tap-changing transformer) is defined as a transformer used to vary the voltage, or the phase angle, or both, of a regulated circuit in steps by means of a device that connects different taps of tapped winding(s) without interrupting the load. In the LTC section - only fill out the LTC details for the side that has the LTC (Low/Primary/Generator side or High/Secondary/Transmission side).
GSU Transformer |  |  | Location of tap changer | High (transmission) side; Low (generator) side; Both
GSU Transformer |  |  | Low or High Tap Settings
GSU Transformer |  | KV | Nominal Voltage (Kava) | Name Plate Nominal KV
GSU Transformer |  |  | Total Number of Tap Positions | How many taps does this transformer has on this side?
GSU Transformer |  |  | Normal Tap Position | The normal tap position on this side of this transformer (ex. 0-15, 1-16,etc.)
GSU Transformer |  |  | Lowest Tap Position | The lowest tap position for this transformer on this side. (ex. 0-15, 1-16,etc.)
GSU Transformer |  |  | Highest Tap Position | The highest tap position for this transformer on this side (ex. 0-15, 1-16,etc.)
GSU Transformer |  |  | Nominal Tap Position (Neutral Step) | The nominal or neutral tap position of this transformer on this side. This tap position is associated with the nominal voltage on this side of this transformer. This position corresponds to 1.0 p.u. of the transformer's tap ratio (ex. 0-15, 1-16,etc.)
GSU Transformer |  | % | Step Size in Percent | Percentage of tap range for each step (ex.6.25%/step.)
GSU Transformer |  | Y/N | Is generator connected on the tertiary winding? | If yes, see Details above for Step-up Transformer Name. Submit details on Transformer if not provided by TDSP.
Split Generation Resource
Split Generation | ALL GEN RES |  | If a single Resource Entity (RE) represents 100% of all units. This is the ONLY option available to Combined Cycle |  | RARF Guide Sections 10.1, 10.2, 10.3, 3.8 | Identification, Settlements
Split Generation |  |  | Resource Entity Name | If single entity represents outputs from all units, enter the Resource Entity Name and Duns number. If different entities represent each unit or if the units are Split Generation Resources, complete section below instead.
Split Generation |  |  | Resource Duns Number
Split Generation |  |  | If units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources.
Split Generation |  |  | Market Participant (Resource) Name | For Split-Generation Resources or if units at the same site are represented by different Resource Entities (RE)
Split Generation |  |  | Market Participant (Resource) Duns Number | Enter the Participant (Resource) DUNS Number
Split Generation |  |  | Fixed Ownership % | Total for each unit must equal 100%
Split Generation |  |  | Master Owner (Y or N) | A single Entity must be identified so the associated QSE can provide generation splitting signals. There must be a single Master PGC/QSE per Generation Site. The Master Resource Entity is responsible for submitting all Resource Specific documentation
CC Config
CC Config | CC |  | Combined Cycle Configurations | Enter the operating configurations for the train. Register all operationally unique configurations. | RARF Guide Section 11.2 | Operations, Planning & Settlement
CC Transitions
CC Transitions | CC |  | Combined Cycle Transitions | Identifies the path(s) the train can take to get from offline to all units on, as well as to go from all units down to offline. Each upward transition should add units or MW, and each downward transition should remove units or reduce MW. | RARF Guide Section 11.3 | Operations, Planning & Settlement
Planning
Planning | ALL GEN RES |  | Generator Details |  | RARF Guide Section 12.1 | Planning, Steady State studies
Planning |  | MVA | What is the MVA base that the following data is based on? | The MVA Base for stated impedances.
Planning |  | KV | What is the kV base that the following data is based on? | The KV Base for stated impedances.
Planning |  | R in p.u. | Machine Impedance Zeq (R+jX) | Steady State machine equivalent impedance in per unit on the machine base identified in this section. Enter the values in R+jX form by entering the R value in the top blank and X value in the second blank. (NEW FORMAT!)
Planning |  | X in p.u.
Planning |  | R in p.u. | Armature Z | Rotor, Stator, and Mutual Coupling impedances are required. Enter the values in R+jX form by entering the R value in the top blank and X value in the second blank. (NEW FORMAT!)
Planning |  | X in p.u.
Planning |  | R in p.u. | Rotor Z
Planning |  | X in p.u.
Planning |  | R in p.u. | Mutual coupling Armature-Rotor Z
Planning |  | X in p.u.
Planning |  | R in p.u. | Positive Sequence Z | Positive, Negative, and Zero Sequence Z are needed for the System Protection Working Group; positive impedance is usually given (nameplate). Enter the values in R+jX form by entering the R value in the top blank and X value in the second blank. (NEW FORMAT!)
Planning |  | X in p.u.
Planning |  | R in p.u. | Negative Sequence Z
Planning |  | X in p.u.
Planning |  | R in p.u. | Zero Sequence Z
Planning |  | X in p.u.
Planning |  |  | Generator Auxiliary Load
Planning |  | MW | Average Amount of Auxiliary Real Power | Enter average MW for Auxiliary Load
Planning |  | MVAR | Average Amount of Auxiliary Reactive Power | Enter average MVAR for Auxiliary Load
Planning |  |  | Generation Auxiliary Load Characteristics for MW Load
Planning |  | % | Large Motor, percent of total MW load | Enter % of total MW load per load type. Enter a percentage (ex. 70% would be entered as 70.0). These values should add up to 100%. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. .
Planning |  | % | Small Motor, percent of total MW load
Planning |  | % | Resistive (Heating) Load, percent of total MW load
Planning |  | % | Discharge Lighting, percent of total MW load
Planning |  | % | Other, percent of total MW load
Planning |  |  | Generation Auxiliary Load Characteristics for MVAR Load
Planning |  | % | Large Motor, percent of total MVAR load | Enter % of total MVAR load per load type. Enter a percentage (ex. 70% would be entered as 70.0). These values should add up to 100%. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. .
Planning |  | % | Small Motor, percent of total MVAR load
Planning |  | % | Discharge Lighting, percent of total MVAR load
Planning |  | % | Other, percent of total MVAR load
Planning |  |  | PSSE Model |  |  | Planning , Transient & Dynamic Studies
Planning |  | Y/N | Generator Form on file with ERCOT? | These referenced forms are posted at (http://www.ercot.com/gridinfo/generation/index.html), and if already on file at ERCOT, do not need to be re-completed for the transition to nodal. These are needed by ERCOT to meet NERC Compliance. ERCOT has adopted PTI's PSSE program as its standard. Indicate in the cells whether the completion of these forms have been submitted to ERCOT or not. ERCOT will work with you to complete and submit these forms.
Planning |  | Y/N | Turbine-Governor Form on file with ERCOT?
Planning |  | Y/N | Excitation Form on file with ERCOT?
Planning |  | Y/N | Do you have a Power System Stabilizer?
Planning |  | Y/N | If so, is Stabilizer Form on file with ERCOT?
Planning |  | Y/N | Do you have a Compensator?
Planning |  | Y/N | If so, is Compensator Form on file with ERCOT?
Planning |  | Y/N | Do you have a Over Excitation Limiter?
Planning |  | Y/N | If so, is Over Excitation Limiter Form on file with ERCOT?
Planning |  | Y/N | Do you have a Under Excitation Limiter?
Planning |  | Y/N | If so, is Under Excitation Limiter Form on file with ERCOT?
Planning |  |  | Reactances
Planning |  | p.u. | Direct Axis Subtransient reactance, X"di | Per Unit on Machine MVA base. The reactance which is determined from the ratio of an initial reduced voltage open circuit condition and the currents from the three-phase fault at the machine terminals at the rated frequency. The initial open circuit voltage is adjusted so the rated current is obtained. the impedance is determined from the currents during the first few cycles.
Planning |  | p.u. | Direct Axis Transient reactance, X'di | Per Unit on Machine MVA base. The reactance which is determined from the ratio of an initial reduced voltage open circuit condition and the currents from the three-phase fault at the machine terminals at the rated frequency. The initial open circuit voltage is adjusted so the rated current is obtained. the initial high decrement currents during the first few cycles are neglected.
Protection
Protection | ALL GEN RES | Sec, KV | Plant Voltage Protection | Provide instantaneous and up to 3 delay & voltage pair settings for over -and undervoltage protection | RARF Guide Section 12.1 | Planning - System Protection
Protection |  | Sec, Hz | Plant Frequency Protection | Provide instantaneous and up to 3 delay & frequency pair settings for over -and underfrequency protection
Protection |  | cycles | Breaker Interruption | After the relay is closed, how many cycles does it take to clear the fault?
Subsynchronous Resonance
Subsynchronous Resonanace | GEN, CC |  | Mass Identifier | Identification of the masses- HP, IP, LP1, LP2, EXC, etc. | RARF Guide Section 12.3 | Planning - Dynamic Studies
Subsynchronous Resonanace |  |  | Mass Inertia | H-value. The inertia constant of each mass, either in MW's, MVA, or lbm.ft²
Subsynchronous Resonanace |  |  | Inertia units | MW's, MVA, or lbm.ft²
Subsynchronous Resonanace |  |  | Associated damping | The damping associated with each mass either in p.u. torque/p.u. speed deviation, or lbf.ft.sec/rad
Subsynchronous Resonanace |  |  | Damping units | p.u. torque/p.u. speed or lbf.ft.sec/rad
Subsynchronous Resonanace |  |  | Stiffness between Masses | The stiffness (spring constant) between each two mass, either in p.u. torque/rad, or lbf.ft/rad (Coupling)
Subsynchronous Resonanace |  |  | Stiffness units | p.u. torque/rad or lbf.ft/rad
Private Network
Private Network | Site | Y/N | Private Network? | Private Use Network Definition: An electric network connected to the ERCOT Transmission Grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation). | RARF Guide Section 12.3 | Planning, Operations
Private Network | Site | MW | Average Amount of Self-Serve private load | Amount of the total site generation MW output used for self serve and not available for the grid.
Private Network |  | MVAR | Average Amount of Self-Serve private reactive load | Amount of the total site generation MVAR output used for self serve and not available for the grid.
Private Network |  | MW | Expected Typical Private Network Net Interchange | MW Net Interchange with ERCOT grid (typical Net=Gen-Load)
Private Network |  | MVAR | Expected Typical Private Network Net Reactive Interchange | MVAR Net Interchange with ERCOT grid (typical Net=Gen-Load)
Private Network |  | MW | Private Network Gross Unit Capability | MW Gross Generation Capability for the Site
Private Network |  | MVAR | Private Network Gross Unit Reactive Capability | MVAR Gross Generation Capability for the Site
Private Network | Site |  | PUN Load Characteristics for MW Load
Private Network |  | % | Large Motor, percent of total MW load | Enter % of total MW load per load type. Enter a percentage (ex. 70% would be entered as 70.0). These values should add up to 100%. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. .
Private Network |  | % | Small Motor, percent of total MW load
Private Network |  | % | Resistive (Heating) Load, percent of total MW load
Private Network |  | % | Discharge Lighting, percent of total MW load
Private Network |  | % | Other, percent of total MW load
Private Network |  |  | PUN Load Characteristics for MVAR Load
Private Network |  | % | Large Motor, percent of total MVAR load | Enter % of total MVAR load per load type. Enter a percentage (ex. 70% would be entered as 70.0). These values should add up to 100%. The split between large and small motor should be along voltage lines - where motors connected at 2400/4160V and above should be considered large, and below 2400/4160V should be considered small. .
Private Network |  | % | Small Motor, percent of total MVAR load
Private Network |  | % | Discharge Lighting, percent of total MVAR load
Private Network |  | % | Other, percent of total MVAR load
Private Network | GEN, CC, WIND | MW | Average Amount of Self-Serve private load | Amount of the total site generation MW output used for self serve and not available for the grid.
Private Network |  | MVAR | Average Amount of Self-Serve private reactive load | Amount of the total site generation MVAR output used for self serve and not available for the grid.
Private Network |  | MW | Expected Typical Private Network Net Interchange | MW Net Interchange with ERCOT grid (typical Net=Gen-Load)
Private Network |  | MVAR | Expected Typical Private Network Net Reactive Interchange | MVAR Net Interchange with ERCOT grid (typical Net=Gen-Load)
Private Network |  | MW | Private Network Gross Unit Capability | MW Gross Generation Capability for the Site
Private Network |  | MVAR | Private Network Gross Unit Reactive Capability | MVAR Gross Generation Capability for the Site
Private Network |  | Y/N | If Unit trips, does Load trip? | This is necessary to determine how much load will appear on the ERCOT grid if the unit trips.
Private Network |  | % | If yes, approximate percentage of Load that will trip? | If unit trips what percentage of load associated with this unit is tripped? Enter % (ex. 70% is entered as 70.0)
Generation Owned Transmission Assets
Generation Owned Transmission Assets | GEN, CC, WIND | Capture lines and equipment other than the generator and step-up transformer that are owned and/or operated by the generation resource and not part of the operations of the TSP. |  |  | RARF Guide Section 14.0 | Network Modeling
Generation Owned Transmission Assets |  | Y/N | Required Resource One-line Submitted to ERCOT? (Y/N) | One-line diagram is required for network modeling. (required per the Nodal Protocols in section 3.10.7)
Generation Owned Transmission Assets |  |  | LINE (any length) | Example includes the transmission line to reach the first TSP-modeled substation.
Generation Owned Transmission Assets |  |  | Status (ADD, DEL, CHANGE) | If exists in Zonal network model, than use "change".
Generation Owned Transmission Assets |  | Y/N | If this is a change, is it for a change in Impedance and/or Ratings? | Indicate if impedance or rating is changed.
Generation Owned Transmission Assets |  |  | ERCOT LINE NAME | Refer to the ERCOT Grid Information Operations and System Planning Data - select the folder “Operations Model Data” then select the zip file for ERCOT Branch Data.
Generation Owned Transmission Assets |  | KV | Line Voltage Level kV | Nominal voltage in KV
Generation Owned Transmission Assets |  |  | TDSP Name | Transmission and/or Distribution Service Provider
Generation Owned Transmission Assets |  |  | ERCOT Station Code Mnemonic (TSP owned Station) | Refer to the ERCOT Grid Information Operations and System Planning Data - select the folder “Operations Model Data” then select the zip file for ERCOT Branch Data. TSP will be familiar with naming conventions and may be able to provide assistance
Generation Owned Transmission Assets |  |  | Switching Device Name(s) (TSP owned Station)
Generation Owned Transmission Assets |  |  | Bus Number (PTI Bus Number) (TSP owned Station)
Generation Owned Transmission Assets |  |  | Station Weather Zone (TSP owned) | Weather Zone for TSP Station
Generation Owned Transmission Assets |  |  | ERCOT Station Code Mnemonic (RE owned Station) | ERCOT Station Code Mnemonic
Generation Owned Transmission Assets |  |  | Switching Device Name(s) (RE owned Station) | ERCOT Mnemonic
Generation Owned Transmission Assets |  |  | Bus Number (PTI Bus Number) (RE owned Station) | ERCOT PTI bus number
Generation Owned Transmission Assets |  |  | Station Weather Zone (RE owned Station) | Weather Zone for RE Station
Generation Owned Transmission Assets |  | p.u. | Resistance in p.u. | Line Impedance
Generation Owned Transmission Assets |  | p.u. | Reactance in p.u.
Generation Owned Transmission Assets |  | p.u. | Charging Susceptance in p.u. | Line Charging as a per unit susceptance
Generation Owned Transmission Assets |  | MVA | Continuous Rating (MVA) | Transmission line ratings in MVA. See ERCOT Operating Guide for details.
Generation Owned Transmission Assets |  | MVA | 2-hr Emergency Rating (MVA)
Generation Owned Transmission Assets |  | MVA | 15-min Rating (MVA)
Generation Owned Transmission Assets |  | Y/N | Has an ICCP Service Request been submitted? | ICCP for real-time monitoring
Generation Owned Transmission Assets |  |  | Comments | Any additional comments to describe line.
Generation Owned Transmission Assets |  |  | BREAKER or SWITCH | Example includes a breaker or switch in service between the generator and the TSP switching device
Generation Owned Transmission Assets |  |  | Status (ADD, DEL, CHANGE) | Indicate whether entry is an addition, deletion, or change.
Generation Owned Transmission Assets |  |  | Switch Name | ERCOT Mnemonic - TSP will be familiar with naming conventions and may be able to provide assistance
Generation Owned Transmission Assets |  |  | Device Status | Normally Open / Normally Closed
Generation Owned Transmission Assets |  | KV | Voltage Level KV | Nominal voltage in KV
Generation Owned Transmission Assets |  |  | PTI Bus Number | ERCOT PTI bus number
Generation Owned Transmission Assets |  | Y/N | Will this station will have or has a Voltage reading? | Telemetry available to ERCOT
Generation Owned Transmission Assets |  |  | If yes, what is the PTI Bus Number where the voltage is read. | ERCOT PTI bus number
Generation Owned Transmission Assets |  | Y/N | Has an ICCP Service Request been submitted? | ICCP for real-time monitoring
Generation Owned Transmission Assets |  |  | Comments | Any additional comments to describe Breaker or Switch.
Generation Owned Transmission Assets |  |  | CAPACITOR or REACTOR | Example includes a capacitor bank in service between the generator and the TSP switching device
Generation Owned Transmission Assets |  |  | Status (ADD, DEL, CHANGE) | Indicate whether entry is an addition, deletion, or change.
Generation Owned Transmission Assets |  |  | Capacitor or Reactor (C/R) | Indicate which device.
Generation Owned Transmission Assets |  |  | Device Name | ERCOT Mnemonic - TSP will be familiar with naming conventions and may be able to provide assistance
Generation Owned Transmission Assets |  | MVAR | Nominal MVAR | MVAR at nominal voltage
Generation Owned Transmission Assets |  | KV | Voltage Level KV | Nominal voltage in KV
Generation Owned Transmission Assets |  |  | PTI Bus Number | ERCOT PTI bus number
Generation Owned Transmission Assets |  |  | Switching device number(s) that this reactive device is directly connected to | ERCOT Mnemonic
Generation Owned Transmission Assets |  | Y/N | Has an ICCP Service Request been submitted? | ICCP for real-time monitoring
Generation Owned Transmission Assets |  |  | Comments | Any additional comments to describe Capacitor or Reactor.
Load Resource Information
Load Resource Information | LOAD |  | Name of End Use Customer | End use customer associated with Load Resource | RARF Guide Section 15.1 | Planning, Operations, Settlements
Load Resource Information |  |  | Common Name for Load Resource | Enter the common name of the load that will be acting as a resource. ( e.g.. South Gulf Refinery, etc.)
Load Resource Information |  |  | Physical Street Address for point of Delivery (POD) | Enter the physical address of the load. Use the street address if known. Use Farm Road reference points or other identification if address is not specific.
Load Resource Information |  |  | Name of City for Point of Delivery (POD) | Enter the name of the nearest Texas city or town.
Load Resource Information |  | Y/N | Is Load Netted From Generation at ERCOT Read Gensite? | Enter Y or N to indicate whether or not the load is netted from the generation at the ERCOT read Gensite.
Load Resource Information |  | Y/N | Is Load Behind a NOIE Settlement Meter Point? | Enter Y or N to indicate whether or not Load is Behind a NOIE Settlement Meter Point?
Load Resource Information |  |  | Load Resource Type (CLR/UFR/Interruptible) | Enter the load type. There are currently 3 types of Loads that can act as Resources, which are: Controllable Load, Interruptible Load, and Underfrequency Relays.
Load Resource Information |  | Y/N | If CLR, will CLR be Dynamically Scheduling?
Load Resource Information |  |  | Dispatch Asset Code (provided by ERCOT) | Enter the Dispatch Asset Code (this code will be provided by ERCOT)
Load Resource Information |  |  | Load Resource Effective Date | Enter the date the load was placed in service.
Load Resource Information |  |  | Load Resource Expiration Date | Enter the date the load was removed from service.
Load Resource Information |  |  | Substation Name for POD | Enter the name of the substation that supplies service to the Point of Delivery of the load.
Load Resource Information |  |  | Substation Code for POD | Enter the TDSP substation code.
Load Resource Information |  |  | ESIID Station Name | Enter the station name associated with the ESIID that will be utilized.
Load Resource Information |  |  | ESIID Station Code | Enter the station code associated with the ESIID that will be utilized.
Load Resource Information |  |  | Transmission Bus POD (PTI Bus No) | Enter the transmission bus location by bus number or by specifying the transmission line. (Luling to Gonzales 138KV, etc.)
Load Resource Information |  | KV | Voltage Level of Telemetered load(s) | Enter the voltage level of the load. Normally this will be between 2.4 and 138 KV.
Load Resource Information |  |  | Meter Reading Entity (TDSP) | Enter who reads the meter.
Load Resource Information |  |  | Meter Reading Entity Duns Number | Enter the Duns number for the entity above.
Load Resource Information |  |  | QSE Name | Enter the name of the Qualified Scheduling Entity who represents the load.
Load Resource Information |  |  | QSE Duns Number | Enter the Duns number for the Qualified Scheduling Entity who represents the load.
Load Resource Information |  |  | ESI-ID assigned to meter | Enter the ESI-ID assigned to the load.
Load Resource Information |  | Y/N | Wholesale Delivery Point? | Enter Y or N, if the point of delivery is a wholesale delivery point.
Load Resource Information |  | minutes | Notice Requirements to Interrupt | Enter the pre-interruption notice requirement in minutes for the load and should correlate to the type of service they are registering as--UFR = Instantaneous; CLR = 10 min; Interruptible = 30 min
Load Resource Information |  | Hz | High Set Under-frequency Relay (UFR) Setting | Enter the high set under-frequency relay setting. Loads acting as Resources that desire to bid into the Responsive Reserve Service market must have a high set under-frequency relay set at 59.7 Hz and be capable of operating in 20 cycles (1/3 second).
Load Resource Information |  |  | Load Resource Control Device | Enter the type of interrupting device. (Control Technology / Interruptible Switch / Circuit Breaker)
Load Resource Information |  | Y/N | If CLR, ability to operate as a UFR type Resource? | Can the CLR be operated as a UFR type resource?
Load Resource Information |  |  | ERCOT Load Zone | Enter the ERCOT Congestion Management Zone--West; North; Northeast; South; or Houston
Load Resource Information |  | MW | Maximum POD Total Load | Enter the maximum total load at the point of delivery.
Load Resource Information |  | MW | Summer Interruptible MW | Enter the summer interruptible load in MW.
Load Resource Information |  | MW | Winter Interruptible MW | Enter the winter interruptible load in MW.
Load Resource Information |  | MW | High Reasonability Limit | New Nodal field per protocol 3.7.1- An "Out-of-Bounds" value chosen by RE and used by ERCOT to alarm/reject data exceeding the value.
Load Resource Information |  | MW | Low Reasonability Limit | New Nodal field per protocol 3.7.1- An "Out-of-Bounds" value chosen by RE and used by ERCOT to alarm/reject data exceeding the value.
Load Resource Information |  | MW/min | CLR High Reasonability Ramp Rate Limit | New Nodal field- An "Out-of-Bounds" value chosen by RE and used by ERCOT to alarm/reject data exceeding the value. For CLR.
Load Resource Information |  | MW/min | CLR Low Reasonability Ramp Rate Limit | New Nodal field- An "Out-of-Bounds" value chosen by RE and used by ERCOT to alarm/reject data exceeding the value. For CLR.
Load Resource Information |  | Y/N | Private Use Network? | Private Use Network Definition: An electric network connected to the ERCOT Transmission Grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation).
Load Resource Parameters
Load Resource Parameters | LOAD |  | Non-CLR Resource Parameters |  | RARF Guide Section 15.1 | Registration purposes only, and are not yet integrated into ERCOT market or operational. However these are required per Protocols.
Load Resource Parameters |  | hours | Minimum Interruption Time | The minimum number of consecutive hours the Resource can be deployed (between breaker open to breaker close).
Load Resource Parameters |  | hours | Minimum Restoration Time | The minimum number of consecutive hours the Resource must remain energized (not deployed), from the time the Resource is restored from interruption and available for the next potential interruption.
Load Resource Parameters |  | hours | Max WEEKLY Deployments | The maximum number of times the Resource can be deployed in seven consecutive days under normal operating conditions;
Load Resource Parameters |  | hours | Max Interruption Time | The maximum number of consecutive hours the Resource can remain deployed before it needs to be energized.
Load Resource Parameters |  | hours | Max DAILY Deployments | The maximum number of times the Resource can be deployed in a day under normal operating conditions.
Load Resource Parameters |  | MWh | Max Weekly Energy | The maximum amount of energy, in MWh, a for which the Resource can be deployed in seven consecutive days
Load Resource Parameters |  | minutes | Minimum Notice Time | The notice time that the Resource requires before deployment (e.g., instantaneous, 30 minutes, etc.).
Load Resource Parameters |  |  | CLR Resource Parameters |  |  | Operations
Load Resource Parameters |  | hours | Max Deployment Time | The maximum amount of time a Controllable Load Resource can be deployed before it must return to normal operating conditions.
Load Resource Parameters |  | MWh | Max Weekly Energy | The maximum amount of energy a Controllable Load Resource can be deployed in seven consecutive days.
Load Resource Parameters |  |  | CLR - Normal Ramp Rate Curve (up to ten points) Upward MW1-10 (MW1/Low to MW10/High end of curve) | Normal Ramp Rate curve in protocols is for curve to span from Low Sustainable Limit to High Sustainable Limit. Since HSL/LSL are subject to daily changes, extending curve to High/Low Reasonability Limits for registration purposes is recommended. Reflected in ERCOT systems as steps. Curve is not interpolated between points. Do not enter zero or negative Ramp Rates.
Load Resource Parameters |  | MW | MW1 | Normal Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here
Load Resource Parameters |  | MW/min | Upward RampRate1 | Enter Normal Rate at which resource can increase MW output in MW/minute for the given output level .
Load Resource Parameters |  | MW/min | Downward RampRate1 | Enter Normal Rate at which resource can decrease MW output in MW/minute for the given output level .
Load Resource Parameters |  |  | CLR - Emergency Ramp Rate Curve (up to ten points) Upward MW1-10 (MW1/Low to MW10/High end of curve) | Emergency Ramp Rate curve in protocols is for curve to span from Low Emergency Limit to High Emergency Limit. Since HEL/LEL are subject to daily changes, extending curve to High/Low Reasonability Limits for registration purposes is recommended. Reflected in ERCOT systems as steps. Curve is not interpolated between points.
Load Resource Parameters |  | MW | MW1 | Emergency Ramp Rate curve is a pairing (MW Output vs. Ramp Rate), enter MW value here
Load Resource Parameters |  | MW/min | Upward RampRate1 | Enter Emergency Rate at which resource can increase MW output in MW/minute for the given output level .
Load Resource Parameters |  | MW/min | Downward RampRate1 | Enter Emergency Rate at which resource can decrease MW output in MW/minute for the given output level .
RARF Glossary v4.0

## Sheet2 (hidden)
General Information | ALL | Y/N
Site Information | ALL GEN RES | MVA
Unit Information | CC | MW
Resource Parameters | GEN | MVAR
Operational Resource Parameters | GEN, CC | KV
Reactive Capability | GEN, CC, WIND | decimal degrees
GSU Transformer | GEN, WIND | meters
Split Generation | LOAD | MW/min
CC Configurations | PUN | hours
CC Transitions | WIND | MWh
Planning | GEN, CC, CFG, WIND | PSI
Protection |  | p.u.
Subsynchronous Resonanace |  | %
Private Network |  | R in p.u.
Generation Owned Transmission Assets |  | X in p.u.
Load Resource Information |  | sec
Load Resource Parameters |  | Hz
cycles
minutes