## Cost Details
All costs are $x1,000
2022 SDG&E Generator Interconnection Unit Cost Guide |  |  |  | "Voltages" |  | 69 kV | 138 kV | 230 kV | 500 kV |  | Notes/Comments:
Revised as of: 01/12/2022
Equipment Categories |  |  |  | Units | [6 empty] | (Example PTO specific Note: Unit costs for equipment at lower voltages estimated on as-needed basis, not published on CAISO website)
New Substation Equipment
|  | Complete Loop-in Substation, equipped with one line position to |  |  |  | 4716 | 9478 | 15200 | 52410 |  | Three element switchyards.
terminate a single gen-tie
New Substation Equipment
|  | Transformer Banks: | [8 empty] | Unit cost of transformer banks
|  |  | 500/230 kV 4-1 Phase | per unit |  |  |  |  | 43641 |  | reflects cost of the highest MVA
|  |  | 500/230 kV 3-1 Phase | per unit |  |  |  |  | 37215 |  | rated transformer for the given
|  |  | 230/138 kV | per unit |  |  |  | 7271 |  |  | voltage
|  |  | 230/69 kV | per unit |  |  |  | 6988
|  |  | 138/69 kV | per unit |  |  | 6066
|  |  | (Add additional options) | per unit
|  | Line Positions to terminate gen-ties and Transformer Bank positions | [8 empty] | Position cost estimate includes cost
|  |  | Single Breaker (add third breaker to breaker and a half) | per unit |  | 695 | 844 | 1850 | 2462 |  | of any related disconnect switches
|  |  | Breaker and a half (2CB) | per unit |  | n/a | n/a | 4465 | 8195 |  | and protection equipment located within
|  |  | Breaker and a half (3CB) | per unit |  | n/a | n/a | 4517 | 10237 |  | the position
|  |  | Double Breaker (2CB, double bus) | per unit |  | 1067 | 1610 | 4517 | 10237 | 6
|  | Double Operating Bus Sections - 2 new buses, spanning 2 positions |  | per unit |  | 1171 | 1530 | 2063 | 2483 |  | Typical configuration for 500 kV, includes "pair" of N/S or E/W buses
|  | Double Operating Bus Sections - 2 new buses, spanning 4 positions |  | per unit |  | 1956 | 2896 | 4048 | 4828 |  | Typical configuration for 230 kV, includes "pair" of N/S or E/W buses
|  | Double Operating Bus Sections - 2 bus extensions, spanning 2 positions |  | per unit |  | n/a | n/a | n/a | n/a |  | Used in substation expansion
|  | Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  | per unit |  | n/a | n/a | n/a | n/a |  | Used in substation expansion
|  | Sectionalizing Breaker |  | per unit
|  | Shunt Capacitors |  | per unit |  | 925 | 1245 | 2596 | n/a |  | Includes cost of CB
| Miscellaneous Equipment (see comments) | [9 empty] | These items are rarely required for
|  | Bus Tie (1CB) |  | lump sum | [6 empty] | high-voltage substations. If required,
|  | Shunt Reactors |  | lump sum | [6 empty] | would be estimated as a lump sum.
|  | Phase Shifter |  | lump sum
|  | Ground Bank |  | lump sum
|  | Series Capacitors |  | lump sum
|  | Static VAR Compensator (SVC) |  | lump sum
|  | Tertiary Reactors (1 reactor, 1 bay) |  | lump sum
| Gas Insulated Substation (in lieu of open air construction) |  |  | lump sum | [6 empty] | Not typical, would be estimated as a
Lump sum, if GIS required
Replacement Substation Equipment
|  | Line drops (Tie Downs)- 3 phases |  | per unit | [6 empty] | Shaded areas are n/a to SDG&E construction
|  | Circuit Breakers (including replacement of foundation) |  | per unit |  | 282 | 386 | 629 | 1890
|  | Circuit Breakers (without TRV caps) |  | per unit
|  | Transient recovery voltage capacitors (set of 3, separate from CBs) |  | per unit
|  | Disconnect switches (incl. steel structures and foundations) |  | per unit |  | 194 | 258 | 358 | 733
|  | Line protection relays (other end of line) |  | per set |  | 742 | 742 | 742 | 742
|  | Bank Protection |  | per unit |  | 749 | 749 | 749 | 749
|  | Bus Protection |  | per unit |  | 662 | 662 | 662 | 662
New Protection Equipment
|  | New SPS |  | lump sum
|  | SPS Relays |  | lump sum
|  | Additional set of bushing current transformers (3) at existing CBs |  | lump sum
Information Technology (IT) Equipment
IT interface equipment - Control Rooms
|  |  | Communication rack placed in existing B station MEER bldg | per set
|  |  | Comm. Rack with own environmental enclosure | per set
|  |  | Full Comm. package for AA or A stations | per set
|  |  | Prefab communications building | per unit
|  |  | 48V DC power supply for comm. equipment | per set
|  |  | 100' self-supporting comm. tower (3 legs) | per unit
|  |  | 120' self-supporting comm. tower (4 legs) | per unit
IT interface equipment - miscellaneous equipment
|  |  | Lightwave terminal | per unit
|  |  | Microwave terminal and dish antennas | per set
|  |  | Dehydrator for microwave antennas | per unit
|  |  | Channel bank | per unit
|  |  | Digital Access Cross Connect (DACS) | per unit
|  |  | Network synchronization equipment (BITS clock) | per unit
|  |  | Large router for network access to work bases | per unit
|  |  | Small router for equipment monitoring, "data beyond SCADA" | per unit
|  |  | T1 cross connect | per unit
|  |  | Fiber to Telco connection (high voltage protected) | per unit
IT interface equipment - T/L
|  |  | Fiber optic cable on existing poles | per mile
|  |  | Fiber optic cable on new poles | per mile
New Transmission Line
Complexity
|  | Single Circuit Steel Poles |  | per mile | Low | 4320 | 4320 | 4320 | N/A |  | Includes installation of new structures and new conductor, and complete removal of old line. --69kV - Assumes installation of 12 poles/mile (2 DE, 10 Tangent Poles). -138kV - Assumes installation of 9 poles/mile (2 DE, x 7 Tangent Poles) -230kV - Assumes installation of 6 poles/mile (1 DE, 5 Tangent Poles) Assumes BASE CASE scenario with fully loaded cost. Contingency and escalation rates MUST be applied to get final project costs. | Complexity Factors Include: 1) Remote locations with difficult access 2) Type of CPUC permitting, including environmental restrictions & any mitigation required 3) Freeway/railroad crossings 4) Single circuit vs. double circuit/bundled 5) Distribution poles replaced and/or wire reconductored 6) New SDGE fiber installed or existing SDGE fiber spliced 7) Type of material
[5 empty] | Medium | 6480 | 6480 | 6480 | N/A
[5 empty] | High | 8640 | 8640 | 8640 | N/A
Removal of Transmission Line (complete tear down)
|  | Single Circuit |  | per mile |  | 1080 | 1080 | N/A | N/A |  | Cost of removal assumes wood poles and one conductor per phase removed - 12 poles per mile. These costs do not include contingency.
Reconductor/Upgrade Transmission Line
Complexity
|  | Single Circuit Steel Poles |  | per mile | Low | 1620 | 1620 | 1620 | N/A |  | Includes installation of new conductor and removal of old conductor. Assumes BASE CASE scenario with fully loaded cost. Contingency and escalation rates MUST be applied to get final project costs. | Complexity Factors Include: 1) Remote locations with difficult access 2) Type of CPUC permitting, including environmental restrictions & any mitigation required 3) Freeway/railroad crossings 4) Single circuit vs. double circuit/bundled 5) Distribution poles replaced and/or wire reconductored 6) New SDGE fiber installed or existing SDGE fiber spliced 7) Type of material
[5 empty] | Medium | 2160 | 2160 | 2160 | N/A
[5 empty] | High | 2700 | 2700 | 2700 | N/A
Metering
|  | Upgrade of existing RTUs |  | lump sum
Lump Sum costs, in addition to per-unit or lump-sum costs listed above:
| Engineering costs |  |  | lump sum | [6 empty] | Engineering costs are variable and will be estimated as a lump sum.
| Capitalized Licensing and Permitting Costs, including |  |  | lump sum | [6 empty] | N/A
mitigation measures, FAA permits, etc.
| Civil work: Site Preparation including site grading, ground grid, | [9 empty] | Site Development costs are highly variable and will be estimated as a lump sum.
| and walls/fencing/containment |  |  | lump sum
| General Facilities: station light & power, backup generator, |  |  | lump sum
station utilities (water, gas, etc. if manned substation)
| Substation Control (MEER) Buildings |  |  | lump sum
| Incremental cost for transmission line crossings (roads, |  |  | lump sum
streams, rail, highway, other T\L)
| Land cost for substations and T/L ROW |  |  | lump sum | [6 empty] | Land costs are highly variable.
As a result, will be estimated as a lump sum
| Incremental cost of soil/geotechnical mitigation measures |  |  | lump sum | [6 empty] | Unable to perform detailed geotechnical
analysis of land in Phase I study, but
any known geotech mitigation measures
will be estimated as a lump sum
| Incremental environmental monitoring and mitigations |  |  | lump sum
| Corporate Overheads (A&G, P&B, and AFUDC) | [9 empty] | N/A
Income Tax Component of Contribution (ITCC)

## Factors & Assumptions
Assumptions in the unit cost guide
All labor is straight time and based on a 5 day work week schedule.
General contingency factor: may add upt 50% for Transmission. Estimates include EMF field management plan implementation.
Transmission line design in high wind areas is based on GO-95 Rule 31.1 for known local conditions applying NESC 250C design factors. This can result in a cost increase as the designs may change from wood equivalent steel to engineered steel poles with foundations. Foundations assume a mix of micro-pile and pier type.
** For Substation construction costs in remote areas a factor multiplier should be applied for labor and labor overheads. Apply a Factor amount of 1.25 to the total cost of the Substation work. Site Purchase, site Development or grading costs are not included in Substation costs.
Unit cost guide assumes facilities are constructed by Union crews under the direction of SDG&E.
In addition to material and construction costs the unit costs include exemplary costs for engineering, project management, construction management, contracted surveying, internal Land Services support, environmental, permitting, and labor overhead costs.
Unit costs exclude AFUDC and CIAC.
Unit costs exclude generator's responsibility for Income Tax Component of Contribution (ITCC), (will be added to total cost estimates, if required)
Transmission line cost per mile assumes conventional construction.
Cost per mile of T\L requiring helicopter construction (or deconstruction) will have higher than published per-unit cost, the labor component of helicopter construction is incrementally higher, which is not included in the per-unit cost
Typically SDG&E will perform project specific costs estimates for PTO Interconnections, Reliability and Delivery Network upgrades instead of using the per-unit costs. These costs are provided for the IC to use in their selection of alternative sites or methods of interconnection.
A minimum cost of $180k is required for any project, regardless of assigned network upgrades or PTO's Interconnection facilties, to account for the administration, project management, documentation, engineering, design, and land management directly related to the Generator Interconnection. This "Cost of Interconnection" is considered a Network Upgrade for cost recovery purposes

## Escalation Rates and Factors 21
SUPPLEMENT TO THE SDG&E PTO 2022 UNIT COST GUIDE
OVERVIEW :
Current PTO Unit Cost Guide as posted on the CAISO website is in 2022 Constant Dollars.
PTO’s cost estimating is done in constant dollars and then escalated over the years during which the
project will be constructed, arriving at project costs in nominal dollars.
DEFINITIONS USED :
Project Cost in Constant Dollars represents the cost of the Project if all costs were paid for at a single point
in time.
Project Cost in Nominal Dollars represents the cost of the Project taking into account when actual dollars will be spent.
Mathematical formula: Cost in Nominal Dollars |  |  |  |  | = Cost in Constant Dollars + Escalation
= Cost in Constant Dollars x Escalation Factor
CURRENT PTO ESCALATION RATES *: Revised January 2022
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Escalation Rates |  | 2.3% | 5.089% | 2.928% | 1.641% | 2.799% | 4.712% | 2.4% | 1.562% | 0.8654% | 1.335% | 1.693% | 1.85% | 2.089% | 2.046% | 2.092% | 1.879%
Escalation Factors | 0.826 | 0.845 | 0.888 | 0.914 | 0.929 | 0.955 | 1 | 1.024 | 1.04 | 1.049 | 1.063 | 1.081 | 1.101 | 1.124 | 1.147 | 1.171 | 1.193
* Escalation Rates are from IHS Global Insight's 4th Quarter 2021 Power Planner (released January 2022) electric utility construction cost forecast for "Total Transmission Plant, Pacific Region--JUEPT@PCF".
| 693.5 | 709.5 | 745 | 766.75 | 784.7048 | 797.7597 | 812.13 | 829.6404 | 848.0514 | 865.4402 | 882.6149 | 900.603 | 918.6878 | 937.0499 | 953.5024
| 0.86931 | 0.88937 | 0.93387 | 0.96113 | 0.98364 | 1 | 1.018 | 1.04 | 1.063 | 1.0848 | 1.1064 | 1.1289 | 1.1516 | 1.1746 | 1.1952