## Read Me
*CAISO Public*
2026 Summer Loads and Resources Assessment Report
2026 Summer Loads and Resources Assessment - Technical Appendix
Description | An hourly loads and resource contribution analysis was performed to analyze the hourly reserve margin for the expected “All RA eligible” fleet of Summer 2026. The multi-hour stack assessment of this fleet indicates a reasonable margin above the planning reserve margin (PRM) required to achieve a 0.1 LOLE target. The multi-hour approach for all RA eligible resource portfolio focuses on a reasonable expectation of resource availability during every hour of the peak day in each of the summer months. For most resource types, the NQC value provides a reasonable estimation of the contribution/availability of those resources every hour.
Data Sources
Existing and New resources | - Existing resources are based on CAISO 2026 NQC list published in February 2026. - Expected new resources are resources not on the NQC list, but are expected to be online by June 30, 2026. The NQC MW of an expected resource (excluding wind, solar, and battery) is based upon technology factors in the 2026 NQC list. - Existing and new resources contracted under the Strategic Reliability Reserve (SRR) program are excluded from this stack analysis.
Demand | The load profiles used in this analysis are based on the CEC’s 2025 IEPR 1-in-2 planning forecast for CAISO for the peak day in each summer month of 2026.
Energy storage | Battery storage resources are assumed to be capable of one 4-hour cycle per day, but also are capable of spreading out their discharge energy across more than four hours if necessary. The base scenario optimizes battery discharge to maintain the maximum percent surplus over the 24 hour period. The batteries are tuned upward during this time range until 95 percent of the 4 hour storage depth is reached.
Nuclear | Nuclear capacity within the CAISO footprint is included in the model, and capacity outside the CAISO footprint (Palo Verde dynamic import) is included as imports.
Wind and Solar | Wind and solar profiles are derived based on eight (8) years of historical generation data (2018 – 2025) for the five (5) highest load days using exceedance methodology. Solar profiles are calculated using a 70 percent exceedance level. Wind profiles are calculated using an 80 percent exceedance level for summer, and 65% exceedance level for non-summer months.
Demand Response | Demand response (DR) capacity includes CPUC-jurisdictional utility (IOU) DR, non-CPUC jurisdictional DR, and third party DR. DR capacity for PG&E, SCE, and SDG&E is sourced from the utility provided projections to the CPUC. DR for third party providers are sourced from the 2026 NQC list. Non-CPUC jurisdictional load serving entities (municipal utilities) DR values are sourced from DMM’s 2024 DR issues and performance report. DR capacity is assumed to be available from HE 18 to 23 (PDT)
Imports | Net Import capacity is allowed up to the Maximum Import Capability (MIC) value of 11,665 MW except during the evening net peak hours (HE17-23) where it is limited to 5,500 MW plus output from the Sunzia wind resource. The Sunzia output is derived from NREL wind profile data and capped at 1,009 MW to reflect transmission constraints.
Other Renewables | Includes existing and expected resources from Biogas, Biomass, and Geothermal fuel categories
Other | Includes non-demand response resources clasified as "Other" such as qualified facilities, Waste to Power, Distillate, and Hybrid fuel types
Planning Reserve Margin | The PRM required to meet a 0.1 LOLE is calculated in two steps: 1) The model constructs the resource stack and optimizes battery dispatch to maximize percent surplus during the evening peak hours in September (17 – 23), achieving an hourly surplus of 13,494 MW. This results in an 'achieved PRM' of 30.8 percent based on the current portfolio. 2) The model then integrates results from the probabilistic study, which identifies 2,547 MW of surplus that can be removed to achieve a 0.1 LOLE target. After evenly distributing this reduction across all hours, the surplus during September peak hours (17 – 23) decreases to 10,947 MW. The model subsequently recalculates the PRM, resulting in a requirement of 25 percent to meet the reliability target.
17.5 percent Load-weighted PRM of LSE monthly RA obligations: | The majority of LSE’s are under CPUC jurisdiction and are required to meet a 18 percent PRM for their RA obligation; the remaining LSE’s have a mix of PRMs depending on their Local Regulatory Authority (LRA).

## Monthly Charts
MONTH | HOUR (PDT) | 2025 IEPR Forecast | Forecast + 17.5% PRM | Forecast + 25.0% PRM | Charging Load | Natural Gas | Nuclear | Hydro | Other | Other Renewables | Solar | Wind | Imports | Battery Storage | Demand Response | Charging Load Curve
5 | 1 | 25190 | 29598.25 | 31487.5 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 4064.5746 | 11665 | 0 | 0 | 31487.5
5 | 2 | 23503 | 27616.025 | 29378.75 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3773.4784 | 11665 | 0 | 0 | 29378.75
5 | 3 | 22463 | 26394.025 | 28078.75 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3512.4239 | 11665 | 0 | 0 | 28078.75
5 | 4 | 21857 | 25681.975 | 27321.25 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3135.5164 | 11665 | 0 | 0 | 27321.25
5 | 5 | 21889 | 25719.575 | 27361.25 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 2693.374 | 11665 | 0 | 0 | 27361.25
5 | 6 | 22612 | 26569.1 | 28265 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 16.3775 | 2235.6472 | 11665 | 0 | 0 | 28265
5 | 7 | 23304 | 27382.2 | 29130 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 1768.7479 | 1853.5831 | 11665 | 0 | 0 | 29130
5 | 8 | 23834 | 28004.95 | 29792.5 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 7546.6355 | 1203.9964 | 11665 | 0 | 0 | 29792.5
5 | 9 | 23667 | 27808.725 | 29583.75 | 3849.383 | 25945 | 2280 | 5968 | 1106 | 1665 | 11491.3047 | 845.9498 | 11665 | 0 | 0 | 33433.133
5 | 10 | 22909 | 26918.075 | 28636.25 | 6687.6824 | 25945 | 2280 | 5968 | 1106 | 1665 | 13096.2781 | 756.478 | 11665 | 0 | 0 | 35323.9324
5 | 11 | 21665 | 25456.375 | 27081.25 | 8918.7739 | 25945 | 2280 | 5968 | 1106 | 1665 | 13683.8087 | 712.0705 | 11665 | 0 | 0 | 36000.0239
5 | 12 | 20810 | 24451.75 | 26012.5 | 10232.6123 | 25945 | 2280 | 5968 | 1106 | 1665 | 13934.1096 | 659.1651 | 11665 | 0 | 0 | 36245.1123
5 | 13 | 20729 | 24356.575 | 25911.25 | 10523.5851 | 25945 | 2280 | 5968 | 1106 | 1665 | 14138.5981 | 606.7483 | 11665 | 0 | 0 | 36434.8351
5 | 14 | 21365 | 25103.875 | 26706.25 | 9547.6342 | 25945 | 2280 | 5968 | 1106 | 1665 | 13800.2403 | 799.3612 | 11665 | 0 | 0 | 36253.8842
5 | 15 | 22464 | 26395.2 | 28080 | 8158.1062 | 25945 | 2280 | 5968 | 1106 | 1665 | 13701.4228 | 884.1552 | 11665 | 0 | 0 | 36238.1062
5 | 16 | 24212 | 28449.1 | 30265 | 5689.0412 | 25945 | 2280 | 5968 | 1106 | 1665 | 13034.4059 | 1321.4303 | 11665 | 0 | 0 | 35954.0412
5 | 17 | 26243 | 30835.525 | 32803.75 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 11462.4556 | 2283.1334 | 6509 | 0 | 0 | 32803.75
5 | 18 | 28610 | 33616.75 | 35762.5 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 9223.8407 | 2958.2984 | 6509 | 2915.4505 | 0 | 35762.5
5 | 19 | 30424 | 35748.2 | 38030 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 4412.7256 | 3223.8761 | 6509 | 9071.6894 | 572.5336 | 38030
5 | 20 | 30978 | 36399.15 | 38722.5 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 452.7183 | 3127.5921 | 6509 | 11725.0129 | 572.5336 | 38722.5
5 | 21 | 31029 | 36459.075 | 38786.25 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3608.0147 | 6509 | 11725.0129 | 572.5336 | 38786.25
5 | 22 | 29988 | 35235.9 | 37485 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3993.7542 | 6509 | 11246.5669 | 572.5336 | 37485
5 | 23 | 27939 | 32828.325 | 34923.75 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3967.4677 | 6509 | 7886.6984 | 572.5336 | 34923.75
5 | 24 | 26183 | 30765.025 | 32728.75 | 0 | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3888.5135 | 11665 | 1403.569 | 0 | 32728.75
6 | 1 | 30134 | 35407.45 | 37667.5 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 3035.3124 | 11665 | 0 | 0 | 37667.5
6 | 2 | 27085 | 31824.875 | 33856.25 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 2426.6115 | 11665 | 0 | 0 | 33856.25
6 | 3 | 25545 | 30015.375 | 31931.25 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 1985.5121 | 11665 | 0 | 0 | 31931.25
6 | 4 | 24687 | 29007.225 | 30858.75 | 165.1364 | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 1837.5882 | 11665 | 0 | 0 | 31023.8864
6 | 5 | 24588 | 28890.9 | 30735 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 1407.2298 | 11665 | 0 | 0 | 30735
6 | 6 | 25165 | 29568.875 | 31456.25 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 31.3069 | 1062.5257 | 11665 | 0 | 0 | 31456.25
6 | 7 | 25878 | 30406.65 | 32347.5 | 545.6781 | 25889 | 2280 | 6248 | 1687 | 1681 | 2370.353 | 973.1944 | 11665 | 0 | 0 | 32893.1781
6 | 8 | 27161 | 31914.175 | 33951.25 | 5460.8 | 25889 | 2280 | 6248 | 1687 | 1681 | 7888.9211 | 745.2964 | 11665 | 0 | 0 | 39412.05
6 | 9 | 27927 | 32814.225 | 34908.75 | 8412.6825 | 25889 | 2280 | 6248 | 1687 | 1681 | 11246.8501 | 560.2603 | 11665 | 0 | 0 | 43321.4325
6 | 10 | 27969 | 32863.575 | 34961.25 | 10496.8423 | 25889 | 2280 | 6248 | 1687 | 1681 | 13111.1396 | 437.3436 | 11665 | 0 | 0 | 45458.0923
6 | 11 | 28213 | 33150.275 | 35266.25 | 11288.3545 | 25889 | 2280 | 6248 | 1687 | 1681 | 13861.9848 | 575.8782 | 11665 | 0 | 0 | 46554.6045
6 | 12 | 28815 | 33857.625 | 36018.75 | 10738.9726 | 25889 | 2280 | 6248 | 1687 | 1681 | 14125.1626 | 466.7478 | 11665 | 0 | 0 | 46757.7226
6 | 13 | 30045 | 35302.875 | 37556.25 | 9327.7445 | 25889 | 2280 | 6248 | 1687 | 1681 | 14178.283 | 492.9465 | 11665 | 0 | 0 | 46883.9945
6 | 14 | 32330 | 37987.75 | 40412.5 | 6180.5918 | 25889 | 2280 | 6248 | 1687 | 1681 | 13765.1508 | 624.9674 | 11665 | 0 | 0 | 46593.0918
6 | 15 | 34980 | 41101.5 | 43725 | 2933.1972 | 25889 | 2280 | 6248 | 1687 | 1681 | 13487.6053 | 904.6668 | 11665 | 0 | 0 | 46658.1972
6 | 16 | 37916 | 44551.3 | 47395 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 12843.9644 | 1412.3668 | 11665 | 0 | 0 | 47395
6 | 17 | 39318 | 46198.65 | 49147.5 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 11505.9043 | 1972.0738 | 6509 | 2738.266 | 0 | 49147.5
6 | 18 | 40950 | 48116.25 | 51187.5 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 9660.2112 | 2653.8564 | 6509 | 5563.7293 | 864.4643 | 51187.5
6 | 19 | 41537 | 48805.975 | 51921.25 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 5699.3294 | 2937.8503 | 6509 | 10168.2001 | 864.4643 | 51921.25
6 | 20 | 40660 | 47775.5 | 50825 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 1284.6251 | 3437.0845 | 6509 | 12747.9704 | 864.4643 | 50825
6 | 21 | 39511 | 46425.425 | 49388.75 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 16.6515 | 3747.1949 | 6509 | 11933.6344 | 864.4643 | 49388.75
6 | 22 | 37852 | 44476.1 | 47315 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 3992.2504 | 6509 | 9132.7163 | 864.4643 | 47315
6 | 23 | 34932 | 41045.1 | 43665 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 4079.2095 | 6509 | 5399.4834 | 0 | 43665
6 | 24 | 32032 | 37637.6 | 40040 | 0 | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 3940.5311 | 11665 | 0 | 0 | 40040
7 | 1 | 32217 | 37854.975 | 40271.25 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3487.4066 | 11665 | 0 | 0 | 40271.25
7 | 2 | 29273 | 34395.775 | 36591.25 | 670.4484 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3494.0847 | 11665 | 0 | 0 | 37261.6984
7 | 3 | 27641 | 32478.175 | 34551.25 | 2429.5088 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3245.0429 | 11665 | 0 | 0 | 36980.7588
7 | 4 | 26675 | 31343.125 | 33343.75 | 3551.5906 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3161.2893 | 11665 | 0 | 0 | 36895.3406
7 | 5 | 26476 | 31109.3 | 33095 | 3203.2241 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 2687.1748 | 11665 | 0 | 0 | 36298.2241
7 | 6 | 27219 | 31982.325 | 34023.75 | 1679.3811 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 9.693 | 2227.9374 | 11665 | 0 | 0 | 35703.1311
7 | 7 | 28202 | 33137.35 | 35252.5 | 1356.6573 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 1179.4654 | 1787.2616 | 11665 | 0 | 0 | 36609.1573
7 | 8 | 29701 | 34898.675 | 37126.25 | 5112.7384 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 6047.4209 | 1373.4078 | 11665 | 0 | 0 | 42238.9884
7 | 9 | 30679 | 36047.825 | 38348.75 | 8849.1593 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 10518.9673 | 819.4953 | 11665 | 0 | 0 | 47197.9093
7 | 10 | 31350 | 36836.25 | 39187.5 | 10088.8827 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 12412.7398 | 572.0769 | 11665 | 0 | 0 | 49276.3827
7 | 11 | 32030 | 37635.25 | 40037.5 | 10224.8254 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13280.3028 | 491.4671 | 11665 | 0 | 0 | 50262.3254
7 | 12 | 33620 | 39503.5 | 42025 | 8476.3389 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13553.6925 | 432.4532 | 11665 | 0 | 0 | 50501.3389
7 | 13 | 35087 | 41227.225 | 43858.75 | 6844.9619 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13566.8411 | 602.8167 | 11665 | 0 | 0 | 50703.7119
7 | 14 | 37833 | 44453.775 | 47291.25 | 3291.1468 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13374.8652 | 744.8239 | 11665 | 0 | 0 | 50582.3968
7 | 15 | 40911 | 48070.425 | 51138.75 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13031.6723 | 1085.5303 | 11665 | 0 | 0 | 51138.75
7 | 16 | 43792 | 51455.6 | 54740 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 12436.428 | 1881.1694 | 11665 | 0 | 0 | 54740
7 | 17 | 45272 | 53194.6 | 56590 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 11267.4676 | 2639.6783 | 6509 | 5655.93 | 0 | 56590
7 | 18 | 46301 | 54403.675 | 57876.25 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 9131.1984 | 3230.6388 | 6509 | 7582.1134 | 1073.3337 | 57876.25
7 | 19 | 46016 | 54068.8 | 57520 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 5184.4885 | 3305.8316 | 6509 | 11022.056 | 1073.3337 | 57520
7 | 20 | 44183 | 51915.025 | 55228.75 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 961.5725 | 3701.9482 | 6509 | 12224.8204 | 1073.3337 | 55228.75
7 | 21 | 42183 | 49565.025 | 52728.75 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 4111.5315 | 6509 | 9931.5509 | 1073.3337 | 52728.75
7 | 22 | 40436 | 47512.3 | 50545 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 4274.6562 | 6443.6885 | 7363.2528 | 1073.3337 | 50545
7 | 23 | 37291 | 43816.925 | 46613.75 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 4136.3535 | 6359.1059 | 4105.6765 | 89 | 46613.75
7 | 24 | 34306 | 40309.55 | 42882.5 | 0 | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3979.1818 | 11665 | 0 | 0 | 42882.5
8 | 1 | 31805 | 37370.875 | 39756.25 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2839.3252 | 11665 | 0 | 0 | 39756.25
8 | 2 | 29064 | 34150.2 | 36330 | 491.3225 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2773.0759 | 11665 | 0 | 0 | 36821.3225
8 | 3 | 27467 | 32273.725 | 34333.75 | 2106.9523 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2366.9447 | 11665 | 0 | 0 | 36440.7023
8 | 4 | 26449 | 31077.575 | 33061.25 | 3063.4265 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2053.6904 | 11665 | 0 | 0 | 36124.6765
8 | 5 | 26322 | 30928.35 | 32902.5 | 2813.4079 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 1742.306 | 11665 | 0 | 0 | 35715.9079
8 | 6 | 27221 | 31984.675 | 34026.25 | 1376.0721 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 1580.6421 | 11665 | 0 | 0 | 35402.3221
8 | 7 | 28524 | 33515.7 | 35655 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 392.0205 | 1207.0512 | 11665 | 0 | 0 | 35655
8 | 8 | 29522 | 34688.35 | 36902.5 | 3070.2073 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 4245.2737 | 890.6531 | 11665 | 0 | 0 | 39972.7073
8 | 9 | 30164 | 35442.7 | 37705 | 8222.7709 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 9007.9026 | 569.0563 | 11665 | 0 | 0 | 45927.7709
8 | 10 | 30630 | 35990.25 | 38287.5 | 10962.7204 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 11527.1041 | 536.0445 | 11665 | 0 | 0 | 49250.2204
8 | 11 | 31346 | 36831.55 | 39182.5 | 11498.0237 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 12766.8179 | 407.0148 | 11665 | 0 | 0 | 50680.5237
8 | 12 | 32786 | 38523.55 | 40982.5 | 10165.7418 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 13307.0145 | 324.5146 | 11665 | 0 | 0 | 51148.2418
8 | 13 | 34498 | 40535.15 | 43122.5 | 8289.9771 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 13562.3315 | 398.1791 | 11665 | 0 | 0 | 51412.4771
8 | 14 | 37412 | 43959.1 | 46765 | 3718.241 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 13041.9527 | 461.7752 | 11665 | 0 | 0 | 50483.241
8 | 15 | 40213 | 47250.275 | 50266.25 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 12671.3224 | 523.2137 | 11665 | 0 | 0 | 50266.25
8 | 16 | 42688 | 50158.4 | 53360 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 11556.0793 | 690.2073 | 11665 | 0 | 0 | 53360
8 | 17 | 44147 | 51872.725 | 55183.75 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 10023.1406 | 1221.9074 | 6474.3344 | 5387.1367 | 0 | 55183.75
8 | 18 | 45511 | 53475.425 | 56888.75 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 6975.4569 | 1761.354 | 6509 | 8657.8878 | 990.8502 | 56888.75
8 | 19 | 45390 | 53333.25 | 56737.5 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 2520.5665 | 2334.4377 | 6509 | 12260.761 | 990.8502 | 56737.5
8 | 20 | 43810 | 51476.75 | 54762.5 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 134.6503 | 2594.2466 | 6509 | 12200.4599 | 990.8502 | 54762.5
8 | 21 | 41824 | 49143.2 | 52280 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2848.0762 | 6509 | 9410.1362 | 990.8502 | 52280
8 | 22 | 39818 | 46786.15 | 49772.5 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 3086.3096 | 6506.2061 | 6487.2746 | 990.8502 | 49772.5
8 | 23 | 36619 | 43027.325 | 45773.75 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2746.4662 | 6447.366 | 3481.7437 | 58 | 45773.75
8 | 24 | 33632 | 39517.6 | 42040 | 0 | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2665.4249 | 11665 | 0 | 0 | 42040
9 | 1 | 31904 | 37487.2 | 39880 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1207.7087 | 11665 | 0 | 0 | 39880
9 | 2 | 28847 | 33895.225 | 36058.75 | 774.419 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1179.5168 | 11665 | 0 | 0 | 36833.169
9 | 3 | 27272 | 32044.6 | 34090 | 2766.5282 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1170.5168 | 11665 | 0 | 0 | 36856.5282
9 | 4 | 26279 | 30877.825 | 32848.75 | 3765.8924 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 962.756 | 11665 | 0 | 0 | 36614.6424
9 | 5 | 26059 | 30619.325 | 32573.75 | 3560.5508 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 580.707 | 11665 | 0 | 0 | 36134.3008
9 | 6 | 27014 | 31741.45 | 33767.5 | 2289.2067 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 534.022 | 11665 | 0 | 0 | 36056.7067
9 | 7 | 28829 | 33874.075 | 36036.25 | 178.7029 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 158.5948 | 538.3576 | 11665 | 0 | 0 | 36214.9529
9 | 8 | 30065 | 35326.375 | 37581.25 | 2828.5977 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 3489.9487 | 526.4117 | 11665 | 0 | 0 | 40409.8477
9 | 9 | 31045 | 36477.875 | 38806.25 | 8248.271 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 8805.2316 | 452.1998 | 11665 | 0 | 0 | 47054.521
9 | 10 | 32164 | 37792.7 | 40205 | 10158.6933 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 11543.7428 | 334.7064 | 11665 | 0 | 0 | 50363.6933
9 | 11 | 33020 | 38798.5 | 41275 | 10512.734 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12652.3511 | 360.453 | 11665 | 0 | 0 | 51787.734
9 | 12 | 34225 | 40214.375 | 42781.25 | 9628.4349 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13197.4375 | 325.1105 | 11665 | 0 | 0 | 52409.6849
9 | 13 | 36070 | 42382.25 | 45087.5 | 7461.2398 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13311.6623 | 351.9872 | 11665 | 0 | 0 | 52548.7398
9 | 14 | 38804 | 45594.7 | 48505 | 3605.5929 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12859.312 | 506.9397 | 11665 | 0 | 0 | 52110.5929
9 | 15 | 41613 | 48895.275 | 52016.25 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12424.1951 | 514.9338 | 11665 | 0 | 0 | 52016.25
9 | 16 | 45004 | 52879.7 | 56255 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 11773.8157 | 527.5494 | 11665 | 0 | 0 | 56255
9 | 17 | 46087 | 54152.225 | 57608.75 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 8964.9146 | 644.4709 | 6509 | 6682.9046 | 0 | 57608.75
9 | 18 | 46844 | 55041.7 | 58555 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 5520.3037 | 871.2763 | 6509 | 9800.3395 | 970.5018 | 58555
9 | 19 | 46546 | 54691.55 | 58182.5 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 1172.8306 | 1277.6952 | 6509 | 13207.7744 | 970.5018 | 58182.5
9 | 20 | 44877 | 52730.475 | 56096.25 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13.0622 | 1472.3258 | 6509 | 12020.0754 | 970.5018 | 56096.25
9 | 21 | 42389 | 49807.075 | 52986.25 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1759.443 | 6509 | 8599.3367 | 970.5018 | 52986.25
9 | 22 | 40017 | 47019.975 | 50021.25 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1893.5393 | 6509 | 5466.5412 | 970.5018 | 50021.25
9 | 23 | 36609 | 43015.575 | 45761.25 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1783.7719 | 6509 | 2108.4283 | 81 | 45761.25
9 | 24 | 33702 | 39599.85 | 42127.5 | 0 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1722.1895 | 11665 | 0 | 0 | 42127.5

## Chart Data
MONTH | Day | HOUR (PDT) | 2025 IEPR Forecast | Forecast + 17.5% PRM | Forecast + 25.0% PRM | Charging Load (Y/N) | Natural Gas | Nuclear | Hydro | Other | Other Renewables | Solar | Wind | Imports | Battery Storage | Demand Response | Surplus MW | Suprlus % | Surplus MW at 0.1 LOLE | Surplus % at 0.1 LOLE
5 | 27 | 1 | 25190 | 29598.25 | 31487.5 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 4064.5746 | 11665 | 0 | 0 | 27503.5746 | 109.2% | 24956.5746 | 99.07%
5 | 27 | 2 | 23503 | 27616.025 | 29378.75 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3773.4784 | 11665 | 0 | 0 | 28899.4784 | 123% | 26352.4784 | 112.1%
5 | 27 | 3 | 22463 | 26394.025 | 28078.75 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3512.4239 | 11665 | 0 | 0 | 29678.4239 | 132.1% | 27131.4239 | 120.8%
5 | 27 | 4 | 21857 | 25681.975 | 27321.25 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3135.5164 | 11665 | 0 | 0 | 29907.5164 | 136.8% | 27360.5164 | 125.2%
5 | 27 | 5 | 21889 | 25719.575 | 27361.25 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 2693.374 | 11665 | 0 | 0 | 29433.374 | 134.5% | 26886.374 | 122.8%
5 | 27 | 6 | 22612 | 26569.1 | 28265 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 16.3775 | 2235.6472 | 11665 | 0 | 0 | 28269.0246 | 125% | 25722.0246 | 113.8%
5 | 27 | 7 | 23304 | 27382.2 | 29130 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 1768.7479 | 1853.5831 | 11665 | 0 | 0 | 28947.3311 | 124.2% | 26400.3311 | 113.3%
5 | 27 | 8 | 23834 | 28004.95 | 29792.5 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 7546.6355 | 1203.9964 | 11665 | 0 | 0 | 33545.632 | 140.7% | 30998.632 | 130.1%
5 | 27 | 9 | 23667 | 27808.725 | 29583.75 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 11491.3047 | 845.9498 | 11665 | 0 | 0 | 37299.2545 | 157.6% | 34752.2545 | 146.8%
5 | 27 | 10 | 22909 | 26918.075 | 28636.25 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 13096.2781 | 756.478 | 11665 | 0 | 0 | 39572.7562 | 172.7% | 37025.7562 | 161.6%
5 | 27 | 11 | 21665 | 25456.375 | 27081.25 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 13683.8087 | 712.0705 | 11665 | 0 | 0 | 41359.8792 | 190.9% | 38812.8792 | 179.2%
5 | 27 | 12 | 20810 | 24451.75 | 26012.5 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 13934.1096 | 659.1651 | 11665 | 0 | 0 | 42412.2748 | 203.8% | 39865.2748 | 191.6%
5 | 27 | 13 | 20729 | 24356.575 | 25911.25 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 14138.5981 | 606.7483 | 11665 | 0 | 0 | 42645.3465 | 205.7% | 40098.3465 | 193.4%
5 | 27 | 14 | 21365 | 25103.875 | 26706.25 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 13800.2403 | 799.3612 | 11665 | 0 | 0 | 41863.6016 | 195.9% | 39316.6016 | 184%
5 | 27 | 15 | 22464 | 26395.2 | 28080 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 13701.4228 | 884.1552 | 11665 | 0 | 0 | 40750.578 | 181.4% | 38203.578 | 170.1%
5 | 27 | 16 | 24212 | 28449.1 | 30265 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 13034.4059 | 1321.4303 | 11665 | 0 | 0 | 38772.8362 | 160.1% | 36225.8362 | 149.6%
5 | 27 | 17 | 26243 | 30835.525 | 32803.75 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 11462.4556 | 2283.1334 | 6509 | 0 | 0 | 30975.589 | 118% | 28428.589 | 108.3%
5 | 27 | 18 | 28610 | 33616.75 | 35762.5 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 9223.8407 | 2958.2984 | 6509 | 2915.4505 | 0 | 29960.5897 | 104.7% | 27413.5897 | 95.82%
5 | 27 | 19 | 30424 | 35748.2 | 38030 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 4412.7256 | 3223.8761 | 6509 | 9071.6894 | 572.5336 | 30329.8247 | 99.69% | 27782.8247 | 91.32%
5 | 27 | 20 | 30978 | 36399.15 | 38722.5 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 452.7183 | 3127.5921 | 6509 | 11725.0129 | 572.5336 | 28372.8569 | 91.59% | 25825.8569 | 83.37%
5 | 27 | 21 | 31029 | 36459.075 | 38786.25 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3608.0147 | 6509 | 11725.0129 | 572.5336 | 28349.5612 | 91.36% | 25802.5612 | 83.16%
5 | 27 | 22 | 29988 | 35235.9 | 37485 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3993.7542 | 6509 | 11246.5669 | 572.5336 | 29297.8547 | 97.7% | 26750.8547 | 89.21%
5 | 27 | 23 | 27939 | 32828.325 | 34923.75 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3967.4677 | 6509 | 7886.6984 | 572.5336 | 27960.6998 | 100.1% | 25413.6998 | 90.96%
5 | 27 | 24 | 26183 | 30765.025 | 32728.75 | N | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3888.5135 | 11665 | 1403.569 | 0 | 27738.0825 | 105.9% | 25191.0825 | 96.21%
6 | 24 | 1 | 30134 | 35407.45 | 37667.5 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 3035.3124 | 11665 | 0 | 0 | 22351.3124 | 74.17% | 19804.3124 | 65.72%
6 | 24 | 2 | 27085 | 31824.875 | 33856.25 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 2426.6115 | 11665 | 0 | 0 | 24791.6115 | 91.53% | 22244.6115 | 82.13%
6 | 24 | 3 | 25545 | 30015.375 | 31931.25 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 1985.5121 | 11665 | 0 | 0 | 25890.5121 | 101.4% | 23343.5121 | 91.38%
6 | 24 | 4 | 24687 | 29007.225 | 30858.75 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 1837.5882 | 11665 | 0 | 0 | 26600.5882 | 107.8% | 24053.5882 | 97.43%
6 | 24 | 5 | 24588 | 28890.9 | 30735 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 1407.2298 | 11665 | 0 | 0 | 26269.2298 | 106.8% | 23722.2298 | 96.48%
6 | 24 | 6 | 25165 | 29568.875 | 31456.25 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 31.3069 | 1062.5257 | 11665 | 0 | 0 | 25378.8327 | 100.8% | 22831.8327 | 90.73%
6 | 24 | 7 | 25878 | 30406.65 | 32347.5 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 2370.353 | 973.1944 | 11665 | 0 | 0 | 26915.5474 | 104% | 24368.5474 | 94.17%
6 | 24 | 8 | 27161 | 31914.175 | 33951.25 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 7888.9211 | 745.2964 | 11665 | 0 | 0 | 30923.2175 | 113.9% | 28376.2175 | 104.5%
6 | 24 | 9 | 27927 | 32814.225 | 34908.75 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 11246.8501 | 560.2603 | 11665 | 0 | 0 | 33330.1104 | 119.3% | 30783.1104 | 110.2%
6 | 24 | 10 | 27969 | 32863.575 | 34961.25 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 13111.1396 | 437.3436 | 11665 | 0 | 0 | 35029.4833 | 125.2% | 32482.4833 | 116.1%
6 | 24 | 11 | 28213 | 33150.275 | 35266.25 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 13861.9848 | 575.8782 | 11665 | 0 | 0 | 35674.863 | 126.4% | 33127.863 | 117.4%
6 | 24 | 12 | 28815 | 33857.625 | 36018.75 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 14125.1626 | 466.7478 | 11665 | 0 | 0 | 35226.9104 | 122.3% | 32679.9104 | 113.4%
6 | 24 | 13 | 30045 | 35302.875 | 37556.25 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 14178.283 | 492.9465 | 11665 | 0 | 0 | 34076.2295 | 113.4% | 31529.2295 | 104.9%
6 | 24 | 14 | 32330 | 37987.75 | 40412.5 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 13765.1508 | 624.9674 | 11665 | 0 | 0 | 31510.1182 | 97.46% | 28963.1182 | 89.59%
6 | 24 | 15 | 34980 | 41101.5 | 43725 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 13487.6053 | 904.6668 | 11665 | 0 | 0 | 28862.2721 | 82.51% | 26315.2721 | 75.23%
6 | 24 | 16 | 37916 | 44551.3 | 47395 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 12843.9644 | 1412.3668 | 11665 | 0 | 0 | 25790.3312 | 68.02% | 23243.3312 | 61.3%
6 | 24 | 17 | 39318 | 46198.65 | 49147.5 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 11505.9043 | 1972.0738 | 6509 | 2738.266 | 0 | 21192.2441 | 53.9% | 18645.2441 | 47.42%
6 | 24 | 18 | 40950 | 48116.25 | 51187.5 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 9660.2112 | 2653.8564 | 6509 | 5563.7293 | 864.4643 | 22086.2612 | 53.93% | 19539.2612 | 47.71%
6 | 24 | 19 | 41537 | 48805.975 | 51921.25 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 5699.3294 | 2937.8503 | 6509 | 10168.2001 | 864.4643 | 22426.8442 | 53.99% | 19879.8442 | 47.86%
6 | 24 | 20 | 40660 | 47775.5 | 50825 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 1284.6251 | 3437.0845 | 6509 | 12747.9704 | 864.4643 | 21968.1443 | 54.03% | 19421.1443 | 47.76%
6 | 24 | 21 | 39511 | 46425.425 | 49388.75 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 16.6515 | 3747.1949 | 6509 | 11933.6344 | 864.4643 | 21344.9452 | 54.02% | 18797.9452 | 47.58%
6 | 24 | 22 | 37852 | 44476.1 | 47315 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 3992.2504 | 6509 | 9132.7163 | 864.4643 | 20431.431 | 53.98% | 17884.431 | 47.25%
6 | 24 | 23 | 34932 | 41045.1 | 43665 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 4079.2095 | 6509 | 5399.4834 | 0 | 18840.6929 | 53.94% | 16293.6929 | 46.64%
6 | 24 | 24 | 32032 | 37637.6 | 40040 | N | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 3940.5311 | 11665 | 0 | 0 | 21358.5311 | 66.68% | 18811.5311 | 58.73%
7 | 22 | 1 | 32217 | 37854.975 | 40271.25 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3487.4066 | 11665 | 0 | 0 | 21416.1987 | 66.47% | 18869.1987 | 58.57%
7 | 22 | 2 | 29273 | 34395.775 | 36591.25 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3494.0847 | 11665 | 0 | 0 | 24366.8768 | 83.24% | 21819.8768 | 74.54%
7 | 22 | 3 | 27641 | 32478.175 | 34551.25 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3245.0429 | 11665 | 0 | 0 | 25749.835 | 93.16% | 23202.835 | 83.94%
7 | 22 | 4 | 26675 | 31343.125 | 33343.75 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3161.2893 | 11665 | 0 | 0 | 26632.0814 | 99.84% | 24085.0814 | 90.29%
7 | 22 | 5 | 26476 | 31109.3 | 33095 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 2687.1748 | 11665 | 0 | 0 | 26356.9669 | 99.55% | 23809.9669 | 89.93%
7 | 22 | 6 | 27219 | 31982.325 | 34023.75 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 9.693 | 2227.9374 | 11665 | 0 | 0 | 25164.4225 | 92.45% | 22617.4225 | 83.09%
7 | 22 | 7 | 28202 | 33137.35 | 35252.5 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 1179.4654 | 1787.2616 | 11665 | 0 | 0 | 24910.5191 | 88.33% | 22363.5191 | 79.3%
7 | 22 | 8 | 29701 | 34898.675 | 37126.25 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 6047.4209 | 1373.4078 | 11665 | 0 | 0 | 27865.6208 | 93.82% | 25318.6208 | 85.25%
7 | 22 | 9 | 30679 | 36047.825 | 38348.75 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 10518.9673 | 819.4953 | 11665 | 0 | 0 | 30805.2548 | 100.4% | 28258.2548 | 92.11%
7 | 22 | 10 | 31350 | 36836.25 | 39187.5 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 12412.7398 | 572.0769 | 11665 | 0 | 0 | 31780.6088 | 101.4% | 29233.6088 | 93.25%
7 | 22 | 11 | 32030 | 37635.25 | 40037.5 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13280.3028 | 491.4671 | 11665 | 0 | 0 | 31887.5619 | 99.56% | 29340.5619 | 91.6%
7 | 22 | 12 | 33620 | 39503.5 | 42025 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13553.6925 | 432.4532 | 11665 | 0 | 0 | 30511.9379 | 90.76% | 27964.9379 | 83.18%
7 | 22 | 13 | 35087 | 41227.225 | 43858.75 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13566.8411 | 602.8167 | 11665 | 0 | 0 | 29228.4499 | 83.3% | 26681.4499 | 76.04%
7 | 22 | 14 | 37833 | 44453.775 | 47291.25 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13374.8652 | 744.8239 | 11665 | 0 | 0 | 26432.4813 | 69.87% | 23885.4813 | 63.13%
7 | 22 | 15 | 40911 | 48070.425 | 51138.75 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13031.6723 | 1085.5303 | 11665 | 0 | 0 | 23351.9947 | 57.08% | 20804.9947 | 50.85%
7 | 22 | 16 | 43792 | 51455.6 | 54740 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 12436.428 | 1881.1694 | 11665 | 0 | 0 | 20671.3895 | 47.2% | 18124.3895 | 41.39%
7 | 22 | 17 | 45272 | 53194.6 | 56590 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 11267.4676 | 2639.6783 | 6509 | 5655.93 | 0 | 19280.868 | 42.59% | 16733.868 | 36.96%
7 | 22 | 18 | 46301 | 54403.675 | 57876.25 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 9131.1984 | 3230.6388 | 6509 | 7582.1134 | 1073.3337 | 19706.0764 | 42.56% | 17159.0764 | 37.06%
7 | 22 | 19 | 46016 | 54068.8 | 57520 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 5184.4885 | 3305.8316 | 6509 | 11022.056 | 1073.3337 | 19559.5019 | 42.51% | 17012.5019 | 36.97%
7 | 22 | 20 | 44183 | 51915.025 | 55228.75 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 961.5725 | 3701.9482 | 6509 | 12224.8204 | 1073.3337 | 18768.467 | 42.48% | 16221.467 | 36.71%
7 | 22 | 21 | 42183 | 49565.025 | 52728.75 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 4111.5315 | 6509 | 9931.5509 | 1073.3337 | 17923.2082 | 42.49% | 15376.2082 | 36.45%
7 | 22 | 22 | 40436 | 47512.3 | 50545 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 4274.6562 | 6443.6885 | 7363.2528 | 1073.3337 | 17199.7234 | 42.54% | 14652.7234 | 36.24%
7 | 22 | 23 | 37291 | 43816.925 | 46613.75 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 4136.3535 | 6359.1059 | 4105.6765 | 89 | 15879.928 | 42.58% | 13332.928 | 35.75%
7 | 22 | 24 | 34306 | 40309.55 | 42882.5 | N | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3979.1818 | 11665 | 0 | 0 | 19818.974 | 57.77% | 17271.974 | 50.35%
8 | 12 | 1 | 31805 | 37370.875 | 39756.25 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2839.3252 | 11665 | 0 | 0 | 20569.1247 | 64.67% | 18022.1247 | 56.66%
8 | 12 | 2 | 29064 | 34150.2 | 36330 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2773.0759 | 11665 | 0 | 0 | 23243.8753 | 79.97% | 20696.8753 | 71.21%
8 | 12 | 3 | 27467 | 32273.725 | 34333.75 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2366.9447 | 11665 | 0 | 0 | 24434.7441 | 88.96% | 21887.7441 | 79.69%
8 | 12 | 4 | 26449 | 31077.575 | 33061.25 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2053.6904 | 11665 | 0 | 0 | 25139.4899 | 95.05% | 22592.4899 | 85.42%
8 | 12 | 5 | 26322 | 30928.35 | 32902.5 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 1742.306 | 11665 | 0 | 0 | 24955.1055 | 94.81% | 22408.1055 | 85.13%
8 | 12 | 6 | 27221 | 31984.675 | 34026.25 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 1580.6421 | 11665 | 0 | 0 | 23894.4416 | 87.78% | 21347.4416 | 78.42%
8 | 12 | 7 | 28524 | 33515.7 | 35655 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 392.0205 | 1207.0512 | 11665 | 0 | 0 | 22609.8712 | 79.27% | 20062.8712 | 70.34%
8 | 12 | 8 | 29522 | 34688.35 | 36902.5 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 4245.2737 | 890.6531 | 11665 | 0 | 0 | 25148.7262 | 85.19% | 22601.7262 | 76.56%
8 | 12 | 9 | 30164 | 35442.7 | 37705 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 9007.9026 | 569.0563 | 11665 | 0 | 0 | 28947.7583 | 95.97% | 26400.7583 | 87.52%
8 | 12 | 10 | 30630 | 35990.25 | 38287.5 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 11527.1041 | 536.0445 | 11665 | 0 | 0 | 30967.9481 | 101.1% | 28420.9481 | 92.79%
8 | 12 | 11 | 31346 | 36831.55 | 39182.5 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 12766.8179 | 407.0148 | 11665 | 0 | 0 | 31362.6321 | 100.1% | 28815.6321 | 91.93%
8 | 12 | 12 | 32786 | 38523.55 | 40982.5 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 13307.0145 | 324.5146 | 11665 | 0 | 0 | 30380.3285 | 92.66% | 27833.3285 | 84.89%
8 | 12 | 13 | 34498 | 40535.15 | 43122.5 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 13562.3315 | 398.1791 | 11665 | 0 | 0 | 28997.3101 | 84.06% | 26450.3101 | 76.67%
8 | 12 | 14 | 37412 | 43959.1 | 46765 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 13041.9527 | 461.7752 | 11665 | 0 | 0 | 25626.5274 | 68.5% | 23079.5274 | 61.69%
8 | 12 | 15 | 40213 | 47250.275 | 50266.25 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 12671.3224 | 523.2137 | 11665 | 0 | 0 | 22516.3355 | 55.99% | 19969.3355 | 49.66%
8 | 12 | 16 | 42688 | 50158.4 | 53360 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 11556.0793 | 690.2073 | 11665 | 0 | 0 | 19093.0861 | 44.73% | 16546.0861 | 38.76%
8 | 12 | 17 | 44147 | 51872.725 | 55183.75 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 10023.1406 | 1221.9074 | 6474.3344 | 5387.1367 | 0 | 16829.3185 | 38.12% | 14282.3185 | 32.35%
8 | 12 | 18 | 45511 | 53475.425 | 56888.75 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 6975.4569 | 1761.354 | 6509 | 8657.8878 | 990.8502 | 17253.3483 | 37.91% | 14706.3483 | 32.31%
8 | 12 | 19 | 45390 | 53333.25 | 56737.5 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 2520.5665 | 2334.4377 | 6509 | 12260.761 | 990.8502 | 17095.4149 | 37.66% | 14548.4149 | 32.05%
8 | 12 | 20 | 43810 | 51476.75 | 54762.5 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 134.6503 | 2594.2466 | 6509 | 12200.4599 | 990.8502 | 16489.0065 | 37.64% | 13942.0065 | 31.82%
8 | 12 | 21 | 41824 | 49143.2 | 52280 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2848.0762 | 6509 | 9410.1362 | 990.8502 | 15803.862 | 37.79% | 13256.862 | 31.7%
8 | 12 | 22 | 39818 | 46786.15 | 49772.5 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 3086.3096 | 6506.2061 | 6487.2746 | 990.8502 | 15122.44 | 37.98% | 12575.44 | 31.58%
8 | 12 | 23 | 36619 | 43027.325 | 45773.75 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2746.4662 | 6447.366 | 3481.7437 | 58 | 13984.3754 | 38.19% | 11437.3754 | 31.23%
8 | 12 | 24 | 33632 | 39517.6 | 42040 | N | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2665.4249 | 11665 | 0 | 0 | 18568.2244 | 55.21% | 16021.2244 | 47.64%
9 | 2 | 1 | 31904 | 37487.2 | 39880 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1207.7087 | 11665 | 0 | 0 | 18691.5188 | 58.59% | 16144.5188 | 50.6%
9 | 2 | 2 | 28847 | 33895.225 | 36058.75 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1179.5168 | 11665 | 0 | 0 | 21720.327 | 75.29% | 19173.327 | 66.47%
9 | 2 | 3 | 27272 | 32044.6 | 34090 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1170.5168 | 11665 | 0 | 0 | 23286.327 | 85.39% | 20739.327 | 76.05%
9 | 2 | 4 | 26279 | 30877.825 | 32848.75 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 962.756 | 11665 | 0 | 0 | 24071.5661 | 91.6% | 21524.5661 | 81.91%
9 | 2 | 5 | 26059 | 30619.325 | 32573.75 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 580.707 | 11665 | 0 | 0 | 23909.5172 | 91.75% | 21362.5172 | 81.98%
9 | 2 | 6 | 27014 | 31741.45 | 33767.5 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 534.022 | 11665 | 0 | 0 | 22907.8321 | 84.8% | 20360.8321 | 75.37%
9 | 2 | 7 | 28829 | 33874.075 | 36036.25 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 158.5948 | 538.3576 | 11665 | 0 | 0 | 21255.7625 | 73.73% | 18708.7625 | 64.9%
9 | 2 | 8 | 30065 | 35326.375 | 37581.25 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 3489.9487 | 526.4117 | 11665 | 0 | 0 | 23339.1705 | 77.63% | 20792.1705 | 69.16%
9 | 2 | 9 | 31045 | 36477.875 | 38806.25 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 8805.2316 | 452.1998 | 11665 | 0 | 0 | 27600.2416 | 88.9% | 25053.2416 | 80.7%
9 | 2 | 10 | 32164 | 37792.7 | 40205 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 11543.7428 | 334.7064 | 11665 | 0 | 0 | 29102.2593 | 90.48% | 26555.2593 | 82.56%
9 | 2 | 11 | 33020 | 38798.5 | 41275 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12652.3511 | 360.453 | 11665 | 0 | 0 | 29380.6143 | 88.98% | 26833.6143 | 81.26%
9 | 2 | 12 | 34225 | 40214.375 | 42781.25 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13197.4375 | 325.1105 | 11665 | 0 | 0 | 28685.3581 | 83.81% | 26138.3581 | 76.37%
9 | 2 | 13 | 36070 | 42382.25 | 45087.5 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13311.6623 | 351.9872 | 11665 | 0 | 0 | 26981.4597 | 74.8% | 24434.4597 | 67.74%
9 | 2 | 14 | 38804 | 45594.7 | 48505 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12859.312 | 506.9397 | 11665 | 0 | 0 | 23950.0618 | 61.72% | 21403.0618 | 55.16%
9 | 2 | 15 | 41613 | 48895.275 | 52016.25 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12424.1951 | 514.9338 | 11665 | 0 | 0 | 20713.9391 | 49.78% | 18166.9391 | 43.66%
9 | 2 | 16 | 45004 | 52879.7 | 56255 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 11773.8157 | 527.5494 | 11665 | 0 | 0 | 16685.1752 | 37.07% | 14138.1752 | 31.42%
9 | 2 | 17 | 46087 | 54152.225 | 57608.75 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 8964.9146 | 644.4709 | 6509 | 6682.9046 | 0 | 14437.1002 | 31.33% | 11890.1002 | 25.8%
9 | 2 | 18 | 46844 | 55041.7 | 58555 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 5520.3037 | 871.2763 | 6509 | 9800.3395 | 970.5018 | 14550.2315 | 31.06% | 12003.2315 | 25.62%
9 | 2 | 19 | 46546 | 54691.55 | 58182.5 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 1172.8306 | 1277.6952 | 6509 | 13207.7744 | 970.5018 | 14314.6122 | 30.75% | 11767.6122 | 25.28%
9 | 2 | 20 | 44877 | 52730.475 | 56096.25 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13.0622 | 1472.3258 | 6509 | 12020.0754 | 970.5018 | 13830.7754 | 30.82% | 11283.7754 | 25.14%
9 | 2 | 21 | 42389 | 49807.075 | 52986.25 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1759.443 | 6509 | 8599.3367 | 970.5018 | 13172.0917 | 31.07% | 10625.0917 | 25.07%
9 | 2 | 22 | 40017 | 47019.975 | 50021.25 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1893.5393 | 6509 | 5466.5412 | 970.5018 | 12545.3924 | 31.35% | 9998.3924 | 24.99%
9 | 2 | 23 | 36609 | 43015.575 | 45761.25 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1783.7719 | 6509 | 2108.4283 | 81 | 11596.0103 | 31.68% | 9049.0103 | 24.72%
9 | 2 | 24 | 33702 | 39599.85 | 42127.5 | N | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1722.1895 | 11665 | 0 | 0 | 17407.9997 | 51.65% | 14860.9997 | 44.1%
5 | 27 | 1 | 25190 | 29598.25 | 31487.5 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 4064.5746 | 11665 | 0 | 0 | 27503.5746 | 109.2% | 24956.5746 | 99.07%
5 | 27 | 2 | 23503 | 27616.025 | 29378.75 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3773.4784 | 11665 | 0 | 0 | 28899.4784 | 123% | 26352.4784 | 112.1%
5 | 27 | 3 | 22463 | 26394.025 | 28078.75 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3512.4239 | 11665 | 0 | 0 | 29678.4239 | 132.1% | 27131.4239 | 120.8%
5 | 27 | 4 | 21857 | 25681.975 | 27321.25 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3135.5164 | 11665 | 0 | 0 | 29907.5164 | 136.8% | 27360.5164 | 125.2%
5 | 27 | 5 | 21889 | 25719.575 | 27361.25 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 2693.374 | 11665 | 0 | 0 | 29433.374 | 134.5% | 26886.374 | 122.8%
5 | 27 | 6 | 22612 | 26569.1 | 28265 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 16.3775 | 2235.6472 | 11665 | 0 | 0 | 28269.0246 | 125% | 25722.0246 | 113.8%
5 | 27 | 7 | 23304 | 27382.2 | 29130 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 1768.7479 | 1853.5831 | 11665 | 0 | 0 | 28947.3311 | 124.2% | 26400.3311 | 113.3%
5 | 27 | 8 | 23834 | 28004.95 | 29792.5 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 7546.6355 | 1203.9964 | 11665 | 0 | 0 | 33545.632 | 140.7% | 30998.632 | 130.1%
5 | 27 | 9 | 27516.383 | 31658.108 | 33433.133 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 11491.3047 | 845.9498 | 11665 | 0 | 0 | 33449.8715 | 121.6% | 30902.8715 | 112.3%
5 | 27 | 10 | 29596.6824 | 33605.7574 | 35323.9324 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 13096.2781 | 756.478 | 11665 | 0 | 0 | 32885.0738 | 111.1% | 30338.0738 | 102.5%
5 | 27 | 11 | 30583.7739 | 34375.1489 | 36000.0239 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 13683.8087 | 712.0705 | 11665 | 0 | 0 | 32441.1053 | 106.1% | 29894.1053 | 97.74%
5 | 27 | 12 | 31042.6123 | 34684.3623 | 36245.1123 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 13934.1096 | 659.1651 | 11665 | 0 | 0 | 32179.6625 | 103.7% | 29632.6625 | 95.46%
5 | 27 | 13 | 31252.5851 | 34880.1601 | 36434.8351 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 14138.5981 | 606.7483 | 11665 | 0 | 0 | 32121.7614 | 102.8% | 29574.7614 | 94.63%
5 | 27 | 14 | 30912.6342 | 34651.5092 | 36253.8842 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 13800.2403 | 799.3612 | 11665 | 0 | 0 | 32315.9674 | 104.5% | 29768.9674 | 96.3%
5 | 27 | 15 | 30622.1062 | 34553.3062 | 36238.1062 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 13701.4228 | 884.1552 | 11665 | 0 | 0 | 32592.4718 | 106.4% | 30045.4718 | 98.12%
5 | 27 | 16 | 29901.0412 | 34138.1412 | 35954.0412 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 13034.4059 | 1321.4303 | 11665 | 0 | 0 | 33083.795 | 110.6% | 30536.795 | 102.1%
5 | 27 | 17 | 26243 | 30835.525 | 32803.75 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 11462.4556 | 2283.1334 | 6509 | 0 | 0 | 30975.589 | 118% | 28428.589 | 108.3%
5 | 27 | 18 | 28610 | 33616.75 | 35762.5 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 9223.8407 | 2958.2984 | 6509 | 2915.4505 | 0 | 29960.5897 | 104.7% | 27413.5897 | 95.82%
5 | 27 | 19 | 30424 | 35748.2 | 38030 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 4412.7256 | 3223.8761 | 6509 | 9071.6894 | 572.5336 | 30329.8247 | 99.69% | 27782.8247 | 91.32%
5 | 27 | 20 | 30978 | 36399.15 | 38722.5 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 452.7183 | 3127.5921 | 6509 | 11725.0129 | 572.5336 | 28372.8569 | 91.59% | 25825.8569 | 83.37%
5 | 27 | 21 | 31029 | 36459.075 | 38786.25 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3608.0147 | 6509 | 11725.0129 | 572.5336 | 28349.5612 | 91.36% | 25802.5612 | 83.16%
5 | 27 | 22 | 29988 | 35235.9 | 37485 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3993.7542 | 6509 | 11246.5669 | 572.5336 | 29297.8547 | 97.7% | 26750.8547 | 89.21%
5 | 27 | 23 | 27939 | 32828.325 | 34923.75 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3967.4677 | 6509 | 7886.6984 | 572.5336 | 27960.6998 | 100.1% | 25413.6998 | 90.96%
5 | 27 | 24 | 26183 | 30765.025 | 32728.75 | Y | 25945 | 2280 | 5968 | 1106 | 1665 | 0 | 3888.5135 | 11665 | 1403.569 | 0 | 27738.0825 | 105.9% | 25191.0825 | 96.21%
6 | 24 | 1 | 30134 | 35407.45 | 37667.5 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 3035.3124 | 11665 | 0 | 0 | 22351.3124 | 74.17% | 19804.3124 | 65.72%
6 | 24 | 2 | 27085 | 31824.875 | 33856.25 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 2426.6115 | 11665 | 0 | 0 | 24791.6115 | 91.53% | 22244.6115 | 82.13%
6 | 24 | 3 | 25545 | 30015.375 | 31931.25 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 1985.5121 | 11665 | 0 | 0 | 25890.5121 | 101.4% | 23343.5121 | 91.38%
6 | 24 | 4 | 24852.1364 | 29172.3614 | 31023.8864 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 1837.5882 | 11665 | 0 | 0 | 26435.4518 | 106.4% | 23888.4518 | 96.12%
6 | 24 | 5 | 24588 | 28890.9 | 30735 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 1407.2298 | 11665 | 0 | 0 | 26269.2298 | 106.8% | 23722.2298 | 96.48%
6 | 24 | 6 | 25165 | 29568.875 | 31456.25 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 31.3069 | 1062.5257 | 11665 | 0 | 0 | 25378.8327 | 100.8% | 22831.8327 | 90.73%
6 | 24 | 7 | 26423.6781 | 30952.3281 | 32893.1781 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 2370.353 | 973.1944 | 11665 | 0 | 0 | 26369.8692 | 99.8% | 23822.8692 | 90.16%
6 | 24 | 8 | 32621.8 | 37374.975 | 39412.05 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 7888.9211 | 745.2964 | 11665 | 0 | 0 | 25462.4176 | 78.05% | 22915.4176 | 70.25%
6 | 24 | 9 | 36339.6825 | 41226.9075 | 43321.4325 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 11246.8501 | 560.2603 | 11665 | 0 | 0 | 24917.4279 | 68.57% | 22370.4279 | 61.56%
6 | 24 | 10 | 38465.8423 | 43360.4173 | 45458.0923 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 13111.1396 | 437.3436 | 11665 | 0 | 0 | 24532.641 | 63.78% | 21985.641 | 57.16%
6 | 24 | 11 | 39501.3545 | 44438.6295 | 46554.6045 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 13861.9848 | 575.8782 | 11665 | 0 | 0 | 24386.5085 | 61.74% | 21839.5085 | 55.29%
6 | 24 | 12 | 39553.9726 | 44596.5976 | 46757.7226 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 14125.1626 | 466.7478 | 11665 | 0 | 0 | 24487.9378 | 61.91% | 21940.9378 | 55.47%
6 | 24 | 13 | 39372.7445 | 44630.6195 | 46883.9945 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 14178.283 | 492.9465 | 11665 | 0 | 0 | 24748.485 | 62.86% | 22201.485 | 56.39%
6 | 24 | 14 | 38510.5918 | 44168.3418 | 46593.0918 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 13765.1508 | 624.9674 | 11665 | 0 | 0 | 25329.5264 | 65.77% | 22782.5264 | 59.16%
6 | 24 | 15 | 37913.1972 | 44034.6972 | 46658.1972 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 13487.6053 | 904.6668 | 11665 | 0 | 0 | 25929.0748 | 68.39% | 23382.0748 | 61.67%
6 | 24 | 16 | 37916 | 44551.3 | 47395 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 12843.9644 | 1412.3668 | 11665 | 0 | 0 | 25790.3312 | 68.02% | 23243.3312 | 61.3%
6 | 24 | 17 | 39318 | 46198.65 | 49147.5 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 11505.9043 | 1972.0738 | 6509 | 2738.266 | 0 | 21192.2441 | 53.9% | 18645.2441 | 47.42%
6 | 24 | 18 | 40950 | 48116.25 | 51187.5 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 9660.2112 | 2653.8564 | 6509 | 5563.7293 | 864.4643 | 22086.2612 | 53.93% | 19539.2612 | 47.71%
6 | 24 | 19 | 41537 | 48805.975 | 51921.25 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 5699.3294 | 2937.8503 | 6509 | 10168.2001 | 864.4643 | 22426.8442 | 53.99% | 19879.8442 | 47.86%
6 | 24 | 20 | 40660 | 47775.5 | 50825 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 1284.6251 | 3437.0845 | 6509 | 12747.9704 | 864.4643 | 21968.1443 | 54.03% | 19421.1443 | 47.76%
6 | 24 | 21 | 39511 | 46425.425 | 49388.75 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 16.6515 | 3747.1949 | 6509 | 11933.6344 | 864.4643 | 21344.9452 | 54.02% | 18797.9452 | 47.58%
6 | 24 | 22 | 37852 | 44476.1 | 47315 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 3992.2504 | 6509 | 9132.7163 | 864.4643 | 20431.431 | 53.98% | 17884.431 | 47.25%
6 | 24 | 23 | 34932 | 41045.1 | 43665 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 4079.2095 | 6509 | 5399.4834 | 0 | 18840.6929 | 53.94% | 16293.6929 | 46.64%
6 | 24 | 24 | 32032 | 37637.6 | 40040 | Y | 25889 | 2280 | 6248 | 1687 | 1681 | 0 | 3940.5311 | 11665 | 0 | 0 | 21358.5311 | 66.68% | 18811.5311 | 58.73%
7 | 22 | 1 | 32217 | 37854.975 | 40271.25 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3487.4066 | 11665 | 0 | 0 | 21416.1987 | 66.47% | 18869.1987 | 58.57%
7 | 22 | 2 | 29943.4484 | 35066.2234 | 37261.6984 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3494.0847 | 11665 | 0 | 0 | 23696.4284 | 79.14% | 21149.4284 | 70.63%
7 | 22 | 3 | 30070.5088 | 34907.6838 | 36980.7588 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3245.0429 | 11665 | 0 | 0 | 23320.3262 | 77.55% | 20773.3262 | 69.08%
7 | 22 | 4 | 30226.5906 | 34894.7156 | 36895.3406 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3161.2893 | 11665 | 0 | 0 | 23080.4908 | 76.36% | 20533.4908 | 67.93%
7 | 22 | 5 | 29679.2241 | 34312.5241 | 36298.2241 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 2687.1748 | 11665 | 0 | 0 | 23153.7428 | 78.01% | 20606.7428 | 69.43%
7 | 22 | 6 | 28898.3811 | 33661.7061 | 35703.1311 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 9.693 | 2227.9374 | 11665 | 0 | 0 | 23485.0414 | 81.27% | 20938.0414 | 72.45%
7 | 22 | 7 | 29558.6573 | 34494.0073 | 36609.1573 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 1179.4654 | 1787.2616 | 11665 | 0 | 0 | 23553.8618 | 79.69% | 21006.8618 | 71.07%
7 | 22 | 8 | 34813.7384 | 40011.4134 | 42238.9884 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 6047.4209 | 1373.4078 | 11665 | 0 | 0 | 22752.8824 | 65.36% | 20205.8824 | 58.04%
7 | 22 | 9 | 39528.1593 | 44896.9843 | 47197.9093 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 10518.9673 | 819.4953 | 11665 | 0 | 0 | 21956.0955 | 55.55% | 19409.0955 | 49.1%
7 | 22 | 10 | 41438.8827 | 46925.1327 | 49276.3827 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 12412.7398 | 572.0769 | 11665 | 0 | 0 | 21691.7261 | 52.35% | 19144.7261 | 46.2%
7 | 22 | 11 | 42254.8254 | 47860.0754 | 50262.3254 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13280.3028 | 491.4671 | 11665 | 0 | 0 | 21662.7365 | 51.27% | 19115.7365 | 45.24%
7 | 22 | 12 | 42096.3389 | 47979.8389 | 50501.3389 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13553.6925 | 432.4532 | 11665 | 0 | 0 | 22035.599 | 52.35% | 19488.599 | 46.3%
7 | 22 | 13 | 41931.9619 | 48072.1869 | 50703.7119 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13566.8411 | 602.8167 | 11665 | 0 | 0 | 22383.488 | 53.38% | 19836.488 | 47.31%
7 | 22 | 14 | 41124.1468 | 47744.9218 | 50582.3968 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13374.8652 | 744.8239 | 11665 | 0 | 0 | 23141.3345 | 56.27% | 20594.3345 | 50.08%
7 | 22 | 15 | 40911 | 48070.425 | 51138.75 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 13031.6723 | 1085.5303 | 11665 | 0 | 0 | 23351.9947 | 57.08% | 20804.9947 | 50.85%
7 | 22 | 16 | 43792 | 51455.6 | 54740 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 12436.428 | 1881.1694 | 11665 | 0 | 0 | 20671.3895 | 47.2% | 18124.3895 | 41.39%
7 | 22 | 17 | 45272 | 53194.6 | 56590 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 11267.4676 | 2639.6783 | 6509 | 5655.93 | 0 | 19280.868 | 42.59% | 16733.868 | 36.96%
7 | 22 | 18 | 46301 | 54403.675 | 57876.25 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 9131.1984 | 3230.6388 | 6509 | 7582.1134 | 1073.3337 | 19706.0764 | 42.56% | 17159.0764 | 37.06%
7 | 22 | 19 | 46016 | 54068.8 | 57520 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 5184.4885 | 3305.8316 | 6509 | 11022.056 | 1073.3337 | 19559.5019 | 42.51% | 17012.5019 | 36.97%
7 | 22 | 20 | 44183 | 51915.025 | 55228.75 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 961.5725 | 3701.9482 | 6509 | 12224.8204 | 1073.3337 | 18768.467 | 42.48% | 16221.467 | 36.71%
7 | 22 | 21 | 42183 | 49565.025 | 52728.75 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 4111.5315 | 6509 | 9931.5509 | 1073.3337 | 17923.2082 | 42.49% | 15376.2082 | 36.45%
7 | 22 | 22 | 40436 | 47512.3 | 50545 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 4274.6562 | 6443.6885 | 7363.2528 | 1073.3337 | 17199.7234 | 42.54% | 14652.7234 | 36.24%
7 | 22 | 23 | 37291 | 43816.925 | 46613.75 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 4136.3535 | 6359.1059 | 4105.6765 | 89 | 15879.928 | 42.58% | 13332.928 | 35.75%
7 | 22 | 24 | 34306 | 40309.55 | 42882.5 | Y | 25823 | 2280 | 6763 | 1915 | 1699.7921 | 0 | 3979.1818 | 11665 | 0 | 0 | 19818.974 | 57.77% | 17271.974 | 50.35%
8 | 12 | 1 | 31805 | 37370.875 | 39756.25 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2839.3252 | 11665 | 0 | 0 | 20569.1247 | 64.67% | 18022.1247 | 56.66%
8 | 12 | 2 | 29555.3225 | 34641.5225 | 36821.3225 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2773.0759 | 11665 | 0 | 0 | 22752.5528 | 76.98% | 20205.5528 | 68.37%
8 | 12 | 3 | 29573.9523 | 34380.6773 | 36440.7023 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2366.9447 | 11665 | 0 | 0 | 22327.7918 | 75.5% | 19780.7918 | 66.89%
8 | 12 | 4 | 29512.4265 | 34141.0015 | 36124.6765 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2053.6904 | 11665 | 0 | 0 | 22076.0633 | 74.8% | 19529.0633 | 66.17%
8 | 12 | 5 | 29135.4079 | 33741.7579 | 35715.9079 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 1742.306 | 11665 | 0 | 0 | 22141.6975 | 76% | 19594.6975 | 67.25%
8 | 12 | 6 | 28597.0721 | 33360.7471 | 35402.3221 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 1580.6421 | 11665 | 0 | 0 | 22518.3694 | 78.74% | 19971.3694 | 69.84%
8 | 12 | 7 | 28524 | 33515.7 | 35655 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 392.0205 | 1207.0512 | 11665 | 0 | 0 | 22609.8712 | 79.27% | 20062.8712 | 70.34%
8 | 12 | 8 | 32592.2073 | 37758.5573 | 39972.7073 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 4245.2737 | 890.6531 | 11665 | 0 | 0 | 22078.519 | 67.74% | 19531.519 | 59.93%
8 | 12 | 9 | 38386.7709 | 43665.4709 | 45927.7709 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 9007.9026 | 569.0563 | 11665 | 0 | 0 | 20724.9875 | 53.99% | 18177.9875 | 47.35%
8 | 12 | 10 | 41592.7204 | 46952.9704 | 49250.2204 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 11527.1041 | 536.0445 | 11665 | 0 | 0 | 20005.2277 | 48.1% | 17458.2277 | 41.97%
8 | 12 | 11 | 42844.0237 | 48329.5737 | 50680.5237 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 12766.8179 | 407.0148 | 11665 | 0 | 0 | 19864.6084 | 46.36% | 17317.6084 | 40.42%
8 | 12 | 12 | 42951.7418 | 48689.2918 | 51148.2418 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 13307.0145 | 324.5146 | 11665 | 0 | 0 | 20214.5867 | 47.06% | 17667.5867 | 41.13%
8 | 12 | 13 | 42787.9771 | 48825.1271 | 51412.4771 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 13562.3315 | 398.1791 | 11665 | 0 | 0 | 20707.333 | 48.4% | 18160.333 | 42.44%
8 | 12 | 14 | 41130.241 | 47677.341 | 50483.241 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 13041.9527 | 461.7752 | 11665 | 0 | 0 | 21908.2864 | 53.27% | 19361.2864 | 47.07%
8 | 12 | 15 | 40213 | 47250.275 | 50266.25 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 12671.3224 | 523.2137 | 11665 | 0 | 0 | 22516.3355 | 55.99% | 19969.3355 | 49.66%
8 | 12 | 16 | 42688 | 50158.4 | 53360 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 11556.0793 | 690.2073 | 11665 | 0 | 0 | 19093.0861 | 44.73% | 16546.0861 | 38.76%
8 | 12 | 17 | 44147 | 51872.725 | 55183.75 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 10023.1406 | 1221.9074 | 6474.3344 | 5387.1367 | 0 | 16829.3185 | 38.12% | 14282.3185 | 32.35%
8 | 12 | 18 | 45511 | 53475.425 | 56888.75 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 6975.4569 | 1761.354 | 6509 | 8657.8878 | 990.8502 | 17253.3483 | 37.91% | 14706.3483 | 32.31%
8 | 12 | 19 | 45390 | 53333.25 | 56737.5 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 2520.5665 | 2334.4377 | 6509 | 12260.761 | 990.8502 | 17095.4149 | 37.66% | 14548.4149 | 32.05%
8 | 12 | 20 | 43810 | 51476.75 | 54762.5 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 134.6503 | 2594.2466 | 6509 | 12200.4599 | 990.8502 | 16489.0065 | 37.64% | 13942.0065 | 31.82%
8 | 12 | 21 | 41824 | 49143.2 | 52280 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2848.0762 | 6509 | 9410.1362 | 990.8502 | 15803.862 | 37.79% | 13256.862 | 31.7%
8 | 12 | 22 | 39818 | 46786.15 | 49772.5 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 3086.3096 | 6506.2061 | 6487.2746 | 990.8502 | 15122.44 | 37.98% | 12575.44 | 31.58%
8 | 12 | 23 | 36619 | 43027.325 | 45773.75 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2746.4662 | 6447.366 | 3481.7437 | 58 | 13984.3754 | 38.19% | 11437.3754 | 31.23%
8 | 12 | 24 | 33632 | 39517.6 | 42040 | Y | 25862 | 2280 | 6635 | 1392 | 1700.7994 | 0 | 2665.4249 | 11665 | 0 | 0 | 18568.2244 | 55.21% | 16021.2244 | 47.64%
9 | 2 | 1 | 31904 | 37487.2 | 39880 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1207.7087 | 11665 | 0 | 0 | 18691.5188 | 58.59% | 16144.5188 | 50.6%
9 | 2 | 2 | 29621.419 | 34669.644 | 36833.169 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1179.5168 | 11665 | 0 | 0 | 20945.908 | 70.71% | 18398.908 | 62.11%
9 | 2 | 3 | 30038.5282 | 34811.1282 | 36856.5282 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1170.5168 | 11665 | 0 | 0 | 20519.7987 | 68.31% | 17972.7987 | 59.83%
9 | 2 | 4 | 30044.8924 | 34643.7174 | 36614.6424 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 962.756 | 11665 | 0 | 0 | 20305.6738 | 67.58% | 17758.6738 | 59.11%
9 | 2 | 5 | 29619.5508 | 34179.8758 | 36134.3008 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 580.707 | 11665 | 0 | 0 | 20348.9663 | 68.7% | 17801.9663 | 60.1%
9 | 2 | 6 | 29303.2067 | 34030.6567 | 36056.7067 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 534.022 | 11665 | 0 | 0 | 20618.6254 | 70.36% | 18071.6254 | 61.67%
9 | 2 | 7 | 29007.7029 | 34052.7779 | 36214.9529 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 158.5948 | 538.3576 | 11665 | 0 | 0 | 21077.0596 | 72.66% | 18530.0596 | 63.88%
9 | 2 | 8 | 32893.5977 | 38154.9727 | 40409.8477 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 3489.9487 | 526.4117 | 11665 | 0 | 0 | 20510.5727 | 62.35% | 17963.5727 | 54.61%
9 | 2 | 9 | 39293.271 | 44726.146 | 47054.521 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 8805.2316 | 452.1998 | 11665 | 0 | 0 | 19351.9706 | 49.25% | 16804.9706 | 42.77%
9 | 2 | 10 | 42322.6933 | 47951.3933 | 50363.6933 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 11543.7428 | 334.7064 | 11665 | 0 | 0 | 18943.566 | 44.76% | 16396.566 | 38.74%
9 | 2 | 11 | 43532.734 | 49311.234 | 51787.734 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12652.3511 | 360.453 | 11665 | 0 | 0 | 18867.8802 | 43.34% | 16320.8802 | 37.49%
9 | 2 | 12 | 43853.4349 | 49842.8099 | 52409.6849 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13197.4375 | 325.1105 | 11665 | 0 | 0 | 19056.9232 | 43.46% | 16509.9232 | 37.65%
9 | 2 | 13 | 43531.2398 | 49843.4898 | 52548.7398 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13311.6623 | 351.9872 | 11665 | 0 | 0 | 19520.2199 | 44.84% | 16973.2199 | 38.99%
9 | 2 | 14 | 42409.5929 | 49200.2929 | 52110.5929 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12859.312 | 506.9397 | 11665 | 0 | 0 | 20344.469 | 47.97% | 17797.469 | 41.97%
9 | 2 | 15 | 41613 | 48895.275 | 52016.25 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12424.1951 | 514.9338 | 11665 | 0 | 0 | 20713.9391 | 49.78% | 18166.9391 | 43.66%
9 | 2 | 16 | 45004 | 52879.7 | 56255 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 11773.8157 | 527.5494 | 11665 | 0 | 0 | 16685.1752 | 37.07% | 14138.1752 | 31.42%
9 | 2 | 17 | 46087 | 54152.225 | 57608.75 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 8964.9146 | 644.4709 | 6509 | 6682.9046 | 0 | 14437.1002 | 31.33% | 11890.1002 | 25.8%
9 | 2 | 18 | 46844 | 55041.7 | 58555 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 5520.3037 | 871.2763 | 6509 | 9800.3395 | 970.5018 | 14550.2315 | 31.06% | 12003.2315 | 25.62%
9 | 2 | 19 | 46546 | 54691.55 | 58182.5 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 1172.8306 | 1277.6952 | 6509 | 13207.7744 | 970.5018 | 14314.6122 | 30.75% | 11767.6122 | 25.28%
9 | 2 | 20 | 44877 | 52730.475 | 56096.25 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13.0622 | 1472.3258 | 6509 | 12020.0754 | 970.5018 | 13830.7754 | 30.82% | 11283.7754 | 25.14%
9 | 2 | 21 | 42389 | 49807.075 | 52986.25 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1759.443 | 6509 | 8599.3367 | 970.5018 | 13172.0917 | 31.07% | 10625.0917 | 25.07%
9 | 2 | 22 | 40017 | 47019.975 | 50021.25 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1893.5393 | 6509 | 5466.5412 | 970.5018 | 12545.3924 | 31.35% | 9998.3924 | 24.99%
9 | 2 | 23 | 36609 | 43015.575 | 45761.25 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1783.7719 | 6509 | 2108.4283 | 81 | 11596.0103 | 31.68% | 9049.0103 | 24.72%
9 | 2 | 24 | 33702 | 39599.85 | 42127.5 | Y | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1722.1895 | 11665 | 0 | 0 | 17407.9997 | 51.65% | 14860.9997 | 44.1%

## Sheet3 (hidden)
MONTH | 9
Charging Load (Y/N) | N
Row Labels | Natural Gas | Nuclear | Hydro | Other | Other Renewables | Solar | Wind | Imports | Battery Storage | Demand Response | Sum of 2025 IEPR Forecast | Sum of Forecast + 17.5% PRM | Sum of Forecast + 25.0% PRM
1 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1207.7087 | 11665 | 0 | 0 | 31904 | 37487.2 | 39880
2 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1179.5168 | 11665 | 0 | 0 | 28847 | 33895.225 | 36058.75
3 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1170.5168 | 11665 | 0 | 0 | 27272 | 32044.6 | 34090
4 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 962.756 | 11665 | 0 | 0 | 26279 | 30877.825 | 32848.75
5 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 580.707 | 11665 | 0 | 0 | 26059 | 30619.325 | 32573.75
6 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 534.022 | 11665 | 0 | 0 | 27014 | 31741.45 | 33767.5
7 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 158.5948 | 538.3576 | 11665 | 0 | 0 | 28829 | 33874.075 | 36036.25
8 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 3489.9487 | 526.4117 | 11665 | 0 | 0 | 30065 | 35326.375 | 37581.25
9 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 8805.2316 | 452.1998 | 11665 | 0 | 0 | 31045 | 36477.875 | 38806.25
10 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 11543.7428 | 334.7064 | 11665 | 0 | 0 | 32164 | 37792.7 | 40205
11 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12652.3511 | 360.453 | 11665 | 0 | 0 | 33020 | 38798.5 | 41275
12 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13197.4375 | 325.1105 | 11665 | 0 | 0 | 34225 | 40214.375 | 42781.25
13 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13311.6623 | 351.9872 | 11665 | 0 | 0 | 36070 | 42382.25 | 45087.5
14 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12859.312 | 506.9397 | 11665 | 0 | 0 | 38804 | 45594.7 | 48505
15 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 12424.1951 | 514.9338 | 11665 | 0 | 0 | 41613 | 48895.275 | 52016.25
16 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 11773.8157 | 527.5494 | 11665 | 0 | 0 | 45004 | 52879.7 | 56255
17 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 8964.9146 | 644.4709 | 6509 | 6682.9046 | 0 | 46087 | 54152.225 | 57608.75
18 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 5520.3037 | 871.2763 | 6509 | 9800.3395 | 970.5018 | 46844 | 55041.7 | 58555
19 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 1172.8306 | 1277.6952 | 6509 | 13207.7744 | 970.5018 | 46546 | 54691.55 | 58182.5
20 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 13.0622 | 1472.3258 | 6509 | 12020.0754 | 970.5018 | 44877 | 52730.475 | 56096.25
21 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1759.443 | 6509 | 8599.3367 | 970.5018 | 42389 | 49807.075 | 52986.25
22 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1893.5393 | 6509 | 5466.5412 | 970.5018 | 40017 | 47019.975 | 50021.25
23 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1783.7719 | 6509 | 2108.4283 | 81 | 36609 | 43015.575 | 45761.25
24 | 25901 | 2280 | 6180 | 1660 | 1701.8101 | 0 | 1722.1895 | 11665 | 0 | 0 | 33702 | 39599.85 | 42127.5
Grand Total | 621624 | 54720 | 148320 | 39840 | 40843.4433 | 115887.4027 | 21498.5883 | 243868 | 57885.4 | 4933.5092 | 855285 | 1004959.875 | 1069106.25