## PGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Trigger Year | Current Expected Construction Start | Expected CPUC Permit Application | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service Jul 2022 TDF | Expected In-Service Oct 2022 TDF | Expected In-Service Jan 2023 TDF | Expected In-Service Apr 2023 TDF | Expected In-Service Jul 2023 TDF | Expected In-Service Oct 2023 TDF | Expected In-Service Jan 2024 TDF | Expected In-Service July 2024 TDF (Current) | Agregate MW in Queue with Executed LGIA | Notes
C9P2-F17 | Panoche 115 kV circuit breakers 152 overstress | Replace Panoche 115 kV circuit breaker 152 and associated switches/relays | PG&E | C9 | Reliability | SCD overstress | Removed | [14 empty] | In-Service
Impact to C14 | Morro Bay MPAC | New 230kV MPAC building relocates 230kV equipment from existing Control Building | PG&E | n/a | Capacity | MPAC | Removed | 2014 | 46885 |  |  | n/a | n/a | 46455 | 2027-05-06 | 2027-05-06 | 2028-05-30 | 2029-05-25 | 2029-05-25 | 2024-03-01 |  | Q3-2024 - Removed. NO triggers.
20rsmt-3 | Midway 230 kV Bus Section E overload mitigation | Replace limiting conductor and/or fittings on Bus Section E to achieve 3372 A min. rating | PG&E | RA-20 | Reliability | Bus Flow | In-Service | 2021 |  |  | 44834 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 |  |  | 509.7 | In-Service
20rsmt-7a | Tesla 500 kV circuit breaker 632 overstress | Replace Tesla 500 kV circuit breaker 632 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Service | 2021 | 44533 |  | 44533 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 1110 | In-Service
21rsmt-4 | Monta Vista 115 kV circuit breaker 1322 overstress | Replace Monta Vista 115 kV circuit breaker 1322 | PG&E | RA-21 | TPP | SCD overstress | In-Service | 2021 | 44470 |  | 44500 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 1200 | In-Service
22rsmt-3 | Metcalf 230 kV Substation Circuit Breaker #No 292 Upgrade | Upgrade Metcalf Circuit Breaker #292 due to overstress issues | PG&E | RA-22 | TPP-Approved | (blank) | In-Service | 2022 |  |  |  | 45658 | 45992 | 44831 | 2022-09-27 | 2022-09-27 | 2022-09-27 | 2022-09-27 |  |  | 0 | In-Service
C11P2-FC01 | Midway 500kV CB's 722 Overstress | Midway Sub: Replace 500kV CB's 722, SW's and Relays | PG&E | C11 | Reliability | SCD overstress | In-Service | 2021 | 44834 |  | 46022 | 2025-12-31 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2100.1 | In-Service
C11P2-FP01 | Midway 500 kV circuit breakers 732, 802, 832 and 842 overstress | Replace Midway 500 kV circuit breakers 732, 802, 832 and 842 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Service | 2021 | 44926 |  | 44834 | 2025-12-31 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2100.1 | In-Service
C11P2-NC01 | Tesla Substation 230 kV bus section D and circuit breakers 372, 382 and 842 overstress (reactors) TESLA: 230KV BUS REACTORS C - D | Increase Tesla Substation 230 kV series bus reactors between bus section C and D and D and E | PG&E | C11 | Reliability | SCD overstress | In-Service | 2019 | 45092 | N/A | 45230 | 2023-10-27 | 2023-09-28 | 2023-11-29 | 2023-12-19 | 2024-03-29 | 2024-03-29 | 2024-03-29 | 2024-04-18 | 2024-03-25 | 1850.3 | Q3-2024 - In-Service March 2024
C11P2-NC01 | Tesla Substation 230 kV bus section D and circuit breakers 372, 382 and 842 overstress (reactors) TESLA: 230KV BUS REACTORS D - E | Increase Tesla Substation 230 kV series bus reactors between bus section C and D and D and E | PG&E | C11 | TPP-Approved | SCD overstress | In-Service | 2019 | 2022-04-19 | N/A | 2023-10-31 | 2023-04-05 | 2023-03-28 | 2023-05-01 | 2023-06-13 | 2023-07-27 | 2023-06-14 | 2023-06-14 | 2023-06-14 | 2023-06-14 | 1850.3 | In-Service
C12P1-NPN02 | Lodi Substation 60 kV circuit breakers 12 and 22 overstress | (blank) | PG&E | C12 | TPP | SCD overstress | In-Service | 2011 | 44047 |  | 44648 | 2022-12-29 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 0 | In-Service
C12P2-GRNU3 | Midway Substation 500 kV CB 712 overstress | Replace Midway Substation 500 kV CB 712 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Service | 2021 | 44926 |  | 46022 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 1800 | In-Service
C12P2-KC01 | Midway Substation 500kV CB 722 Overload mitigation | Replace Midway 500 kV CB 722 to achieve 3600 A emergency rating | PG&E | C12 | Reliability | Bus Flow | In-Service | 2021 | 2022-12-31 |  | 2025-12-31 | 2025-12-31 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 3374.8 | In-Service
C12P2-PNU-02 | Gates 230 kV circuit breakers 352, 362 and 372 overstress mitigation (Cap Banks) | Replace Gates 230 kV circuit breakers 352, 362 and 372 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Service | 2022 | 44858 |  | 45046 | 2023-03-31 | 2023-03-31 | 2023-04-06 | 2023-04-06 | 2023-05-23 | 2023-07-14 | 2023-07-12 | 2023-07-12 | 2023-07-12 | 3439.7 | In-Service
C13P1-FPT02 | Warnerville-Bellota 230 kV line reconductoring | The project proposes to reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations with 1113 kcmil steel-supported aluminum conductors with emergency capability of 1890 Amps. The project includes the installation of a new Optical Ground Wire (OPGW) that will replace the existing aging third-party owned OPGW. The project will upgrade the Bellota, Cottle, and Warnerville terminals and upgrade the line fault protection to current safety standards. The project includes replacing a manual bypass switch and installing an additional shield wire. Key construction elements are as follows: • Replace 148 steel electric transmission lattice towers with 148 new tubular steel poles (TSP’s) • Replace 1 manual bypass switch • Replace 22.5 miles of the Bellota-Warnerville 230 kV circuit • Replace 19.9 miles of the Bellota-Cottle 230 kV circuit • Replace 2.5 miles of the Cottle-Melones 230 kV circuit • Replace 0.1 mile of the Warnerville-Wilson 230 kV circuit • Replace 22.5 miles of OPGW with new OPGW • Install 22.5 miles of shield wire • Upgrade transmission line terminals at Bellota, Cottle, and Warnerville substations | PG&E | C13 | Deliverability | Re-conductor | In-Service | 2013 | 44713 | NOC: AL 6047-E | 45653 | 45412 | 45412 | 45412 | 2024-04-30 | 2024-04-30 | 2024-04-30 | 2024-05-31 | 2024-04-30 | 2024-03-31 | 32 | Q3-2024 - In-service as of March 2024.
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | PG&E | C13 | Reliability | SCD overstress | In-Service | 2018 | 44844 |  | 45808 | 44832 | 44896 | 44902 | 44866 | 44866 | 44866 | 44866 | 44866 | 44866 | 2093 | In-Service
C13P2-GGR01 | Tesla 500 kV circuit breakers 622 overstress | Replace Tesla 500 kV circuit breaker 622 with 63 kA interrupting capability. Only went to 50 kA | PG&E | C13 | Reliability | SCD overstress | In-Service | 2021 | [7 empty] | 2021-12-20 | 2021-12-20 | 2021-12-20 | 2021-12-20 | 2021-12-20 | 600 | In-Service
C13P2-SPN01 | Midway Substation 500 kV Control Building | Existing PG&E project to replace the 500 kV Control Building at Midway (Needed for Midway RAS) | PG&E | C13 | Reliability | RAS (Reliability) | In-Service | 2024 | 44621 | [10 empty] | 2023-03-15 | 100 | In-Service
C8P1-35 | Re-conductor Los Banos-Quinto SS 230 kV Line | Re-conductor 6.11 mi Quinto Sw Sta-Los Banos 230 kV Line with super bundled 795 ACSS | PG&E | C8 | Deliverability | Re-conductor | In-Service | 2017 | 44623 |  | 44712 | 45062 | 45062 | 45062 | 2023-04-28 | 2023-05-10 | 2023-05-08 | 2023-05-08 | 2023-05-08 | 2023-05-08 | 1680 | In-Service
C8P2-6 | Re-conductor Los Banos-Q779 SS #1 230 kV Line | Re-conductor 4.5 mi Los Banos-Padre Flat SS #1 230 kV Line with 1113 ACSS and upgrade equipment to 1900 A. | PG&E | C8 | Deliverability | Re-conductor | In-Service | 2017 | 44858 |  | 44986 | 44985 | 44985 | 44909 | 2022-12-24 | 2022-12-24 | 2022-12-24 | 2022-12-24 | 2022-12-24 | 2022-12-24 | 1052 | In-Service
C9P2-F13-F15 | Gates 230kV Bus Section E and CB 312, 322, 2102, 2202 overload mitigation (BAAH) | Gates Substation 230 kV circuit breakers 312, 322, 2102, 2202 overload – convert bus section E to BAAH and move Panoche-Gates #1 and #2 230 kV lines and Q1117/Q1120/Q1139/Q1242/Q1243 into bus section E | PG&E | C9 | Reliability | Bus Flow | In-Service | 2019 | 44414 |  | 45016 | 44999 | 45077 | 44999 | 2023-05-23 | 2023-05-31 | 2023-04-17 | 2023-04-17 | 2023-04-17 | 2023-04-17 | 2731.6 | In-Service
C9P2-N09 | Re-conductor Stockton A-Weber #3 60 kV Line (Stockton A-Hazelton Jct) | Re-conductor 0.9 mi of Stockton A-Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC. | PG&E | C9 | Reliability | Re-conductor | In-Service | 2018 | 44575 |  | 44651 | 44620 | 44620 | 44620 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 25 | In-Service
19rsmt-3 | Schindler 70kV Bus Normal & Outage Overload | Upgrade Schindler 70 kV Bus to 1113 kcmil AAC | PG&E | RA-19 | Reliability | Bus Flow | Not Triggered | [13 empty] | 0 | Q3-2024 - no generation triggers
20rsmt-4 | Metcalf 115kV breakers Overstress (almost all breakers), install bus reactors on 230kV banks due to existing space constraints on the 115kV Bus | Install 4-3 ohm reactors at low side of Metcalf 115 kV 230kV Transformers | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 46321 |  | 45716 | 45891 | 45903 | 45965 | 46051 | 46058 | 46213 | 46486 | 46450 | 47483 | 1025 | Q3-2024 - Finalizing scoping in late Q3 2024. Analysis of Transient Recovery Voltages and Reactor Electro Magnetic Transient models on the 230kV and 115kV Networks are in process as required for ordering Circuit Breakers. The materials will be ordered approximately Q4 2024. Long Lead Material Received date is approximately in 2027. In-service date estimated to be delayed to Dec 2029.
20rsmt-5 | Tesla 500 kV circuit breaker 612 overstress | Replace Tesla Substation 500 kV CB 612 and associated switches/relays | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 45719 |  | 45352 | 45440 | 45478 | 45512 | 45519 | 45593 | 45838 | 45706 | 46111 | 45961 | 1110 | Q3-2024 - Material delays and subsequent construction sequencing have prolonged the project schedule. Existing Generator impact.
20rsmt-6 | 20RSMTRAS-02 (Reliability) to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | 20RSMTRAS-02 RAS to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | PG&E | RA-20 | Reliability | RAS (Reliability) | In-Flight | 2020 | 46028 |  | 45291 | 45289 | 45289 | 45230 | 45291 | 45610 | 45610 | 45785 | 45841 | 46205 | 0 | Q3-2024 - ISD moved out. Project install depends on Midway 230kV MPAC building project on critical path.
20rsmt-7b | Tesla 500 kV circuit breakers 542 and 642 overstress | Replace Tesla 500 kV circuit breakers 542 and 642 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 45597 |  | 45504 | 45189 | 45394 | 45478 | 45485 | 45559 | 45616 | 45415 | 45838 | 45874 | 2598 | Q3-2024 - Material delays and subsequent construction sequencing have prolonged the project schedule. Existing Generator impact.
21rsmt-1 | Henrietta Substation 70kV CBs 12 and 72 Overstress | Henrietta Sub: Replace 70kV CB 12 & 72 and switches. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 46037 |  | 46022 | 46189 | 45714 | 46279 | 46302 | 46302 | 46302 | 46302 | 46302 | 46714 | 0 | Q3-2024 - not currently triggered by a generation project. The project was previously on hold and has resumed scoping in 2024 and will perform design in 2025.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 1 - incl CB282) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 44386 |  | 46081 | 45265 | 45265 | 45996 | 45996 | 45996 | 45996 | 45717 | 45604 | 45747 | 0 | Q3-2024 - CB 282 (Phase 1 Mar 2025), CB 262 (Phase 3 Dec 2026), CB 182 (Phase 4 Feb 2026). Dates based on preliminary clearance sequencing.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 3 - incl CB262) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 46030 |  | 46081 | 45581 | 45581 | 46363 | 46363 | 46363 | 46363 | 46357 | 46360 | 46387 | 0 | Q3-2024 - CB 282 (Phase 1 Mar 2025), CB 262 (Phase 3 Dec 2026), CB 182 (Phase 4 Feb 2026). Dates based on preliminary clearance sequencing.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 4 - incl CB182) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 46692 |  | 46081 | 44958 | 45027 | 45608 | 45608 | 45608 | 45608 | 46784 | 46734 | 46081 | 0 | Q3-2024 - CB 282 (Phase 1 Mar 2025), CB 262 (Phase 3 Dec 2026), CB 182 (Phase 4 Feb 2026). Dates based on preliminary clearance sequencing.
21rsmt-5 | Palo Alto 115 kV circuit breakers 412 and 442 overstress | Replace Palo Alto 115 kV circuit breakers 412 and 442 with 63 kA interrupting capability | PG&E | RA-21 | TPP | SCD overstress | In-Flight | 2021 | 47214 |  | 45565 | 45743 | 46183 | 46699 | 46699 | 46699 | 46699 | 47206 | 47409 | 48129 | 250 | Q3-2024 - Project re-kicked off in 2024 to mitigate Generation delays. Material lead times on critical path
21rsmt-SCD-23 | El Cerrito G 115kV CB 112, 142, 132 Overstress | Replace Overstressed Circuit Breakers | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2011 | 45303 |  |  | 45491 | 45490 | 45975 | 46017 | 46017 | 46017 | 45778 | 45778 | 45784 | 0 | Q3-2024 - no date changes at this time.
22rsmt-2 | Cottonwood 60 kV many CB overstress upgrade | Replace Cottonwood 60 kV circuit breakers 22, 32, 42, 52, 62, 82 | PG&E | RA-22 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
22rsmt-4 | New 230 kV switching station to loop Dos Amigos – Panoche # 3 230 kV | Build a new 2 bay 230 kV BAAH switching station to loop in the Dos Amigos – Panoche # 3 230 kV Line requiring access road, land and land rights acquisition and permitting, remote end protection upgrades, and OPGW/fiber telecommunication work | PG&E | RA-22 | Deliverability | New Station | Initiating |  | 47232 |  |  | n/a | n/a | 47118 | 47118 | 47118 | 47118 | 47088 | 47088 | 47389 | 752 | Q3-2024 - Project is in planning and scoping and has yet to move into permitting.
C11P2-GP01 | Moraga-Castro Valley 230 kV Line Capacity Increase Project | The project scope of work involves upgrading the limiting substation equipment (jumper conductors and wave traps) on the Moraga-Castro Valley and Castro Valley-Newark 230 kV lines to utilize their full conductor ratings. | PG&E | C11 | Deliverability | Re-conductor | In-Flight | 2011 | 45478 | TBD | 45191 | 45236 | 45358 | 45371 | 45463 | 45590 | 45581 | 46106 | 46106 | 45620 | 290.8 | Q3-2024 - Design complete. Starting construction Sept. 2024
C11P2-ND01 | Re-conductor Fulton-Hopland 60 kV Line (Fitch Mountain Tap-Geysers Jct) | Re-conductor Fulton-Hopland 60 kV Line (Fitch Mountain Tap 009/005A-Geysers Jct 016/004) ~7 mi total length with 715 AAC | PG&E | C11 | Deliverability | Re-conductor | In-Flight | 2018 | 46428 | 45552 | 46112 | 46752 | 46752 | 45964 | 46066 | 46167 | 46178 | 46114 | 46104 | 46477 |  | Q3-2024 - Prioritization of this project and construction sequencing impacts due to other projects in the area. The project remains sensitive to clearance constraints and construction resource dependencies in event of severe weather and fire mitigation / response.
C11P2-ND03 | North Dublin-Cayetano 230 kV Line | Reconductor North Dublin-Cayetano 230 kV Line 2.63 miles OH Line & 2.82 UG cable with new UG cable 797 MVA/2000 A | PG&E | C11 | Deliverability | Re-conductor | In-Flight | 2021 | 45609 |  | 46022 | 46022 | 46022 | 45741 | 45741 | 45698 | 45740 | 45741 | 45677 | 45736 | 290.8 | Q3-2024 - Project is on track to finalize construction seqencing summer of 2024. There are sequencing complications with related impacting Generation and Network Upgrade projects.
C11P2-NP01 | Contra Costa 230kV SW's 601, 603 overload. Replaced by Line relocation project | Contra Costa PP: Replace 230kV SW's 601 & 603 and jumpers. | PG&E | C11 | Reliability | Bus Flow | Replaced | 2021 | 45649 |  | 46022 | 46022 | 45845 | 45779 | 45807 | 45800 | 45799 | 45800 | 45800 | 45799 | 200 | Q3-2024 - See C11P2-NP02, C11P2-NP01 Line Reconfiguration notes
C11P2-NP02 | Contra Costa 230kV Bus Sections D, E and F and circuit breaker 820 overload. Replaced by Line relocation project | Contra Costa PP: Reconductor Bus Sections D, E and F. Replace circuit breaker 820. | PG&E | C11 | Reliability | Bus Flow | Replaced | 2021 | 45649 |  | 46022 | 46022 | 45845 | 45779 | 45807 | 45800 | 45799 | 45800 | 45800 | 45799 | 690.8 | Q3-2024 - See C11P2-NP02, C11P2-NP01 Line Reconfiguration notes
C11P2-NP02, C11P2-NP01 | Contra Costa PP 230 kV Line Terminals Reconfiguration Project | Swap the Lone Tree line and Birds Landing Sw Sta. line between Sec 2D and Sec 2E and Move the Wind Master (Delta) line to section 2E. Replaces the need for: Contra Costa 230kV Bus Sections D, E and F and circuit breaker 820 overload Contra Costa 230kV SW's 601, 603 overload | PG&E | C11 | Reliability | Bus Flow | In-Flight | 2022 | 45435 | N/A | 46022 | 46022 | 45845 | 45692 | 45807 | 45800 | 45799 | 45800 | 45800 | 45799 |  | Q3-2024 - Project is on track to finalize construction seqencing summer of 2025. There are sequencing complications with related impacting Generation and Network Upgrade projects.
C11P2-NR01 | Cottonwood Substation 230 kV circuit breakers 222, 232, 242 overstress | Replace Cottonwood Substation 230 kV circuit breakers 222, 232, 242 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Flight | 2022 | 46084 |  | 45350 | 45384 | 45436 | 45897 | 45897 | 45723 | 45799 | 46412 | 46191 | 46624 | 500 | Q3-2024 - Design completion planned Q1 2025. Long lead material on critical path.
C12P1-GCR01 | Moraga 115 kV circuit breakers 582, 612, 622, 642 and 712 overstress | Replace Moraga 115 kV circuit breakers 582, 612, 622, 642 and 712 | PG&E | C12 | TPP | SCD overstress | In-Flight | 2022 | 45722 |  | 46296 | 46388 | 47080 | 47401 | 47080 | 47080 | 47080 | 47080 | 45340 | 46359 | 200 | Q3-2024 - CB 582 in-service Jan 2023. CB 612 and CB 622 ISD being replaced under emergency with planned ISD Feb 2024. The remaining two breakers CB 642 and CB 712 design is complete and materials onsite. No active generation triggering this project.
C12P1-GPT01 | Ames Distribution 115 kV circuit breaker 132 overstress | Replace Ames Distribution 115 kV circuit breaker 132 | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2019 | 46896 |  | 45382 | 45457 | 45526 | 46091 | 46091 | 46091 | 46091 | 46836 | 46836 | 47703 | 450 | Q3-2024 - Project is in scoping. Long lead material driving schedule.
C12P1-NPT01 | Gold Hill Substation 115 kV circuit breakers 142 and 172 overstress | Replace Gold Hill Substation 115 kV circuit breakers 142 and 172 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2021 | 45352 |  | 45199 | 45295 | 45243 | 45840 | 45897 | 45685 | 45658 | 45658 | 45617 | 45657 | 49.9 | Q3-2024 - On track to go in-service by the end of 2024. Impact to generation has been on a suspended project which is still in the planning stages.
C12P1-NPT03 | Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 overstress | Replace Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2020 | 44348 |  | 45657 | 45657 | 45240 | 45413 | 45657 | 45565 | 45565 | 45657 | 45656 | 45798 | 49.9 | Q3-2024 - Breakers will be energized at the end of the year but line relocations will be incomplete through May/June 2025. Beakers not in use until May 2025
C12P1-NPT04 | Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 overstress | Replace Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2021 | 45602 |  | 45382 | 45470 | 45628 | 45722 | 45797 | 45883 | 45946 | 45946 | 46547 | 46331 | 1740.8 | Q3-2024 - Long lead material on critical path. Breakers received and construction sequencing remains the main driver of the project schedule.
C12P2-GRNU2 | Gates Substation 230 kV Bus Overstress (Reactors on Bus E and F) | Install series bus reactors between Gates Substation 230 kV bus sections E and F | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2022 |  |  | 45992 | 45992 | 46022 | 45747 | 45747 | 45747 | 45443 |  | 46142 | 46139 | 3450 | Q3-2024 - Material delays drove the construction start delays and clearances drives change to ISD
C12P2-LDNU1 | Ripon-Manteca 115 kV Line Reconductor | Reconductor Ripon-Manteca 115 kV line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total) | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 46266 | 45819 | 46752 | 46737 | 46737 | 46737 | 46737 | 47007 | 46496 | 46517 | 46517 | 46681 | 99 | Q3-2024 - 30% design due in June 2024
C12P2-LDNU2 | Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line Reconductor | Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV line 25.23 miles section of various conductors from 018/115-043/277 | PG&E | C12 | TPP | Re-conductor | In-Flight | 2021 | 46436 | 45986 | 46752 | 46737 | 46737 | 46737 | 46737 | 47007 | 46812 | 47001 | 47001 | 47245 | 99 | Q3-2024 - 30% design due in June 2024
C12P2-LDNU3 | Bellota-Riverbank-Melones Sw Sta 115 kV Line 115 kV Line Reconductor | Reconductor a total of 17 miles of Bellota-Riverbank-Melones SW STA 115 kV Line with 477 ACSS | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 46708 | 45741 | 46752 | 46737 | 46752 | 46752 | 46752 | 47007 | 46855 | 46983 | 46983 | 47065 | 99 | Q3-2024 - Scope approval planned in Dec 2024.
C12P2-LDNU4 | Stanislaus-Melones SW STA-Riverbank Jct Sw Sta 115 kV Line Reconductor | Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/043 - scope taken over by the more comprehensive STAN-MELONES TAP LINES: REPL CU COND P3 project. | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 46876 |  | 46752 | 46737 | 46737 | 46737 | 46737 | 47007 | 46902 | 46912 | 46955 | 46955 | 99 | Q3-2024 - Projects to reconductor lines in Stanislaus, Melones, Riverbank, Ripon areas are being sequenced. As engineering nears completion and permitting is concluded, the project will reise its final schedule proceeding into construction and clearances.
C12P2-LDNUs overlap | Manteca-Ripon-Riverbank-Melones Area 115 kV Line Reconductoring Project | Reconductor 2.4 miles between Manteca and Ripon Jct and 1.8 miles between Riverbank SW STA and Valley Home Tap | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2022 | 46861 | TBD |  | 46874 | 46143 | 46143 | 46143 | 46143 | 46143 | 46904 | 47151 | 47400 |  | Q3-2024 - Project ISD delayed due to schedule/construction sequencing date adjustments.
C13P1-FLO01 | Helm-Crescent Sw Sta 70 kV Line Reconductor | Reconductor a total of 4.77 miles of Helm-Crescent Sw Sta 70 kV Line with 1113 AAC and upgrade any limiting equipment to enable full conductor rating ~1400 A | PG&E | C13 | Deliverability | Re-conductor | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 overstress | Replace Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2018 | 46420 |  | 45808 | 45806 | 45798 | 46070 | 45790 | 46079 | 45923 | 46508 | 47268 | 46624 | 2093 | Q3-2024 - Scope, design, and materials have prolonged the project schedule.
C13P1-KGR01 | QC13P2RAS-04 Midway 500/230 kV Transformer Overload RAS | QC13P2RAS-04 Modify existing Midway 500/230 kV transformer overload SPS to include transformer outage detection and transformer overload detection for Bank 11, 12, and 13 | PG&E | C13 | Reliability | RAS (Reliability) | Initiating | 2024 | [11 empty] | 47768 | 100 | Q3-2024 - Recently triggered by Generation
C13P1-KGR05 | Midway Substation 230 kV bus and 27 circuit breakers overstress - Revised to Install Bus Reactors (2) | Install 2 x 16 ohm series bus reactors between Midway Substation 230 kV bus sections D and E (16 ohm parallel/8 ohm net) | PG&E | C13 | Reliability | SCD overstress | Initiating | 2024 | [11 empty] | 47768 | 1250 | Q3-2024 - Recently triggered by Generation
C13P1-KPN02 | Convert Midway Substation 230 kV Bus D to BAAH | Convert Midway Substation 230 kV to BAAH in order to install bus reactors & RAS | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2016 | 46492 |  |  |  |  | 45772 | 45772 | 45772 | 45785 | 46748 | 47542 | 46773 | 1250 | Q3-2024 - no date changes at this time.
C13P1-WGR03 | Mesa Substation 115 kV CBs 142 overstress | Replace Mesa Substation 115 kV CB 142 with 63 kA interrupting capability | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-GGD01 | PGAE_250_QC14P1RAS-03-gbay-tassajara–q1877ss-overload-RAS | RAS to trips Q1877 at Q1877SS Switching Station when an overload occurs in GRANT-Q1877SS or Q1877SS-EASTSHORE 115kV Lines due to outage of Q1877SS-EASTSHORE or GRANT-Q1877SS 115kV Lines, respectively, when Q1877 is in discharging mode. | PG&E | C14 | Reliability | RAS (Reliability) | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-GGR03 | Ames Distribution 115 kV circuit breaker 112 & 122 overstress | Replace Ames Distribution 115 kV circuit breakers 112 & 122 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-GGR06 | Newark 115 kV bus overstress beyond 63 kA | Install series bus reactors between Newark Substation 115 kV bus secions E and F | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-GGR07 | Newark 230 kV cap bank circuit breakers 974, 984 & 994 overstress | Replace Newark 230 kV cap bank circuit breakers 974, 984 & 994 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-GGR08 | Sobrante 115 kV CB 112 overstress | Replace Sobrante 115 kV circuit breaker 112 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-GGR09 | Tesla 230 kV Bus Overstress (2 CB with Line relocations) | Relocate a Tesla - Tracy #2 230kV line to Bus Sect. C - into BAAH bay position where Newark #2 line resides today. Newark #2 will shift to a new BAAH bay. Includes costs for (9) 230kV T-Line structures (4,000 feet of new line), BAAH bay w/2 CB's. | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-KGR11 | Midway 500 kV CB 742, 822, 912, 932, 942 Overstress | Replace Midway 500 kV CB 742, 822, 912, 942 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 1150 | Q3-2024 - not triggered
C14P1-NGR02 | Cottonwood 230 kV circuit breaker 272 & 292 overstress | Replace Cottonwood 230 kV circuit breaker 272 & 292 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-NLD02 | Eagle Rock-Cortina 115 kV Line (Lower Lake Sw Sta-Highland J2-Cache J) | Reconductor 2.5 miles of Eagle Rock-Cortina 115 kV (Lower Lake SW STA-Highland J2 section) to 477 ACSS and upgrade any limiting equipment | PG&E | C14 | Deliverability | Re-conductor | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-NLD04 | Ukiah-Hopland-Cloverdale 115 kV Line (Cloverdale-Hopland J) and Geysers #3-Eagle Rock 115 kV Line (Geysers34-Eagle Rock) | Reconductor 14.79 miles of Ukiah-Hopland-Cloverdale 115 kV (Cloverdale-Hopland Jt) to 477 ACSS and upgrade any limiting equipment | PG&E | C14 | Deliverability | Re-conductor | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-NLD05 | Geyser #3-Cloverdale 115 kV Line (Aidlin SwSta-Cloverdale) | Reconductor 8 miles of Geyser #3-Cloverdale (MPE Tap-Cloverdale) 115 kV to 477 ACSS and upgrade any limiting equipment | PG&E | C14 | Deliverability | Re-conductor | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P1-NLD06 | Ukiah-Hopland-Cloverdale 115 kV Line (Cloverdale-Hopland J) and Geysers #3-Eagle Rock 115 kV Line (Geysers34-Eagle Rock) | Reconductor entire Geysers #3-Eagle Rock 115 kV (1.77 miles) to 1113 AAC and upgrade any limiting equipment | PG&E | C14 | Deliverability | Re-conductor | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-FGR04 | Los Banos 500 kV circuit breakers 822, 832 & 842 overstress | Replace Los Banos 500 kV circuit breakers 822, 832 & 842 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 1150 | Q3-2024 - not triggered
C14P2-FGR05 | Transient stability mitigation: Panoche-Mendota 115 kV lines RAS | RAS should trip the output of Q1940 for the loss of Panoche-Mendota 115 kV line to mitigate the oscillations and voltage criteria violations. | PG&E | C14 | Reliability | RAS (Reliability) | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-FGR06 | Transient Stability: Updated dynamic models required | Updated dynamic models required that exhibits acceptable performance. | PG&E | C14 | Reliability | Transient Stability | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-FPN02 | Los Banos 230 kV circuit breaker 252 & 262 overstress | Relocate CB 262, 242 & 252 and their line terminal to the new 230 kV BAAH bus section. 242 & 252 line terminals would be crossed if we only move one line. | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-FPN03 | Los Banos 230 kV circuit breakers 212 & 222 overstress | Replace Los Banos 230 kV circuit breakers 212 & 222 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-FPN05 | Los Banos: Q1381 is assigned a 230 kV BAAH Bus Section CB 262 Overtress | Needed for CB 262 Overtress GRNU | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-FPN06 | Panoche 115 kV circuit breakers 132 & 152 overstress |  | PG&E | C14 | Reliability | SCD overstress | In-Flight | [12 empty] | 46871 | 0 | Q3-2024 - Part of the New Manning project scope
C14P2-FPN07 | Panoche 230 kV bus overstress above 40 kA design and circuit breakers 212, 232, 242 ,252, 262, 272, 282, 292, 302, 312, 332, 412 & 422 overstress |  | PG&E | C14 | Reliability | SCD overstress | In-Flight | [12 empty] | 46871 | 1150 | Q3-2024 - Part of the New Manning project scope
C14P2-GGR10 | Claremont (OAK K) 115 kV circuit breaker 122 overstress | Replace Claremont (OAK K) 115 kV circuit breaker 122 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-GGR11 | Palermo 115 kV CB 152 overstress | Replace Palermo 115 kV CB 152 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-GGR12 | Pittsburg 230 kV bus overstress. Bus D-E 230kV Buss Reactors | Install bus reactors between 230 kV sections D & E | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-GGR13 | Ravenswood 115 kV CB 132 and 142 | Replace Ravenswood 115 kV CB 132 and 142 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-GGR14 | Birds Landing Sw Sta 230 kV CB 212, 412 overload mitigation | Upgrade Birds Landing Sw Sta 230 kV bay 2 to 3000 A equipment and replacing 3 circuit breakers and associated switches/relays | PG&E | C14 | Reliability | Bus Flow | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-GGR15 | Pittsburg Substation 230 kV Bus Section E overload. enhance conductor rating | Seek enhanced ratings of 2964/3372A for 2-2300 kcmil AL conductor. Assumes replacement of all fittings to compression and limited reconductor work to attach new fittings. | PG&E | C14 | Reliability | Bus Flow | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-GGR16 | Pittsburg Substation 115 kV Bus Section E overload. Reconductor/Reinforce Bus. | Reconductor bus to 3-2300 kcmil. Evaluate and Reinforce Structures. | PG&E | C14 | Reliability | Bus Flow | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-GGR17 | Midway 230 kV reactor replacement | Replace existing 9 ohm Midway 500/230 kV reactors with 13 ohm reactors, | PG&E | C14 | Reliability | Reactor Upgrade | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-GPN01 | Pittsburg 115 kV bus overstress. Bus D-E 115kV Buss Reactors | Install bus reactors between 115 kV sections D & E | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-GPT04 | Ravenswood 115 kV CB 152, 312, 322 overstress | Replace Ravenswood 115 kV CB 152, 312, 322 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-KGR09 | Kern PP 70 kV circuit breaker 62 overstress | Replace Kern PP 70 kV circuit breaker 62 | PG&E | C14 | Reliability | SCD overstress | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-NLD07 | Hopland Transformer Bank #2 | Replace Hopland 115/60 kV Transformer Bank #2 with 3-phase 100/110 MVA transformer with LTC | PG&E | C14 | Deliverability | Transformer | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C14P2-SGR01 | Midway Substation 500 kV circuit breaker 712 overload mitigation | Replace Midway 500 kV CB 712, switches and jumpers to achieve 4000 A normal rating | PG&E | C14 | Reliability | Bus Flow | Initiating | [12 empty] | TBD | 0 | Q3-2024 - not triggered
C8P1-34 | Re-conductor Padre Flat SS-Panoche #1 230 kV Line | Re-conductor 32.59 mi Q779/Padre Flat SS-Panoche #1 230 kV Line with 795 ACSS | PG&E | C8 | Deliverability | Re-conductor | In-Flight | 2017 | 45190 | 44967 | 45443 | 45433 | 45432 | 45432 | 45422 | 45422 | 45422 | 45790 | 45790 | 45796 | 1020 | Q3-2024 - Delays to obtaining land rights to mitigate conductor blowout, and subsequently construction sequencing for 230kV clearances has moved out this project's schedule. On track to complete in 2025.
C8P2-1 | Re-conductor Borden-Gregg #1 230 kV Line | Re-conductor 6.25 mi Borden-Gregg #1 230 kV Line with 1113 ACSS and upgrade equipment to 2000 A minimum (this is the existing Borden-Gregg 230 kV Line) | PG&E | C8 | Deliverability | Re-conductor | In-Flight | 2017 | 46248 | 45588 | 46027 | 46027 | 46027 | 46027 | 46027 | 46149 | 46149 | 46149 | 46149 | 46395 | 932 | Q3-2024 - Delays to obtaining land rights to mitigate conductor blowout, and coordinating and planning a re-route of a part of the line due to commercial land develpments has moved out this project's schedule. On track to complete in 2027.
C8P2-10 | QC8RAS-02 SPS (Deliverability Triggered RNU) | QC8SPS-02 SPS to modify the existing Hatchet Ridge SPS to trip Q1106 200 MW wind and Hatchet Ridge 102 MW wind for thermal overloads on the Q1106 SS-Cottonwood, Carberry SS-Round Mountain or Pit #3-Carberry SS 230 kV Lines. | PG&E | C8 | Deliverability | RAS (Deliverability) | Deferred | 2017 | 45736 |  | 45135 | 45135 | 45135 | TBD | 46477 | 47094 | 47094 | 47094 | 47094 | 45940 | 200 | Q3-2024 - Generation project is seeking permits prior to moving forward with Utility dependencies.
C8P2-15 | Cottonwood Substation 230 kV Circuit Breaker 522 and 542 Overstress | Cottonwood Substation 230 kV CB Overstress: Replace CB 522 & 542 (rated @ 34.5KA, overstress close-in fault is 35,179A or 2%, 679A). | PG&E | C8 | Reliability | SCD overstress | In-Flight | 2018 | 45531 |  | 45135 | 45153 | 45153 | 45565 | 45565 | 45539 | 46022 | 45992 | 45705 | 46022 | 700 | Q3-2024 - Going into construction. CBs coming in Aug 2024. ISD estimated Aug 2025.
C8P2-3 | QC8RAS-08 RAS (Deliverability Triggered RNU) | QC8RAS-08 RAS to trip Generation offline for outage AND overload of either Gates 500/230 kV Transformer Bank 11 or 12 | PG&E | C8 | Deliverability | RAS (Deliverability) | In-Flight | 2017 |  |  | 44938 | 44938 | 45291 | 45415 | 45415 | 45415 | 45415 | 45415 | 45415 | 45565 | 2990.65 | Q3-2024 - RAS tied to having Bank 11 and 12 operational. Bank 12 out of service for STATCOM project activities.
C9P1-F11 | Re-conductor Dos Amigos PP-Panoche #3 230 kV Line | Re-conductor 23.63 mi Dos Amigos PP-Panoche #3 230 kV Line with 795 ACSS | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2017 | 45673 |  | 45791 | 45777 | 45777 | 45777 | 45777 | 45777 | 45778 | 46143 | 46157 | 46160 | 752 | Q3-2024 - Delays to obtaining land rights to mitigate conductor blowout, and subsequently construction sequencing for 230kV clearances has moved out this project's schedule. On track to complete in 2026.
C9P1-F12 | Re-conductor Borden-Gregg #2 230 kV Line | Re-conductor 6.25 mi Borden-Gregg #2 230 kV Line with 1113 ACSS | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2017 | 46398 | 45588 | 45808 | 45784 | 45784 | 45784 | 45784 | 46038 | 46038 | 46038 | 46038 | 46519 | 932 | Q3-2024 - Delays to obtaining land rights to mitigate conductor blowout, and coordinating and planning a reroute of a part of the line due to commercial land develpments has moved out this project's schedule. On track to complete in 2027.
C9P2-N02 | Re-conductor Fulton-Hopland 60 kV Line (Geysers Jct-Cloverdale Jct-Hopland) | Re-conductor 24.21 mi Fulton-Hopland 60 kV Line (Geysers Jct 016/003A-Cloverdale Jct 026/002-Hopland) with 715 AAC and upgrade any limiting equipment | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2019 | 46428 | 45552 | 46538 | 46477 | 46752 | 45964 | 46066 | 46167 | 46178 | 46114 | 46104 | 46477 |  | Q3-2024 - Prioritization of this project and construction sequencing impacts due to other projects in the area. The project remains sensitive to clearance constraints and construction resource dependencies in event of severe weather and fire mitigation / response.
Impact to C14 | Tesla MPAC | New 230kV MPAC building relocates 230kV equipment from existing Control Building | PG&E | C14 | Capacity | MPAC | In-Flight | 2018 | 45953 |  |  | n/a | n/a | 45574 | 46022 | 46022 | 46022 | 46022 | 46105 | 46182 |  | Q3-2024 - Design completed.
see C12P1-GCR01 | Oakland Clean Energy Initiative (MORAGA 115KV BUS UPGRADE & BK 3 SW) | The project will install two bus-sectionalizing circuit breakers and one bus-tie breaker on the 115 kV buses at Moraga Substation, which will improve the reliability and operational flexibility of the buses. The project will also replace Bank 3 115kV switches 771, 773, 777, 779, 791, 793, & 795 which will improve the reliability and operational flexibility of the buses. | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2018 | 44516 | N/A | 44989 | 45065 | 45125 | 45251 | 45229 | 45748 | 45777 | 45777 | 45777 | 45867 |  | Q3-2024 - no date changes at this time.

## SCE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Serivce July 2022 TDF | Expected In-Service Oct TDF 2022 | Expected In-Service January TDF 2023 | Expected In-Service April TDF 2023 | Expected In-Service July TDF 2023 | Expected In-Service Oct TDF 2023 | Expected In-Service Jan TDF 2024 | Expected In-Service July TDF 2024 | Agregate MW in Queue with Executed LGIA | Notes
PIN6902 | Calcite Substation | New four position 220 kV switchrack | SCE | Serial LGIP | GRNU | New Substation | Plan/Analyze | 2026-07-01 | 2025-04-01 | 44165 | 2024-01-31 |  |  | New | TBD | TBD | 2027-03-01 | 2027-03-01 | 2027-12-31 | 2027-11-01 | 400 | Delay by interconnection customer due to EIR recirculation and forecast to complet mid July 2024. FEIR publication by customer estimated date Q4 2024. According to the customer, the FEIR certification by the San Bernardino County is estimated by Dec. 2024.
SCE-C11P2-EOP-R1 | Lugo - Victorville CRAS - monitoring infrastructure | Infrastructure to convert the Lugo - Victorville RAS to centralized RAS platform | SCE | C11 Phase II | GRNU | RAS/CRAS | Design | 2025-06-01 | N/A | 43770 | 2024-06-01 | Jun-25 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-30 | 2025-06-01 | 2026-06-30 | 2027-12-30 | 950 | ISD change due to excess customers being added to the Tehachepi CRAS in Q2-2024 and to reduce potential cascading impacts to CRAS testing queue for 2024.
SCE-TCP2-EOP-R4 | Lugo - Victorville RAS | Trip generation for Eldorado area 500kV line outages. | SCE | TC Phase II | RNU | RAS/CRAS | Permitting | 2024-10-01 | N/A | 40787 | 44166 | 45047 | 45047 | 45047 | 45261 | 45261 | 2024-04-30 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 530 | Construction to start in October 2024 with an In-service date of June 2025. Project sequencing and outage constraints has slipped the construction start to October 2024
SCE-C12P2-N-R3 | Moorpark CRAS: monitoring infrastructure | New Moorpark CRAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | TBD | N/A | 44378 | 45474 | 45474 | 45474 | 45474 | 45474 | Pending | 2025-10-15 | 2025-10-15 | 2025-10-15 | 2027-12-01 | 735 | Due to challenges with interconnection at Moorpark Substation, Customer suspended project. Customer sold the project to another third party and is investigating possible relocation of project site.
SCE-C9P2-NOL-R1 | New North of Lugo RAS - Backbone Portion | New North of Lugo RAS combining HDPP RAS and Calcite RAS | SCE | C9 Phase II | RNU | RAS/CRAS | Design | 2029-01-01 | N/A | 43040 | 2024-06-01 | 2024-06-30 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2026-06-01 | 2026-06-01 | 2026-06-01 | 2030-06-30 | 800 | Project sequencing and outage constraints has slipped the construction start to 2029 with an In-service date of June 2030
SCE-C11P2-N-L1 | Pardee – Pastoria – Warne 220 kV T/L rating increase | Upgrade terminal equipment and fix ground clearance for Pardee – Pastoria- Warne 230kV line | SCE | C11 Phase II | LDNU | Capacity Increase | Execution | 2023-06-01 | N/A | 44013 | 44849 | 45170 | 45078 | 45078 | 45383 | 45078 | 2023-10-30 | 2024-03-29 | 2024-03-29 | 2025-12-01 | 126 | As it relates to Pardee - Pastoria - Warner 220kV Transmission lines, eight 220kV structures identified to brought in compliance with GO-95 of which seven structures have been raised and brought into compliance. However, the last structure cannot be raised until the Pardee - Pastoria lines 1 & 2 are re-conductored and energized by the end of year 2025. Then, outage required to bring the last 220Kv Structure into compliance with GO-95 can be schedule. Estimated to complete the eight structure by end of year 2025.
SCE-C72021-EOP | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | SCE | 2021 Reassessment | RNU | RAS/CRAS | Design | 2025-06-01 | N/A | 44409 | 2025-06-01 | 2025-06-30 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2026-06-30 | 2027-12-30 | 550 | Project sequencing and outage constraints has slipped the construction start to 2025. Change of project sequencing at Lugo
PIN8483-RNU | South of Vincent CRAS | Add lines south of Vincent to the Tehachapi CRAS | SCE | C13 Phase II | RNU | RAS/CRAS | Design | 2025-12-01 | N/A | 2021-12-31 | 2026-04-30 |  |  | New | 2026-02-01 | 2026-02-01 | 2026-02-01 | 2027-12-15 | 2027-12-15 | 2026-05-01 | 1300 | While developing the schedule for this project, the CRAS monitoring infrastructure portion of the project was discussed with the responsible engineers for the affected substations. It was determined that the in-service date for this scope of work could be earlier than originally thought. Since this part of the project could be brought online before the in-service of the customer's interconnection, it was decided that we would use the earlier in-service date
SCE-C12P2-N-R2 | Tehachapi CRAS: monitoring infrastructure addition | Add N-1 to RAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | 2025-01-01 | N/A | 44228 | 2024-09-01 | 2024-09-01 | 2024-09-01 | 2024-09-01 | 2025-04-01 | 2025-04-01 | 2025-11-01 | 2026-03-01 | 2026-03-01 | 2026-03-01 | 3200 | No ISD change between Jan 2024 TDF and July 2024 TDF
SCE-C10P2-E-R3 | West of Colorado River CRAS Inland/Devers Extension - monitoring infrastructure | Infrastructure to convert the formally referred to as the New Devers RAS and the Inland RAS to centralized RAS platform | SCE | C10 Phase II | RNU | RAS/CRAS | Closeout | 2022-03-01 | N/A | 43435 | 44470 | Aug-25 | 44986 | 44986 | 45078 | 45192 | 45192 | 2024-03-01 | 2024-03-01 | 2024-04-01 | 4555 | Multiple project prioritization shifted the ISD from Jan 2024 TDF to July 2024 TDF
SCE-C9P2-N-R1 | Whirlwind AA Bank CRAS Monitoring Infrastructure | Implement Whirlwind AA Bank CRAS - monitoring infrastructure | SCE | 2018 Reassessment | GRNU | RAS/CRAS | Execution | 2023-08-01 | N/A | 44013 | 44866 | 44958 | 44958 | 44958 | 45078 | 45078 | 2024-03-30 | 2024-06-01 | 2024-12-31 | 2024-12-31 | 1515 | No ISD change between Jan 2024 TDF and July 2024 TDF
SCE-C9C10-N | Windhub AA Bank cRAS - monitoring infrastructure | Windhub AA Bank cRAS - monitoring infrastructure | SCE | 2021 Reassessment | GRNU | RAS/CRAS | Closeout | 2023-03-01 | N/A | 44409 | 44866 | 44958 | 44958 | 44958 | 44986 | 45046 | 2023-12-31 | 2023-09-01 | 2024-12-31 | 2024-02-01 | 1800 | Expected ISD shifted to an earlier start from the Jan 2024 TDF.
SCE-C11P2-E-R1 | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub | SCE | C11 Phase II | RNU | RAS/CRAS | Design | 2028-10-01 | N/A | 43891 | 2026-10-01 | 2026-10-01 | 2026-10-01 | 2026-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 2029-10-01 | 865 | City of Riverside delays caused by their pursuit of additional undergrounding funding
SCE-C10P2-E-R3 | WOCR CRAS Inland/Devers Extension Monitoring (QC10) at Alberhill Sub | WOCR CRAS Inland/Devers Extension Monitoring (QC10) at Alberhill Sub | SCE | C10 Phase II | RNU | RAS/CRAS | Design | Pending | N/A | 43435 | 2025-08-01 | 2025-08-01 | 2025-08-01 | 2027-04-01 | TBD | TBD | TBD | 2029-06-01 | 2029-06-01 | Pending | 4555 | Hold/subject to be cancelled due to Alberhill Substation Project delay

## SDGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service July 2022 TDF | Expected In-Service October 2022 TDF | Expected In-Service January TDF 2023 | Expected In-Service Date April TDF 2023 | Expected In-Service July 2023 TDF | Expected In-Service Oct 2023 TDF | Expected In-Service Jan 2024 TDF | Current Estimated In-Service July 2024 TDF | Notes
SDGE-EXISTING-RNU-01 | Imperial Valley Existing/Modified RAS' | Imperial Valley Existing/Modified RAS' | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-7.1 | Existing Miguel BK 80 / 81 | Existing Miguel BK 80 / 81 | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-02 | Existing Otay Mesa RASs | Existing Otay Mesa RASs | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-04 | Existing ECO/BUE anti-islanding scheme for radial generators | Existing ECO/BUE anti-islanding scheme for radial generators | SDGE |  | PNU |  | Operational
SDGE-C11-PHII-RNU-02 | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | SDGE | C11 Phase II | PNU | Reliability | Operational |  | N/A | N/A | 2024-06-22 | 2024-06-22 | 2024-06-22 | 2024-06-22 | 2024-07-22 | 2024-06-22 | 2024-07-22 | 2024-06-22 | 2024-06-22 | In-Service |  | Placed in service on 6/18/22
SDGE-C08-PHII-RNU-03.1 | TL680 OLS | Overload Scheme to protect TL680C. Previously named as Modify TL684 RAS. | SDGE | C8 Phase II | GRNU | Deliverability | Operational |  | N/A | 1905-07-15 | 2024-06-23 | 2024-06-23 | 2024-06-23 | 2024-06-23 | 2024-06-23 | 2024-06-23 | 2024-04-23 | In-Service | In-Service | In-Service |  | Placed in service on 3/30/23
SDGE-C07-PHI-RNU-01 | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | SDGE | C7 Phase I | PNU | Reliability | Operational |  | N/A | 1905-07-15 | 2024-06-23 | 2024-06-23 | 2024-06-23 | 2024-06-23 |  | 2024-06-23 | 2024-06-23 | 2024-08-23 | 2024-08-23 | 2024-08-23 |  | Placed in service 8/20/23
SDGE-C08-PHII-RNU-04 | Participate in the proposed RAS to protect TL23003 & TL23011 Encina to San Luis Rey 230 kV lines (Proposed grouping RAS to protect Encina/Pen/San Luis Rey 230kV Lines) | Proposed RAS to Protect TL23003 Encina - San Luis Rey 230 kV line | SDGE | C8 Phase II | PNU | [6 empty] | 2024-06-23 | 2024-06-23 | 2024-06-23
SDGE-PRE-AMEND-RNU-01.2 | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | SDGE |  | CANU-GR | [6 empty] | 2024-06-23 | 2024-06-23 | 2024-06-23
SDGE-C14-PHII-RNU-81 | update relay settings for Q1532 - ECO 138 kV #1 line | update relay settings for Q1532 - ECO 138 kV #1 line | SDGE | C14 Phase II | GRNU | Deliverability | Planning | 2024-05-27 | N/A | 2024 | 2024-05-28 | [9 empty] | 2024-05-28

## GLW-VEA
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service July 2022 TDF | Expected In-Service Oct 2022 TDF | Expected In-Service Jan 2023 TDF | Expected In-Service April 2023 TDF | Expected In-Service July 2023 TDF | Expected In-Service Oct 2023 TDF | Expected In-Service Jan 2024 TDF | Expected In-Service July 2024 TDF | Agregate MW in Queue with Executed LGIA | Notes
VEA-C6P2-EOP-R5 | VEA Vista RAS | VEA Vista RAS: Install a new RAS to protect Jackass Flats - Mercury Switch 138 kV line under contingency conditions | VEA | C6 Phase II | RNU | Thermal | Cancelled | N/A | N/A | N/A | N/A | 2022-09-30 | 2022-11-22 | [7 empty] | N/A |  | Project was replaced by upgrading the Jackass Flats - Mercury Switch 138kV line. This project is completed.
VEA-C8P2-VEA-R2 | Innovation RAS | Install a new Innovation RAS | GLW | C8 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 | Complete | Complete | Complete | 1547 | Project completed.
VEA-C9P2-EOP-R3 | Innovation RAS (VEA-GLW portion) | New Innovation RAS (include Desert View RAS from QC8) to trip generation under N-1 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 | Complete | Complete | Complete | 1547 | Project completed.
VEA-C9P2-EOP-R4 | Sloan Canyon RAS (fka Bob RAS - VEA-GLW portion) | New Sloan Canyon RAS to trip generation under N-1 and N-2 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 | Complete | Complete | Complete | 1547 | Project completed.
GLW-2021-EOP-L1 | Trout Canyon - Sloan Canyon 230kV line upgrade | Trout Canyon - Sloan Canyon 230kV line upgrade | GLW | 2021 Reassessment | LDNU |  |  |  |  | N/A | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | N/A | 2027-12-31 | 2027-12-31 | 2026-12-31 | N/A | The Trout Canyon – Sloan Canyon 230kV Line Upgrade is part of the GLW Upgrade Project which was approved through the 2021-2022 TPP and revised in the 2022-2023 TPP to 500kV DCTL. GLW is prioritizing the TC-SC 500kV segment, after further evaluation of the current GLW/VEA Area project permitting timeline, the TC-SC 500kV segment is targeted for December 2026 ISD.