## READ_ME
CAISO PUBLIC
1. The transmission capability estimates in this document are based on the resource-type specific output assumptions that are used in deliverability studies rather than the resources’ installed capacity. The values can be translated into any combination of resource types by applying the currently applicable deliverability study resource output factor.
2. The estimates are over and above the resource amounts that were online as January 1, 2026. The CPUC will need to adjust the estimates to account for resources that came online since then. Retirement of Diablo Canyon is accounted for in the estimates assuming the replacements are at the same or similar location.
3. The estimates have been calculated after modeling as imports and effectively reserving deliverability for out-of-CAISO long lead-time generation resources specified in the Table 1-1 of the 2025-2026 Transmission Plan.
4. Reserved deliverability at the locations and amounts as identified in the Table 1-1 of the 2025-2026 Transmission Plan are included in the transmission plan capability and allocated TPD . 5. Future reservations at the locations and amounts as identified in the Table 1-1 of the 2025-2026 Transmission Plan are included in the available TPD.
6. The available TPD also includes in-state geothermal reservation at the following locations and amounts as included in the CPUC base portfolio for 2025-2026 TPP: 400 MW at Beatty 230 kV, 28 MW at Cloverdale 115 kV, 22 MW at Eagle Rock (PG&E) 115 kV, 54 MW at Fulton 230 kV and 20 MW at Geysers 17 230 kV.
7. The transmission capability estimates of all East of Pisgah area constraints have been calculated with Trout Canyon - Lugo 500 kV line project. The incremental capability is for CPUC information only.

## TxCapabilityEstimates_2026
Transmission capability estimates for use in the CPUC's IRP process - Revised 07/15/2026
Transmission Constraint | Affected Resource Locations | Condition Under Which Constraint is Binding (On-peak and/or Off-peak) | Estimated FCDS Capability Based on On-peak Study Resource Output (MW) |  | Network Upgrade & Cost Estimate ($million) |  | Estimated EODS Capability Based on Off-peak Study Resource Output (MW) |  | Network Upgrade & Cost Estimate ($million) |  | Wind/Solar Area Designation
|  |  | Transmission Plan Capability | Incremental due to Network Upgrade | NU Description (Time to Construct or ISD) | Cost (2022$) | Transmission Plan Capability | Incremental due to Network Upgrade | NU Description (Time to Construct or ISD) | Cost (2022$)
SCE Northern Interconnection Area Constraints
Antelope-Vincent Constraint | Tehachapi, Big Creek | On-Peak | 6638 | 1500 | Upgrade Antelope-Vincent No.1 and 2 500 kV Lines (2 yrs) | 13.2 | 12188 | N/A | N/A | N/A | Solar
Vincent-Lugo Constraint | Tehachapi | On-Peak | 7030 | 1500 | Upgrade Vincent-Lugo No.1 and 2 500 kV Lines (4 yrs) | 85.9 | 10326 | N/A | N/A | N/A | Solar
Pardee-Sylmar Constraint | Big Creek, Ventura | On-Peak | 3038 | 1800 | Install Phase Shifters at Pardee on the Pardee-Sylmar No. 1 and No. 2 230 kV Lines, Reconductor Pardee-Vincent No. 2 220 kV line (9 yrs) | 660 | 4860 | N/A | N/A | N/A | Solar
Windhub Constraint | Tehachapi | On-Peak | 775 | 2500 | New 500 kV Transmission Line from Whirlwind to Windhub 500 kV (9 yrs) | 612 | 2917 | N/A | N/A | N/A | Solar
Moorpark-Pardee Constraint | Ventura | On-Peak | 849 | 900 | Upgrade the Moorpark-Pardee #2 and #3 220 kV and Santa Clara-Vincent 220 kV lines (9 yrs) | 600 | 1218 | N/A | N/A | N/A | Solar
North of Magunden Constraint | Big Creek | On-Peak | 1323 | 500 | Rebuild Magunden - Vestal No.2 230 kV and Magunden - Springville No.2 230 kV Lines (9 yrs) | 1253 | 1789 | N/A | N/A | N/A | Solar
South of Magunden Constraint | Big Creek, Ventura | On-Peak, Off-Peak | 1011 | 2000 | Rebuild various SOM lines (9 yrs) | 4358 | 3468 | 2000 | Rebuild Magunden-Pastoria 230 kV line (9 yrs) | 66 | Solar
Sylmar- Rinaldi Constraint | Big Creek, Ventura | On-Peak | 3177 | 1800 | Install Phase Shifters at Pardee on the Pardee-Sylmar No. 1 and No. 2 230 kV Lines, Reconductor Pardee-Vincent No. 2 220 kV line (9 yrs) | 660 | 4554 | N/A | N/A | N/A | Solar
Antelope-Neenach Constraint | Antelope/Bailey/Pastoria area | On-Peak, Off-Peak | 0 | 2000 | Reconductor Antelope-Bailey 66 kV lines (2 yrs) | 100 | 0 | 15 | Bailey-Neenach-Westpac 66 kV line upgrade | 45 | Solar
SCE Metro Interconnection Area Constraints
Hinson - Del Amo Constraint | LA Basin | On-Peak | 2700 | 800 | Upgrade the Hinson - Del Amo 220 kV Transmission Line (27 months) | 28 | 2700 | N/A | N/A | N/A | Solar
SCE Metro Area Default Constraint | LA Basin | None | 13500 | N/A | N/A | - | 13500 | N/A | N/A | N/A | Solar
SCE North of Lugo (NOL) Interconnection Area Constraints
Control to Inyokern area constraint | Inyokern_North | On-Peak | 0 | 186 | Build a new, series compensated Control-Inyokern 115 kV line and upgrade Inyo Phase Shifter (105 months) | 329 | 120 | N/A | N/A | N/A | Solar
South of Kramer Area Constraint | Inyokern_North_Kramer Victor | On-Peak | 938 | N/A | Approved Project: Convert Kramer - Victor 115 kV lines to 230 kV (120 months) | N/A | 2926 | N/A | N/A | N/A | Solar
Victor to Lugo Area Constraint | Inyokern_North_Kramer Victor | On-Peak | 1339 | N/A | Approved project:Re-conductor the four Lugo-Victor 230 kV lines (54 months) | N/A | 4113 | N/A | N/A | N/A | Solar
Lugo Transformer Area Constraint | Inyokern_North_Kramer, Victor, Pisgah | On-Peak | 1940 | N/A | Approved project: Add a third 500/230 kV transformer at Lugo Substation (54 months) | N/A | 4714 | N/A | N/A | N/A | Solar
Calcite to Lugo Area Constraint | Pisgah | On-Peak | 541 | 1046 | Rebuild Calcite-Lugo 220 kV Transmission Line (105 months) | 239 | 541 | N/A | N/A | N/A | Solar
SCE Eastern Interconnection Area Constraints
Colorado River 500/230 kV Constraint | Colorado River 230 kV | On-Peak, Off-Peak | 346 | 1370 | New Colorado River No. 3 500/230 kV transformer (4 years) | 67 | 2296 | 1299 | Same as ADNU | 67 | Solar
DCRT Constraint | Cielo Azul, Delaney | On-Peak | 1850 | 3000 | New Cielo Azul - Colorado River No. 2 500 kV line, Upgrade the series cap on Cielo Azul - Colorado River No.1 500 kV line to match the conductor rating (6 years) | 463 | 2615 | N/A | N/A | N/A | Solar
Devers-Red Bluff Constraint | SCE Eastern (east of Red Bluff), East of Pisgah, and SDG&E areas | On-Peak, Off-Peak | 4903 | N/A | Approved projects: Devers-Red Bluff 500 kV 1 and 2 Line Upgrade (2028) and Southern Area Reinforcement Project (2034) | N/A | 9590 | N/A | Approved projects: Devers-Red Bluff 500 kV 1 and 2 Line Upgrade (2028) and Southern Area Reinforcement Project (2034) | N/A | Solar
Eagle Mountain Constraint | Eagle Mountain, Julian Hinds, Mirage | On-Peak | 0 | 600 | New Devers-Julian Hinds 220 kV line (10 years) | 1182 | 346 | N/A | N/A | N/A | Solar
Etiwanda-Rancho Vista Constraint | SCE Eastern area | On-Peak | 4604 | 2850 | Etiwanda-Rancho Vista No. 3 220 kV line (3 years) | 89 | 7093 | N/A | N/A | N/A | Solar
Mira Loma-Mesa Constraint | SCE Eastern, EOP, NOL, Metro and SDG&E areas | On-Peak | 20763 | N/A | N/A | N/A | 36145 | N/A | N/A | N/A | Solar
Red Bluff 500/230 kV Constraint | Red Bluff 230 kV | On-Peak, Off-Peak | 1281 | 1200 | New Red Bluff No. 3 500/230 kV transformer (4 years) | 69 | 2493 | 1200 | Same as ADNU | 69 | Solar
Serrano-Alberhill-Valley Constraint | SCE Eastern and SDG&E areas | On-Peak, Off-Peak | 5581 | N/A | Approved projects: • Southern Area Reinforcement Project (2034) • Devers-Valley 500 kV 1 Line Upgrade (2028) • Serrano-Alberhill-Valley 500 kV 1 Line Upgrade (2028) • San Bernardino-Etiwanda 230 kV 1 Line Upgrade (2031) • San Bernardino-Vista 230 kV 1 Line Upgrade (2028) • Vista-Etiwanda 230 kV 1 Line Upgrade (2031) • Mira Loma-Mesa 500kV Underground Third Cable (2026) | N/A | 12434 | N/A | Approved projects: • Southern Area Reinforcement Project (2034) • Devers-Valley 500 kV 1 Line Upgrade (2028) • Serrano-Alberhill-Valley 500 kV 1 Line Upgrade (2028) • San Bernardino-Etiwanda 230 kV 1 Line Upgrade (2031) • San Bernardino-Vista 230 kV 1 Line Upgrade (2028) • Vista-Etiwanda 230 kV 1 Line Upgrade (2031) • Mira Loma-Mesa 500kV Underground Third Cable (2026) | N/A | Solar
East of Pisgah (EOP) Interconnection Area Constraints (SCE, GLW, VEA)
GLW 230kV area constraint | VEA 138kV and GLW 230kV buses | On-Peak, Off-Peak | 3706 | 853 | GLW Core Upgrade and Beatty 230kV Project (2022-23 TPP) (2028) and Trout Canyon-Lugo Project (2025-26 TPP) (2035) | N/A | 3961 | N/A | GLW Core Upgrade and Beatty 230kV Project (2022-23 TPP) (2028) and Trout Canyon-Lugo Project (2025-26 TPP) (2035) | N/A | Solar
Sloan Canyon - Eldorado area constraint | VEA 138kV, GLW 230kV and Eldorado 230kV buses | On-peak, Off-Peak | 4333 | 1180 | Trout Canyon-Lugo Project (2025-26 TPP) (2035) | N/A | 5402 | N/A | Trout Canyon-Lugo Project (2025-26 TPP) (2035) | N/A | Solar
Lugo - Victorville area constraint | East of Pisgah, SCE Eastern,SDG&E and SCE Northern areas | On-peak, Off-Peak | 8669 | 5410 | Trout Canyon-Lugo Project (2025-26 TPP) (2035) | N/A | 12058 | N/A | Trout Canyon-Lugo Project (2025-26 TPP) (2035) | N/A | Solar
Eldorado - McCullough Area constraint | East of Pisgah | On-peak, Off-Peak | 5953 | 1180 | Trout Canyon-Lugo Project (2025-26 TPP) (2035) | N/A | 7357 | N/A | Trout Canyon-Lugo Project (2025-26 TPP) (2035) | N/A | Solar
SDG&E Interconnection Area Constraints
Capistrano-San Onofre 230 kV constraint | SDGE local area | On-peak | 1314 | 920 | Capistrano-San Onofre 230 kV upgrade (60 months) | 58.1 | 1314 | N/A | N/A | N/A | N/A
Chicarita 138 kV constraint | Baja, Imperial, SDGE local area | On-peak | 224 | 700 | Chicarita 138 kV Upgrades (48 months) | 100 | 224 | N/A | N/A | N/A | N/A
El Cajon 69 kV constraint | SDGE local area | On-peak | 406 | 547 | El Cajon 69 kV Upgrade (48 months) | 14.7 | 406 | N/A | N/A | N/A | N/A
Miguel 69 kV constraint | SDGE local area | On-peak | 231 | 431 | Miguel 69 kV upgrades (48 months) | 671.054 | 231 | N/A | N/A | N/A | N/A
Encina - San Luis Rey 230 kV constraint | Baja, Imperial, Arizona, SDGE local area | On-Peak, Off-Peak | 3724 | N/A | Approved Project: Southern California 500 kV Transmission Reinforcement (ISD - 2034); 30 minute emergency rating on Encina Tap-San Luis Rey 230 kV Line | N/A | 8631 | N/A | Same as ADNU | N/A | Solar
San Luis Rey-San Onofre 230 kV line constraint | Baja, Imperial, Arizona, SDGE local area | On-Peak, Off-Peak | 3988 | N/A | Approved Project: Southern California 500 kV Transmission Reinforcement (ISD - 2034); 30 minute emergency rating for San Luis Rey-San Onofre 230 kV #1 line | N/A | 9196 | N/A | Same as ADNU | N/A | Solar
Ocean Ranch 69 kV constraint | SDGE local area | On-peak | 194 | 692 | Ocean Ranch 69 kV upgrade (48 months) | 28.3 | 194 | N/A | N/A | N/A | N/A
Otay Mesa 230 kV constraint | Imperial, SDGE local area | On-peak | 975 | 2189 | Otay Mesa 230 kV upgrade (60 months) | 79.91 | 975 | N/A | N/A | N/A | N/A
Silvergate - Bay Blvd 230 kV constraint | Baja, Imperial, SDGE local area | On-Peak, Off-Peak | 3071 | N/A | Approved Project: Southern California 500 kV Transmission Reinforcement (ISD - 2034); 2 hour emergency rating on Silvergate-Bay Boulevard 230 kV line | N/A | 6266 | N/A | Same as ADNU | N/A | Solar
Silvergate-Old Town 230 kV constraint | Baja, Imperial, SDGE local area | On-peak | 1276 | N/A | Approved Project: Southern California 500 kV Transmission Reinforcement (ISD - 2034); 30 min emergency rating for Silvergate-Old Town and Silvergate-Old Town Tap 230 kV lines | N/A | 2923 | N/A | Same as ADNU | N/A | N/A
Talega 230 kV constraint | SDGE local area | On-peak | 1018 | 2201 | Talega 230 kV Upgrades (60 months) | 210.6 | 1018 | N/A | N/A | N/A | N/A
Trabuco-Capistrano 138 kV constraint | SDGE local area | On-peak | 501 | 556 | Trabuco-Capistrano 138 kV upgrade (48 months) | 103.366 | 501 | N/A | N/A | N/A | N/A
PG&E North of Greater Bay Interconnection Area Constraints
Collinsville-Tesla 500 kV Line | Greater Bay Area, North of Greater Bay Area | On-Peak | 4198 | TBD | Collinsville-Tesla 500 kV Reconductor | 122 | 15004.6355 | N/A | N/A | N/A | Wind
PG&E Greater Bay Interconnection Area Constraints
Bellota Area | Greater Bay Area and North of Greater Bay Area | On-Peak | 0 | TBD | New Bellota 230/115 kV Bank #3 | 18 | 224.4 | N/A | N/A | N/A | Wind
Bay Area | Greater Bay Area and North of Greater Bay Area | On-Peak | 1392 | TBD | New Contra Costa - Newark 230 kV line | 186 | 3258.63 | N/A | N/A | N/A | Wind
Tesla-Westley 230kV Area | Greater Bay Area, North of Greater Bay Area and Fresno | On-Peak | 1166 | TBD | New Tesla - Fink 230 kV line | 138 | 2424.7 | N/A | N/A | N/A | Wind
Vaca – Contra Costa Area | Greater Bay Area and North of Greater Bay Area | On-Peak | 1570 | TBD | New Vaca Dixon - Birds Landing 230 kV line | 98 | 2751.091 | N/A | N/A | N/A | Wind
Lockeford 230 kV Area | Greater Bay Area, North of Greater Bay Area and Fresno | On-Peak | 759 | TBD | Lockford - Bellota 230 kV #1 Line Recoductor | 37 | 3607.45 | N/A | N/A | N/A | Wind
Banta 115 kV Area | Greater Bay Area | On-Peak | 218 | TBD | New Subacco | 335 | 831.6757 | N/A | N/A | N/A | Wind
Tesla 115 kV Area | Greater Bay Area | On-Peak | 218 | TBD | New Tesla - Schulte 115 kV line | 16 | 831.6757 | N/A | N/A | N/A | Wind
PG&E Fresno Interconnection Area Constraints
Gates 500/230 kV Transformer Area | Fresno, Kern and Greater Bay Area | On-Peak | 4467.25 | TBD | New Gates 500/230 kV Transformer #13 | 221 | 11662.75 | N/A | N/A | N/A | Solar
Gregg 230 kV Area | Fresno | On-Peak | 0 | TBD | Gregg- Herndon # 1 & 2 230 kV line Reconductor | 2.8 | 1224 | N/A | N/A | N/A | Solar
Cottle 230 kV Area | Fresno and Greater Bay Area | On-Peak | 485.06 | TBD | New Warnerville - Wilson 230 kV line | 166 | 2588.06 | N/A | N/A | N/A | Solar
Mustang- Henrietta 230 kV Area | Fresno and Kern | On-Peak | 4530.5 | TBD | Mustang – Henrietta tap 1&2 230kV line Reconductor | 5.7 | 4660.975 | N/A | N/A | N/A | Solar
Manning - Gates 500 kV | Fresno and Kern | On-Peak | 7097.04 | TBD | New Manning - Gates 500 kV line | 515 | 10394.64 | N/A | N/A | N/A | Solar
PG&E Kern Interconnection Area Constraints
Manning- Harlan 500 kV Area | Kern | On-Peak | 5319.87 | TBD | New Midway - Manning 500 kV line | 753 | 8347.27 | N/A | N/A | N/A | Solar
Gates-Arco-Midway 230 kV Area | Kern and Fresno | On-Peak | 1567.94 | TBD | New Gates - Midway 230 kV line | 270 | 4591.34 | N/A | N/A | N/A | Solar
Bitterwater- Buena Vista 230kV kV Area | Kern | On-Peak | 186.84 | TBD | New Midway - Wheeler Ridge 230 kV line | 218 | 1029.34 | N/A | N/A | N/A | Solar