## TxCapabilityEstimates_2024_r1
Transmission capability estimates for use in the CPUC's IRP process - Revised 08/28/2024
Transmission Constraint | Affected Resource Locations | Condition Under Which Constraint is Binding (On-peak and/or Off-peak) | Estimated FCDS Capability Based on On-peak Study Resource Output (MW)* |  | ADNU & Cost Estimate ($million) |  | Estimated EODS Capability Based on Off-peak Study Resource Output (MW)* |  | AOPNU & Cost Estimate ($million) |  | Wind/Solar Area Designation
|  |  | Transmission Plan Capability** | Incremental due to ADNU | ADNU Name/Brief Description (Time to Construct or ISD) | Cost (2022$) | Transmission Plan Capability** | Incremental due to AOPNU | AOPNU (Time to Construct) | Cost (2022$)
SCE Northern Interconnection Area Constraints
Antelope-Vincent Constraint | Tehachapi, Big Creek | On-Peak | 6149.12 | 1500 | Upgrade Antelope-Vincent No.1 and 2 500 kV Lines (2 yrs) | 13.2 | 8920.36 | N/A | N/A | N/A | Solar
Vincent-Lugo Constraint | Tehachapi | On-Peak | 6733.24 | 2000 | Upgrade Vincent-Lugo No.1 and 2 500 kV Lines (4 yrs) | 85.9 | 8496.34 | N/A | N/A | N/A | Solar
Pardee-Sylmar Constraint | Big Creek, Ventura | On-Peak | 3530 | 1800 | Install Phase Shifters at Pardee on the Pardee-Sylmar No. 1 and No. 2 230 kV Lines, Reconductor Pardee-Vincent No. 2 220 kV line (9 yrs) | 660 | 6426 | N/A | N/A | N/A | Solar
Windhub Constraint | Tehachapi | On-Peak | 1333.6 | 2500 | New 500 kV Transmission Line from Whirlwind to Windhub 500 kV (9 yrs) | 612 | 2614.3 | N/A | N/A | N/A | Solar
Moorpark-Pardee Constraint | Ventura | On-Peak | 954 | 900 | Upgrade the Moorpark-Pardee #2 and #3 220 kV and Santa Clara-Vincent 220 kV lines (9 yrs) | 600 | 2641 | N/A | N/A | N/A | Solar
North of Magunden Constraint | Big Creek | On-Peak | 876 | 500 | Rebuild Magunden - Vestal No.2 230 kV and Magunden - Springville No.2 230 kV Lines (9 yrs) | 1253 | 1527 | N/A | N/A | N/A | Solar
South of Magunden Constraint | Big Creek, Ventura | On-Peak, Off-Peak | 977 | 2000 | Rebuild various SOM lines (9 yrs) | 4358 | 2138 | 2000 | Rebuild Magunden-Pastoria 230 kV line (9 yrs) | 66 | Solar
Antelope-Neenach Constraint | Antelope/Bailey/Pastoria area | On-Peak, Off-Peak | 0 | 2000 | Reconductor Antelope-Bailey 66 kV lines (2 yrs) | 100 | 0 | 15 | Bailey-Neenach-Westpac 66 kV line upgrade | 45 | Solar
SCE Metro Interconnection Area Constraints
Hinson - Del Amo Constraint | LA Basin | On-Peak | 2700 | 800 | Upgrade the Hinson - Del Amo 220 kV Transmission Line (27 months) | 28 | 2700 | N/A | N/A | N/A | Solar
SCE Metro Area Default Constraint | LA Basin | None | 13500 | N/A | N/A | - | 13500 | N/A | N/A | N/A | Solar
SCE North of Lugo (NOL) Interconnection Area Constraints
Control to Inyokern area constraint | Inyokern_North | On-Peak | 0 | 186 | Build a new, series compensated Control-Inyokern 115 kV line and upgrade Inyo Phase Shifter (105 months) | 329 | 120 | N/A | N/A | N/A | Solar
South of Kramer Area Constraint | Inyokern_North_Kramer Victor | On-Peak | 456 | N/A | Approved Project: Convert Kramer - Victor 115 kV lines to 230 kV (120 months) | N/A | 1190 | N/A | N/A | N/A | Solar
Victor to Lugo Area Constraint | Inyokern_North_Kramer Victor | On-Peak | 1034 | N/A | Approved project:Re-conductor the four Lugo-Victor 230 kV lines (54 months) | N/A | 1878 | N/A | N/A | N/A | Solar
Lugo Transformer Area Constraint | Inyokern_North_Kramer, Victor, Pisgah | On-Peak | 1328 | N/A | Approved project: Add a third 500/230 kV transformer at Lugo Substation (54 months) | N/A | 2427 | N/A | N/A | N/A | Solar
Calcite to Lugo Area Constraint | Pisgah | On-Peak | 297 | 1046 | Rebuild Calcite-Lugo 220 kV Transmission Line (105 months) | 239 | 552 | N/A | N/A | N/A | Solar
SCE Eastern Interconnection Area Constraints
Colorado River 500/230 kV Constraint | Colorado River 230 kV | On-Peak, Off-Peak | 1160 | 1370 | New Colorado River No. 3 500/230 kV transformer (4 years) | 67 | 2202 | 1299 | Same as ADNU | 67 | Solar
DCRT Constraint | Cielo Azul, Delaney | On-Peak | 2300 | 3000 | New Cielo Azul - Colorado River No. 2 500 kV line, Upgrade the series cap on Cielo Azul - Colorado River No.1 500 kV line to match the conductor rating (6 years) | 463 | 2300 | N/A | N/A | N/A | Solar
Devers-Red Bluff Constraint | SCE Eastern (east of Red Bluff), East of Pisgah, and SDG&E areas | On-Peak, Off-Peak | 6665 | N/A | Approved projects: Devers-Red Bluff 500 kV 1 and 2 Line Upgrade (2028) and Southern Area Reinforcement Project (2034) | N/A | 7860 | N/A | Approved projects: Devers-Red Bluff 500 kV 1 and 2 Line Upgrade (2028) and Southern Area Reinforcement Project (2034) | N/A | Solar
Eagle Mountain Constraint | Eagle Mountain, Julian Hinds, Mirage | On-Peak | 0 | 600 | New Devers-Julian Hinds 220 kV line (10 years) | 1182 | 392 | N/A | N/A | N/A | Solar
Etiwanda-Rancho Vista Constraint | SCE Eastern area | On-Peak | 4824 | 3350 | Upgrade Etiwanda-Rancho Vista No. 1 & No. 2 220 kV lines, New Etiwanda-Rancho Vista No. 3 220 kV line (3 years) | 89 | 7313 | N/A | N/A | N/A | Solar
Red Bluff 500/230 kV Constraint | Red Bluff 230 kV | On-Peak, Off-Peak | 1450 | 1200 | New Red Bluff No. 3 500/230 kV transformer (4 years) | 69 | 1603 | 1200 | Same as ADNU | 69 | Solar
Serrano-Alberhill-Valley Constraint | SCE Eastern and SDG&E areas | On-Peak, Off-Peak | 8173 | N/A | Approved projects: • Southern Area Reinforcement Project (2034) • Devers-Valley 500 kV 1 Line Upgrade (2028) • Serrano-Alberhill-Valley 500 kV 1 Line Upgrade (2028) • San Bernardino-Etiwanda 230 kV 1 Line Upgrade (2031) • San Bernardino-Vista 230 kV 1 Line Upgrade (2028) • Vista-Etiwanda 230 kV 1 Line Upgrade (2031) • Mira Loma-Mesa 500kV Underground Third Cable (2026) | N/A | 11704 | N/A | Approved projects: • Southern Area Reinforcement Project (2034) • Devers-Valley 500 kV 1 Line Upgrade (2028) • Serrano-Alberhill-Valley 500 kV 1 Line Upgrade (2028) • San Bernardino-Etiwanda 230 kV 1 Line Upgrade (2031) • San Bernardino-Vista 230 kV 1 Line Upgrade (2028) • Vista-Etiwanda 230 kV 1 Line Upgrade (2031) • Mira Loma-Mesa 500kV Underground Third Cable (2026) | N/A | Solar
East of Pisgah (EOP) Interconnection Area Constraints (SCE, GLW, VEA)
GLW 230kV area constraint | VEA 138kV and GLW 230kV buses | On-Peak, Off-Peak | 3372 | N/A | GLW Core Upgrade and Beatty 230kV Project (2022-23 TPP) (2027) | N/A | 3642 | N/A | N/A | N/A | Solar
Sloan Canyon - Eldorado 500 kV constraint | VEA 138kV, GLW 230kV and Eldorado 230kV buses | On-Peak | 4032 | N/A | N/A | N/A | 4302 | N/A | N/A | N/A | Solar
Lugo - Victorville area constraint | East of Pisgah, SCE Eastern,SDG&E and SCE Northern areas | On-peak, Off-Peak | 10105 | 6800 | Eldorado - Lugo 500kV No.2 line (10 years) | 2165 | 12605 | 6800 | Same as ADNU | 2165 | Solar
SDG&E Interconnection Area Constraints
Capistrano-San Onofre 230 kV constraint | SDGE local area | On-peak | 1324 | 920 | Capistrano-San Onofre 230 kV upgrade (60 months) | 58.1 | 1324 | N/A | N/A | N/A | N/A
Chicarita 138 kV constraint | Baja, Imperial, SDGE local area | On-peak | 224 | 700 | Chicarita 138 kV Upgrades (48 months) | 100 | 224 | N/A | N/A | N/A | N/A
El Cajon 69 kV constraint | SDGE local area | On-peak | 406 | 547 | El Cajon 69 kV Upgrade (48 months) | 14.7 | 406 | N/A | N/A | N/A | N/A
Miguel 69 kV constraint | SDGE local area | On-peak | 231 | 431 | Miguel 69 kV upgrades (48 months) | 671.054 | 231 | N/A | N/A | N/A | N/A
Encina - San Luis Rey 230 kV constraint | Baja, Imperial, Arizona, SDGE local area | On-Peak, Off-Peak | 3880 | N/A | Approved Project: Southern California 500 kV Transmission Reinforcement (ISD - 2034); 30 minute emergency rating on Encina Tap-San Luis Rey 230 kV Line | N/A | 7627 | N/A | Same as ADNU | N/A | Solar
San Luis Rey-San Onofre 230 kV line constraint | Baja, Imperial, Arizona, SDGE local area | On-Peak, Off-Peak | 3906 | N/A | Approved Project: Southern California 500 kV Transmission Reinforcement (ISD - 2034); 30 minute emergency rating for San Luis Rey-San Onofre 230 kV #1 line | N/A | 7833 | N/A | Same as ADNU | N/A | Solar
Ocean Ranch 69 kV constraint | SDGE local area | On-peak | 204 | 692 | Ocean Ranch 69 kV upgrade (48 months) | 28.3 | 204 | N/A | N/A | N/A | N/A
Otay Mesa 230 kV constraint | Imperial, SDGE local area | On-peak | 1175 | 2189 | Otay Mesa 230 kV upgrade (60 months) | 79.91 | 1175 | N/A | N/A | N/A | N/A
Silvergate - Bay Blvd 230 kV constraint | Baja, Imperial, SDGE local area | On-Peak, Off-Peak | 2717 | N/A | Approved Project: Southern California 500 kV Transmission Reinforcement (ISD - 2034); 2 hour emergency rating on Silvergate-Bay Boulevard 230 kV line | N/A | 4894 | N/A | Same as ADNU | N/A | Solar
Silvergate-Old Town 230 kV constraint | Baja, Imperial, SDGE local area | On-peak | 2369 | N/A | Approved Project: Southern California 500 kV Transmission Reinforcement (ISD - 2034); 30 min emergency rating for Silvergate-Old Town and Silvergate-Old Town Tap 230 kV lines | N/A | 2369 | N/A | N/A | N/A | N/A
Talega 230 kV constraint | SDGE local area | On-peak | 1028 | 2201 | Talega 230 kV Upgrades (60 months) | 210.6 | 1028 | N/A | N/A | N/A | N/A
Trabuco-Capistrano 138 kV constraint | SDGE local area | On-peak | 501 | 556 | Trabuco-Capistrano 138 kV upgrade (48 months) | 103.366 | 501 | N/A | N/A | N/A | N/A
PG&E North of Greater Bay Interconnection Area Constraints
Collinsville-Tesla 500 kV Line | Greater Bay Area, North of Greater Bay Area and PG&E South 500 kV | On-Peak | 3379 | 8645 | 500kV Delevan (144 months) | 2851.848 | 7706 | N/A | N/A | N/A | Wind
Woodland- Davis 115kV line | North of Greater Bay Area | On-Peak | 90.45 | 109 | Reconductor Q653F-Davis 115 kV Line (60 months) | 9.329 | 81 | N/A | N/A | N/A | Wind
Cortina-Eagle Rock 115 kV line | North of Greater Bay Area | On-Peak | 971 | 50 | Re-conductor Q1284 Sw Sta-Lower Lake Sw Sta/Eagle Rock 115 kV Line (Q1284 Sw Sta-Cache Jct 1) (60 months) | 50 | 1422 | N/A | N/A | N/A | Wind
Bell-Placer 115kV Line | North of Greater Bay Area | On-Peak | 347 | 480 | Re-conductor Higgins-Bell and Bell-Placer 115 kV Lines (120 months) | 185 | 379 | N/A | N/A | N/A | Wind
Carberry-Round Mountain 230kV Line | North of Greater Bay Area | On-Peak | 15 | 26 | Re-conductor Pit 3-Carberry and Carberry-Round mountain 230 kV Lines (84 months) | 180 | 15 | 25 | Same as ADNU | 180 | Wind
Rocklin-Pleaseant grove 115kV line | North of Greater Bay Area | On-Peak | 50 | 707 | Re-conductor Rio Oso-Lincoln 115 kV Line and Lincoln-Pleasant Grove 115 kV Line (72 months) | 125 | 96 | N/A | N/A | N/A | Wind
Bellota-Weber 230kV line | Greater Bay Area, North of Greater Bay Area and Fresno | On-Peak | 1661 | 460 | Subacco (120 months) | 400 | 2539 | N/A | N/A | N/A | Wind
Rio Oso-Brighton 230kV line |  | On-Peak | 423 | 574 |  |  | 463 | N/A | N/A | N/A | Wind
Rio Oso-Lockeford 230kV line |  | On-Peak | 1042.47 | 485 |  |  | 975 | N/A | N/A | N/A | Wind
PG&E Greater Bay Interconnection Area Constraints
Dumbarton-Newark 115 kV line | Greater Bay Area and North of Greater Bay Area | On-Peak | 1290 | N/A | Approved New Collinsville 500/230 kV Substation Project (2028) | N/A | 3728 | N/A | N/A | N/A | Wind
Eastshore-San Mateo 230 kV line |  | On-Peak | 2146 | N/A |  |  | 4811 | N/A | N/A | N/A | Wind
Lakeville-Ignacio 230 kV line |  | On-Peak | 2257 | N/A |  |  | 768 | N/A | N/A | N/A | Wind
Sobrante-Moraga 230 kV line |  | On-Peak | 3140 | N/A |  |  | 5136 | N/A | N/A | N/A | Wind
Windmaster-Delta pumps 230 kV line | Greater Bay Area and North of Greater Bay Area | On-Peak | 546 | 6034 | Contra Costa to Tesla and Newark 230 kV lines and Birds Landing series reactors( Bay Area ADNU) (86 months) | 417.332 | 3673 | N/A | N/A | N/A | Wind
Contra Costa- Windmaster 230 kV line |  | On-Peak | 1233 | 5601 |  |  | 3667 | N/A | N/A | N/A | Wind
Tesla-Tracy-Pump 230 kV line #2 |  | On-Peak | 4574 | 3521 |  |  | 10136 | N/A | N/A | N/A | Wind
Contra Costa #1 115kV Line | Greater Bay Area | On-Peak | 32 | 131 | Contra Costa 115kV, 60kV reconductors and Bank Replacement (120 months) | 185 | 77 | N/A | N/A | N/A | Wind
Kasson Jct-Heinz 115 kV line | Greater Bay Area, North of Greater Bay Area and Fresno | On-Peak | 298 | 1255 | Nikola (216 months) | 1700 | 495 | N/A | N/A | N/A | Wind
Newark-Newark Distribution 115 kV line |  | On-Peak | 8054 | 831 |  |  | 7290 | N/A | N/A | N/A | Wind
Tesla-Bellota 230 kV line |  | On-Peak | 3154 | 300 |  |  | 4254 | N/A | N/A | N/A | Wind
Eight Mile-Tesla 230 kV line |  | On-Peak | 926 | 163 |  |  | 3909 | N/A | N/A | N/A | Wind
Grant - Eastshore #2 line 115 kV | Greater Bay Area | On-Peak | 962.9 | 290 | Reconductor 1869-Eastshore #1 and #2 115 kV lines (84 months) | 125 | 1220 | N/A | N/A | N/A | Wind
Salado-Crow Creek Sw Sta 60 kV line | Greater Bay Area | On-Peak | 102.97 | 74 | Reconductor Salado 115kV and 60kV Area (144 months) | 400 | 102.97 | N/A | N/A | N/A | Wind
Tesla-Salado 115 kV line |  | On-Peak | 178.92 | 70 |  |  | 180 | N/A | N/A | N/A | Wind
Morganhill-Metcalf 115kV Line | Greater Bay Area | On-Peak | 382 | 712 | Metcalf-Morgan Hill 115kV reconductoring (144 months) | 380 | 273 | N/A | N/A | N/A | Wind
Tesla-Tracy Pump 230 kV Line #1 | Greater Bay Area and North of Greater Bay Area | On-Peak | 9287 | 4344 | Re-conductor 1883 Sw Sta-Tracy Pmp (2.9 miles) (60 months) | 25 | 9538 | N/A | N/A | N/A | Wind
Birds Landing-Contra Costa 230kV Line | Greater Bay Area and North of Greater Bay Area | On-Peak | 656 | 1766 | New double circuit line from Vaca-Contra Costa 230 kV (144 months) | 700 | 1176 | N/A | N/A | N/A | Wind
PG&E Kern Interconnection Area Constraints
Cal Flat-Gates 230 kV line | Kern, Los Padres | On-Peak, Off-Peak | 927 | 1418 | Morro Bay Looping (98 months) | 1008.032 | 1005 | 230 | Same as ADNU | 1008.032 | Solar
Gates-Arco 230 kV Line | Kern | On-Peak, Off-Peak | 1562 | 16891 | Re-conductor and reconfigure Gates-Arco-Midway 230 kV Lines (144 months) | 940 | 1226 | 962 | Same as ADNU | 940 | Solar
Smyrna-Atwell Jct 115kV Line | Kern | On-Peak, Off-Peak | 231 | 687 | Alpaugh-Semitropic Reconductor(96 months) | 220 | 144 | 632 | Same as ADNU | 220 | Solar
Kern 230/115kV TB #4 | Kern | On-Peak | 1912 | 179 | Add New Kern 230/115kV Transformer Bank ( 54 months) | 30 | 1928 | N/A | N/A | N/A | Solar
Maricopa-Copus 70 kV line | Kern | On-Peak, Off-Peak | 94.45 | 206 | Reconductor Kern-Old River 115 and 70 kV (132 months) | 620 | 58 | 67.7 | Same as ADNU | 620 | Solar
Midway-Taft 115 kV line | Kern | On-Peak | 17.78 | 9 |  |  | 270 | N/A |  |  | Solar
Kern-Tevis-Stockdale-Lamont 115kV line | Kern | On-Peak, Off-Peak | 184.8 | 367 | Reconductor Kern-Stockdale-Lamont 115 kV (84 months) | 120 | 109 | 106.58 | Same as ADNU | 120 | Solar
Midway 230/115kV TB #3 | Kern | On-Peak, Off-Peak | 1592 | 784 | Add new Midway 230/115 kV Transformer Bank (96 months) | 150 | 1377 | 1477 | Same as ADNU | 150 | Solar
Semitropic-Midway 115kV Line | Kern | On-Peak, Off-Peak | 240 | 637 | Reconductor Semitropic-Midway-Kern 115 kV and 70 kV Lines (144 months) | 760 | 255 | 475 | Same as ADNU | 760 | Solar
Midway-Buena Vista Jct 230kV Line | Kern | On-Peak | 471 | 234 | Reconductor Midway-Q2011 230 kV Line (72 months) | 100 | 471 | N/A | Same as ADNU | 100 | Solar
PG&E Fresno Interconnection Area Constraints
Gates 500/230kV TB #12 | Fresno, Kern | On-Peak, Off-Peak | 5406 | 14825 | Gates Bank 500/230kV Bank #13 (48 months) | 35 | 3581 | 6843 | Same as ADNU | 35 | Solar
Gates 500/230kV TB #11 | Fresno, Kern | On-Peak, Off-Peak | 5336.9 | 10038 |  |  | 5027 | 6343 |  |  | Solar
Gates 230/70kV TB #5 | Fresno | On-Peak, Off-Peak | 300.67 | 47 | New Gates #6 230/70kV (96 months) | 110 | 272 | 390 | Same as ADNU | 110 | Solar
Tranquility-Helm 230kV Line | Fresno | On-Peak, Off-Peak | 2921 | 2274 | Gregg 500kV (180 months) | 1500 | 2777 | 607 | Same as ADNU | 1500 | Solar
Dairyland-Chowchilla 115kV Line | Fresno | On-Peak, Off-Peak | 1110.5 | 1211 | Mendota 230 kV Conversion (120 months) | 250 | 1066 | 122 | Same as ADNU | 250 | Solar
Chowchilla-Le grand 115kV Line | Fresno | On-Peak, Off-Peak | 0 | 1211 | Le Grand 230 kV Station Conversion (180 months) | 550 | 158 | 546 | Same as ADNU | 550 | Solar
NEW- Melones-Cottle 230kV line | Fresno | On Peak | 687 | N/A | Approved New Manning 500/230 kV Substation Project (2028) | N/A | 945 | N/A | N/A | N/A | Solar
Los Banos 500/230kV TB | Fresno | On-Peak, Off-Peak | 6411 | N/A |  | N/A | 7216 | N/A | N/A | N/A | Solar
Schindler 115/70kV TB #1 | Fresno | On-Peak, Off-Peak | 0 | 3160 | Manning 115 kV Addition (120 months) | 370 | 50 | 87 | Same as ADNU | 370 | Solar
Panoche- Mendota 115 kV line | Fresno | On-Peak, Off-Peak | 1985 | 2019 |  |  | 1216 | 302 |  |  | Solar
Panoche-Oro Loma 115kV Line | Fresno | On-Peak | 1782 | 588 | Reconductor Oro Loma-Panoche 115 kV Lines (86 months) | 0 | 1903 | N/A | N/A | N/A | Solar
Borden-Storey #1 230kV line | Fresno | On-Peak, Off-Peak | 412 | 1247 | Reconductor Wilson-Storey 230 kV Lines (86 months) | 50 | 780 | 2047 | Reconductor Wilson-Storey 230 kV Lines (86 months) | N/A | Solar
Merced 115/70kV TB#2 | Fresno | On-Peak, Off-Peak | 122 | 358 | Replace Bank, and Reconductor Lines at Merced (144 months) | 135 | 156 | 291 | Same as ADNU | 125 | Solar
Helm 230/70kV TB #1 | Fresno | On-Peak, Off-Peak | 38 | 60 | Helm 230/70 kV Transformer Bank replacement (84 months) | 330 | 128 | 226 | Same as ADNU | 135 | Solar
Oro Loma-El Nido 115kV Line | Fresno | On-Peak, Off-Peak | 528 | 3192 | Oro-loma- El nido-Wilson Reconductor (120 months) | 830 | 308 | 65 | Same as ADNU | 330 | Solar
Diablo-Gates 500 kV line | Kern, Fresno | On-Peak, Off-Peak | 5161 | 4125 | New Diablo-Midway #4 500 kV Line (98 months) |  | 5581 | 4125 | Same as ADNU | 830 | Solar
Mustang-Henrietta 230 kV line | Fresno | On-Peak | 5581 | 2479 |  | 214.062 | 3417+2200 | N/A |  |  | Solar
Gates-Panoche 230 kV #1 and #2 Lines | Fresno | On-Peak | 4562 | 8379 | Reconductor Gates-Panoche #1 and #2 230 kV Lines (86 months) | N/A | 2389+2200 | N/A | N/A | N/A | Solar
NEW-Metcalf-Mosslanding 500kV | Fresno | On-Peak | 1666 | N/A | (72 months) | 200 | 6083 | N/A | N/A | N/A | Solar
* The transmission capability estimates are based on the resource-type specific output assumptions that are used in deliverbility studies rather than the resources’ installed capacity. The values can be translated into any combination of resource types by applying the currently applicable deliverability study resource output factor.
**The transmission capability estimates are over and above the resource amounts that were online as at January 1, 2024. The CPUC will need to adjust the estimates to account for resources that came online since then. Retirement of Diablo Canyon is accounted for in the estimates assuming the replacements are at the same or similar location