## READ_ME
CAISO PUBLIC
1. The transmission plan capability, allocated TPD and available TPD are based on the resource-type specific output assumptions that are used in deliverability studies rather than the resources’ installed capacity.
2. The transmission plan capability and available TPD have been calcuated after modeling as imports and effectively reserving deliverability for out-of-CAISO long lead-time generation resources specified in the Table 1-1 of the 2025-2026 Transmission Plan.
3. Reserved deliverability at the locations and amounts as identified in the Table 1-1 of the 2025-2026 Transmission Plan are included in the transmission plan capability and allocated TPD . 4. Future reservations at the locations and amounts as identified in the Table 1-1 of the 2025-2026 Transmission Plan are included in the available TPD.
5. The available TPD also includes in-state geothermal reservation at the following locations and amounts as included in the CPUC base portfolio for 2025-2026 TPP: 400 MW at Beatty 230 kV, 28 MW at Cloverdale 115 kV, 22 MW at Eagle Rock (PG&E) 115 kV, 54 MW at Fulton 230 kV and 20 MW at Geysers 17 230 kV.

## Northern_Substation_List_Matrix
CAISO PUBLIC
PG&E NGBA | TPD ZONE
PG&E GBA | TPD ZONE
PG&E FRESNO | TPD ZONE
PG&E KERN | TPD ZONE
|  |  | PG&E North of Greater Bay Area Constraints | PG&E Greater Bay Area Constraints | [6 empty] | PG&E Kern Area Constraints |  |  | PG&E Fresno Area Constraints
POI Name/Short Description (Point of Delivery to CAISO-Controlled Grid for WDATs, etc.) & kV | Interconnection Study Area | Number of Constraints | Collinsville-Tesla 500 kV Area Constraint | Bellota Area Constraint | Bay Area Constraint | Tesla-Westley 230kV Area Constraint | Vaca – Contra Costa Area Constraint | Lockeford 230 kV Area Constraint | Banta 115 kV Area Constraint | Tesla 115 kV Area Constraint | Harlan - Manning 500 kV Area Constraint | Gates-Arco-Midway 230 kV Area Constraint | Bitterwater- Buena Vista 230kV kV Area Constraint | Gates 500/230 kV Transformer Area Constraint | Gates - Manning 500 kV Area Constraint | Gregg 230 kV Area Constraint | Cottle 230 kV Area Constraint | Mustang- Henrietta 230 kV Area Constraint
Transmission Plan Capability |  |  | 4198 | 0 | 1392 | 1166 | 1571 | 760 | 218 | 218 | 5320 | 1568 | 187 | 4467 | 7097 | 0 | 485 | 4530
Allocated TPD |  |  | 4046 | 0 | 1392 | 1166 | 1571 | 760 | 218 | 218 | 5320 | 1568 | 187 | 4382 | 7097 | 0 | 400 | 4530
Available TPD |  |  | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 85 | 0
1-Number of POI behind Constraint |  |  | 231 | 24 | 26 | 30 | 46 | 23 | 21 | 21 | 55 | 74 | 24 | 180 | 102 | 36 | 61 | 12
7th STANDARD 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
ADOBE SW STA 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
AIRWAYS 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
ALHAMBRA 115 kV | PG&E GBA | 1 | √
ALMADEN 60 kV (TPD limit 93 MW based on injection transfer limit assessment) | PG&E GBA | 0
ALPAUGH 115 kV | PG&E FRESNO | 4 | [8 empty] | √ | √ |  | √ | √
Alpaugh-Smryna 115 kV line | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
ALTO 60 kV | PG&E NGBA | 1 | √
AMES 115 kV (TPD limit 212 MW based on injection transfer limit assessment) | PG&E GBA | 0
AMES DISTRIBUTION 115 kV (TPD limit 260 MW based on injection transfer limit assessment) | PG&E GBA | 0
APPLE HILL 115 kV | PG&E NGBA | 1 | √
APPLIED MATERIALS SW STA 115 kV (TPD limit 294 MW based on injection transfer limit assessment) | PG&E GBA | 0
ARCATA 60 kV | PG&E NGBA | 1 | √
ARCO 230 kV | PG&E KERN | 4 | [9 empty] | √ |  | √ | √ |  |  | √
ARCO 70 kV | PG&E KERN | 4 | [9 empty] | √ |  | √ | √ |  |  | √
Arco-Carneras 70 kV Line | PG&E KERN | 4 | [9 empty] | √ |  | √ | √ |  |  | √
Arco-Twisselman 70 kV Line | PG&E KERN | 4 | [9 empty] | √ |  | √ | √ |  |  | √
ASHLAN AVE 230 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
ATASCADERO 70 kV | PG&E KERN | 2 | [11 empty] | √ | √
ATLANTIC 115 kV | PG&E NGBA | 1 | √
ATLANTIC 230 kV | PG&E NGBA | 1 | √
ATLANTIC 60 kV | PG&E NGBA | 1 | √
ATWATER 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
AVENAL TAP 70 KV LINE | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ |  |  | √
BAHIA 230 kV | PG&E NGBA | 1 | √
BAIR 115 kV (TPD limit 414 MW based on injection transfer limit assessment) | PG&E GBA | 0
BAIR 60 kV (TPD limit 149 MW based on injection transfer limit assessment) | PG&E GBA | 0
BAKERSFIELD 230 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
BARTON 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
BAY MEADOWS 115 kV (TPD limit 211 MW based on injection transfer limit assessment) | PG&E GBA | 0
BELDEN PH 230 kV | PG&E NGBA | 1 | √
BELL 115 kV | PG&E NGBA | 1 | √
BELLEVUE 115 kV | PG&E NGBA | 1 | √
BELLOTA 115 kV | PG&E GBA | 3 |  | √ |  |  |  | √ | √
BELLOTA 230 kV | PG&E GBA | 1 | [5 empty] | √
BELMONT 115 kV (TPD limit 303 MW based on injection transfer limit assessment) | PG&E GBA | 0
BENTON 60 kV | PG&E NGBA | 1 | √
BIOLA 70 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
BIRDS LANDING SW STA 230 kV | PG&E GBA | 3 | √ |  | √ |  | √
BITTERWATER SW STA 230 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
BOGUE 115 kV | PG&E NGBA | 1 | √
BOLINAS 60 kV | PG&E NGBA | 1 | √
BORDEN 230 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
BORDEN 70 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
BRENTWOOD 230 kV | PG&E GBA | 2 | √ |  | √
BRIDGEVILLE 115 kV | PG&E NGBA | 1 | √
BRIDGEVILLE 60 kV | PG&E NGBA | 1 | √
BRIGHTON 115 kV | PG&E NGBA | 1 | √
BRIGHTON 230 kV | PG&E NGBA | 1 | √
BRITTON 115 kV (TPD limit 325 MW based on injection transfer limit assessment) | PG&E GBA | 0
BUCKS CREEK PH 230 kV | PG&E NGBA | 1 | √
BULLARD 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
BURLINGAME 115 kV (TPD limit 277 MW based on injection transfer limit assessment) | PG&E GBA | 0
BUTTE 115 kV | PG&E NGBA | 1 | √
BUTTE 60 kV | PG&E NGBA | 1 | √
CALIENTE SW STA 230 kV | PG&E KERN | 3 | [9 empty] | √ |  | √ | √
CALIFORNIA AVE 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
CALIFORNIA FLATS SW STA 230 kV | PG&E FRESNO | 2 | [11 empty] | √ | √
CALLENDER SW STA 115 kV | PG&E KERN | 2 | [11 empty] | √ | √
CAMP EVERS 115 kV (TPD limit 188 MW based on injection transfer limit assessment) | PG&E GBA | 0
CARBERRY SW STA 230 kV | PG&E NGBA | 1 | √
CARBONA 60 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
CARIBOU PH #1 60 kV | PG&E NGBA | 1 | √
CARIBOU PH #2 115 kV | PG&E NGBA | 1 | √
CARIBOU PH #2 230 kV | PG&E NGBA | 1 | √
CARQUINEZ 115 kV | PG&E NGBA | 1 | √
CASALOMA 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
CASALOMA 230 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
CASCADE 115 kV | PG&E NGBA | 1 | √
CASCADE 60 kV | PG&E NGBA | 1 | √
Cascade-Cottonwood 115 kV Line | PG&E NGBA | 1 | √
CASTRO VALLEY 230 kV | PG&E GBA | 1 | √
CAYETANO 230 kV | PG&E GBA | 2 | √ |  | √
Cayetano-Lonetree 230 kV Line at USWP Jackson 230 kV | PG&E GBA | 2 | √ |  | √
CAYUCOS 70 kV | PG&E KERN | 2 | [11 empty] | √ | √
CHARCA 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
CHEROKEE 60 kV | PG&E GBA | 1 | [5 empty] | √
CHICO A 60 kV | PG&E NGBA | 1 | √
CHOWCHILLA 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
CHRISTIE 115 kV | PG&E GBA | 1 | √
CHRISTIE 60 kV | PG&E GBA | 1 | √
CLAREMONT K 115 kV | PG&E GBA | 1 | √
CLAY 60 kV | PG&E GBA | 1 | [5 empty] | √
CLAYTON 115 kV | PG&E GBA | 1 | √
CLEAR LAKE 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
CLOVERDALE 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
CLOVIS 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
COALINGA #1 70 kV | PG&E FRESNO | 3 | [11 empty] | √ | √ |  |  | √
COALINGA #2 70 kV | PG&E FRESNO | 2 | [11 empty] | √ | √
COBURN 230 kV | PG&E GBA | 1 | [11 empty] | √
COBURN 60 kV | PG&E GBA | 1 | [11 empty] | √
COLEMAN PH 60 kV | PG&E NGBA | 1 | √
COLGATE PH 230 kV | PG&E NGBA | 1 | √
COLLINSVILLE 230 kV | PG&E GBA | 1 | √
COLLINSVILLE 500 kV | PG&E GBA | 1 | √
COLUSA 60 kV | PG&E GBA | 2 | √ |  |  |  | √
CONTRA COSTA 115 kV | PG&E GBA | 2 | √ |  | √
CONTRA COSTA 230 kV | PG&E GBA | 2 | √ |  | √
CONTRA COSTA 60 kV | PG&E GBA | 2 | √ |  | √
CONTRA COSTA PP SW STA 230 kV | PG&E GBA | 2 | √ |  | √
Contra Costa-Delta Pumps 230 kV Line | PG&E GBA | 1 |  |  | √
COOLEY LANDING 115 kV (TPD limit 329 MW based on injection transfer limit assessment) | PG&E GBA | 0
COOLEY LANDING 60 kV (TPD limit 239 MW based on injection transfer limit assessment) | PG&E GBA | 0
COPPERMINE 70 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
COPUS 70 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
Copus-Old River 70 kV Line | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
CORCORAN 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
CORCORAN 70 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
Corcoran-Olive Switching Station 115 kV Line | PG&E FRESNO | 4 | [8 empty] | √ | √ |  | √ | √
CORDELIA 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
CORONA 115 kV | PG&E NGBA | 1 | √
CORTINA 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
CORTINA 230 kV | PG&E NGBA | 2 | √ |  |  |  | √
CORTINA 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
COTATI 60 kV | PG&E NGBA | 1 | √
COTTLE 230 kV | PG&E GBA | 3 | [5 empty] | √ | [7 empty] | √ | √
COTTONWOOD 115 kV | PG&E NGBA | 1 | √
COTTONWOOD 230 kV | PG&E NGBA | 1 | √
COTTONWOOD 60 kV | PG&E NGBA | 1 | √
COUNTRY CLUB 60 kV (TPD limit 146 MW based on injection transfer limit assessment) | PG&E GBA | 0
COYOTE SW STA 230 kV (TPD limit 607 MW based on injection transfer limit assessment) | PG&E GBA | 0
CRAZY HORSE CANYON SW STA 115 kV (TPD limit 420 MW based on injection transfer limit assessment) | PG&E GBA | 0
CRESCENT SW STA 70 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
CRESSEY 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
CRESTA PH 230 kV | PG&E NGBA | 1 | √
CROW CREEK SW STA 60 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
CROWS LANDING 60 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
CURTIS 115 kV | PG&E GBA | 4 |  | √ |  |  |  | √ | √ | √
DAIRYLAND 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
DAVIS 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
DEL MAR 60 kV | PG&E NGBA | 1 | √
DEL MONTE 60 kV (TPD limit 277 MW based on injection transfer limit assessment) | PG&E GBA | 0
DELEVAN 230 kV | PG&E NGBA | 2 | √ |  |  |  | √
Delta Switching Yard-Tesla 230 kV Line | PG&E GBA | 1 |  |  | √
DESCHUTES 60 kV | PG&E NGBA | 1 | √
DIABLO CANYON 230 kV | PG&E KERN | 2 | [11 empty] | √ | √
DIABLO CANYON 500 kV | PG&E KERN | 2 | [8 empty] | √ |  |  |  | √
DINUBA 70 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
DIVIDE 115 kV | PG&E KERN | 2 | [11 empty] | √ | √
DIVIDE 70 kV | PG&E KERN | 2 | [11 empty] | √ | √
DIXON 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
DIXON LANDING 115 kV (TPD limit 335 MW based on injection transfer limit assessment) | PG&E GBA | 0
DOLAN RD 115 kV (TPD limit 94 MW based on injection transfer limit assessment) | PG&E GBA | 0
DRUM #1 PH 115 kV | PG&E NGBA | 1 | √
DUMBARTON 115 kV (TPD limit 241 MW based on injection transfer limit assessment) | PG&E GBA | 0
EAGLE ROCK 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
EAGLE ROCK 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
EAST GRAND 115 kV (TPD limit 392 MW based on injection transfer limit assessment) | PG&E GBA | 0
EAST MARYSVILLE 115 kV | PG&E NGBA | 1 | √
EAST NICOLAUS 115 kV | PG&E NGBA | 1 | √
EAST NICOLAUS 60 kV | PG&E NGBA | 1 | √
EASTSHORE 115 kV | PG&E GBA | 1 | √
EASTSHORE 230 kV (TPD limit 297 MW based on injection transfer limit assessment) | PG&E GBA | 0
EDENVALE 115 kV (TPD limit 335 MW based on injection transfer limit assessment) | PG&E GBA | 0
EDES 115 kV | PG&E GBA | 1 | √
EGBERT 230 kV (TPD limit 392 MW based on injection transfer limit assessment) | PG&E GBA | 0
EIGHT MILE 230 kV (TPD limit 330 MW based on injection transfer limit assessment) | PG&E GBA | 0
EL CAPITAN 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
EL CERRITO G 115 kV | PG&E GBA | 1 | √
EL DORADO PH 115 kV | PG&E NGBA | 1 | √
EL PATIO 115 kV (TPD limit 210 MW based on injection transfer limit assessment) | PG&E GBA | 0
ELECTRA PH 230 kV | PG&E GBA | 1 | [5 empty] | √
ESTRELLA 230 kV | PG&E KERN | 2 | [11 empty] | √ | √
EUREKA E 60 kV | PG&E NGBA | 1 | √
EVERGREEN 115 kV (TPD limit 237 MW based on injection transfer limit assessment) | PG&E GBA | 0
EVERGREEN 60 kV (TPD limit 96 MW based on injection transfer limit assessment) | PG&E GBA | 0
EXCELSIOR SW STA 115 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
EXCHEQUER PH 70 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
FAIRHAVEN 60 kV | PG&E NGBA | 1 | √
FAIRWAY 115 kV | PG&E KERN | 2 | [11 empty] | √ | √
FAMOSO 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
FELLOWS 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
FERN ROAD 500 kV | PG&E NGBA | 1 | √
FIGARDEN 230 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
FINK SW STA 230 kV | PG&E FRESNO | 1 |  |  |  | √
FITCH MOUNTAIN 60 kV | PG&E NGBA | 1 | √
FIVE POINTS SW STA 70 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
FMC 115 kV (TPD limit 252 MW based on injection transfer limit assessment) | PG&E GBA | 0
FORT ORD 60 kV (TPD limit 67 MW based on injection transfer limit assessment) | PG&E GBA | 0
FREMONT 115 kV (TPD limit 288 MW based on injection transfer limit assessment) | PG&E GBA | 0
FRENCH CAMP 60 kV | PG&E GBA | 1 | [5 empty] | √
FROGTOWN 115 kV | PG&E GBA | 4 |  | √ |  |  |  | √ | √ | √
FULTON 115 kV | PG&E NGBA | 1 | √
FULTON 230 kV | PG&E NGBA | 1 | √
FULTON 60 kV | PG&E NGBA | 1 | √
GALLO 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
GARBERVILLE 60 kV | PG&E NGBA | 1 | √
GATES 230 kV | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ |  |  | √
GATES 500 kV | PG&E FRESNO | 1 | [12 empty] | √
GATES 70 kV | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ |  |  | √
Gates-Midway 230 kV Line | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ |  |  | √
Gates-Templeton 230 kV Line | PG&E FRESNO | 2 | [11 empty] | √ | √
Geysers #12-Fulton 230 kV Line | PG&E NGBA | 1 | √
GEYSERS #3 & #4 PP 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
GEYSERVILLE 60 kV | PG&E NGBA | 1 | √
GLASS 70 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
GLENN 230 kV | PG&E NGBA | 2 | √ |  |  |  | √
GLENN 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
GLENWOOD 60 kV (TPD limit 103 MW based on injection transfer limit assessment) | PG&E GBA | 0
GOLD HILL 115 kV | PG&E NGBA | 1 | √
GOLD HILL 230 kV | PG&E NGBA | 1 | √
GRAND ISLAND 115 kV | PG&E NGBA | 1 | √
GRANT 115 kV | PG&E GBA | 1 | √
GREEN VALLEY 115 kV (TPD limit 276 MW based on injection transfer limit assessment) | PG&E GBA | 0
GREENBRAE 60 kV | PG&E NGBA | 1 | √
Greenleaf #1 115 kV Tap | PG&E NGBA | 1 | √
Greenleaf #2 60 kV Tap | PG&E NGBA | 1 | √
GREGG 230 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
GUERNSEY 70 kV | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ | √
GWF HANFORD SW STA 115 kV | PG&E FRESNO | 2 | [9 empty] | √ |  | √
HALF MOON BAY 60 kV (TPD limit 63 MW based on injection transfer limit assessment) | PG&E GBA | 0
HALSEY PH 60 kV | PG&E NGBA | 1 | √
HAMMER 60 kV (TPD limit 96 MW based on injection transfer limit assessment) | PG&E GBA | 0
HAMMONDS 115 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
HARDING 60 kV | PG&E GBA | 1 | [5 empty] | √
HARLAN 500 kV | PG&E FRESNO | 1 | [8 empty] | √
HARRIS 60 kV | PG&E NGBA | 1 | √
HARTER 60 kV | PG&E NGBA | 1 | √
HARTLEY 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
HELM 230 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
HELM 70 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
HENRIETTA 115 kV | PG&E FRESNO | 3 | [9 empty] | √ |  | √ | √
HENRIETTA 230 kV | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ | √
HENRIETTA 70 kV | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ | √
Henrietta-Guernsey 70 kV Line | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ | √
HERDLYN 60 kV | PG&E GBA | 1 |  |  |  | √
HERNDON 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
HERNDON 230 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
HICKS 230 kV (TPD limit 26 MW based on injection transfer limit assessment) | PG&E GBA | 0
HIGGINS 115 kV | PG&E NGBA | 1 | √
HIGHLANDS 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
HOPLAND 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
HOPLAND 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
HORSESHOE 115 kV | PG&E NGBA | 1 | √
HUMBOLDT 115 kV | PG&E NGBA | 1 | √
HUMBOLDT 60 kV | PG&E NGBA | 1 | √
HUMBOLDT BAY PP 60 kV | PG&E NGBA | 1 | √
HUMBOLDT 500 kV | PG&E NGBA | 1 | √
HURON 70 kV | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ |  |  | √
IGNACIO 115 kV | PG&E NGBA | 1 | √
IGNACIO 230 kV | PG&E NGBA | 1 | √
IGNACIO 60 kV | PG&E NGBA | 1 | √
JAMES B BLACK PH 230 kV | PG&E NGBA | 1 | √
JANES CREEK 60 kV | PG&E NGBA | 1 | √
JARVIS 115 kV (TPD limit 270 MW based on injection transfer limit assessment) | PG&E GBA | 0
JAYNE SW STA 70 kV | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ |  |  | √
JEFFERSON 230 kV (TPD limit 499 MW based on injection transfer limit assessment) | PG&E GBA | 0
JEFFERSON 60 kV (TPD limit 201 MW based on injection transfer limit assessment) | PG&E GBA | 0
JESSUP 115 kV | PG&E NGBA | 1 | √
KASSON 115 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
KASSON 60 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
KEARNEY 230 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
KEARNEY 70 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
KELSO 230 kV | PG&E GBA | 1 |  |  | √
Kelso-Tesla 230 kV Line | PG&E GBA | 1 |  |  | √
KENT SW STA 70 kV | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ | √
KERCKHOFF #1 PH 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
KERCKHOFF #2 PH 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
KERMAN 70 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
KERN OIL 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
KERN PP 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
KERN PP 230 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
KERN PP 70 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
Kern-Old River #1 70 kV line | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
KING CITY 60 kV | PG&E GBA | 1 | [11 empty] | √
KINGSBURG 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
KINGSBURG 70 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
Kingsburg-Henrietta 115 kV Line | PG&E FRESNO | 2 | [9 empty] | √ |  | √
KIRKER 115 kV | PG&E GBA | 1 | √
KONOCTI 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
LAKEVIEW 70 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
LAKEVILLE 115 kV | PG&E NGBA | 1 | √
LAKEVILLE 230 kV | PG&E NGBA | 1 | √
LAKEVILLE 60 kV | PG&E NGBA | 1 | √
LAKEWOOD 115 kV | PG&E GBA | 1 | √
LAMBIE SW STA 230 kV | PG&E NGBA | 3 | √ |  | √ |  | √
LAMMERS 115 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
LAMONT 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
LAS AGUILAS SW STA 230 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
LAS GALLINAS A 115 kV | PG&E NGBA | 1 | √
LAS POSITAS 230 kV | PG&E GBA | 2 | √ |  | √
LAS POSITAS 60 kV | PG&E GBA | 2 | √ |  | √
LAURELES 60 kV (TPD limit 41 MW based on injection transfer limit assessment) | PG&E GBA | 0
LAWRENCE 115 kV (TPD limit 247 MW based on injection transfer limit assessment) | PG&E GBA | 0
LAYTONVILLE 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
LE GRAND 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
Le Grand-Chowchilla 115 kV Line | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
LEMOORE 70 kV | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ | √
LEPRINO SW STA 115 kV | PG&E FRESNO | 3 | [9 empty] | √ |  | √ | √
LERDO 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
LINCOLN 115 kV | PG&E NGBA | 1 | √
LIVE OAK SW STA 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
LIVERMORE 60 kV | PG&E GBA | 2 | √ |  | √
LIVINGSTON 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
LLAGAS 115 kV (TPD limit 0 MW based on injection transfer limit assessment) | PG&E GBA | 0
LOCKEFORD 115 kV | PG&E GBA | 2 |  | √ |  |  |  | √
LOCKEFORD 230 kV (TPD limit 210 MW based on injection transfer limit assessment) | PG&E GBA | 0
LOCKEFORD 60 kV (TPD limit 186 MW based on injection transfer limit assessment) | PG&E GBA | 0
LOCKHEED #1 SW STA 115 kV (TPD limit 141 MW based on injection transfer limit assessment) | PG&E GBA | 0
LODI 60 kV (TPD limit 184 MW based on injection transfer limit assessment) | PG&E GBA | 0
LOGAN CREEK 230 kV | PG&E NGBA | 2 | √ |  |  |  | √
LONE TREE 230 kV | PG&E GBA | 2 | √ |  | √
LOS BANOS 230 kV | PG&E FRESNO | 1 |  |  |  | √
LOS BANOS 500 kV (TPD limit 1019 MW based on injection transfer limit assessment) | PG&E FRESNO | 0
LOS BANOS 70 kV | PG&E FRESNO | 1 |  |  |  | √
Los Banos-Midway #2 500 kV Line | PG&E FRESNO | 1 | [8 empty] | √
LOS ESTEROS 115 kV (TPD limit 0 MW based on injection transfer limit assessment) | PG&E GBA | 0
LOS ESTEROS 230 kV (TPD limit 0 MW based on injection transfer limit assessment) | PG&E GBA | 0
LOS GATOS 60 kV (TPD limit 88 MW based on injection transfer limit assessment) | PG&E GBA | 0
Lower Lake-Homestake 115 kV Line | PG&E NGBA | 2 | √ |  |  |  | √
LUCERNE 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
MADERA 70 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
MADISON 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
MAGUNDEN 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
MALAGA 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
MANCHESTER 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
MANNING 230 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
MANNING 500 kV (TPD limit 917 MW based on injection transfer limit assessment) | PG&E FRESNO | 0
MANTECA 115 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
MAPLE CREEK 60 kV | PG&E NGBA | 1 | √
Maricopa-Copus 70 kV Line | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
MARTINEZ PP 115 kV | PG&E GBA | 1 | √
MARYSVILLE 60 kV | PG&E NGBA | 1 | √
MCCALL 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
MCCALL 230 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
MCKEE 115 kV (TPD limit 287 MW based on injection transfer limit assessment) | PG&E GBA | 0
MEADOW LANE 115 kV | PG&E GBA | 1 | √
MELONES SW STA 115 kV | PG&E GBA | 4 |  | √ |  |  |  | √ | √ | √
Melones-Curtis 115 kV Line | PG&E GBA | 4 |  | √ |  |  |  | √ | √ | √
MENDOCINO 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
MENDOCINO 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
MENDOTA 115 kV | PG&E FRESNO | 3 |  |  |  | √ | [7 empty] | √ |  |  | √
MENDOTA 70 kV | PG&E FRESNO | 3 |  |  |  | √ | [7 empty] | √ |  |  | √
Mendota-San Joaquin-Helm 70 kV Line | PG&E FRESNO | 3 |  |  |  | √ | [7 empty] | √ |  |  | √
MENLO 60 kV (TPD limit 120 MW based on injection transfer limit assessment) | PG&E GBA | 0
MERCED 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
MERCED FALLS 70 kV | PG&E GBA | 3 | [11 empty] | √ |  | √ | √
MERCY SPRINGS SW STA 70 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
MERIDIAN 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
MESA 115 kV | PG&E KERN | 2 | [11 empty] | √ | √
MESA 230 kV | PG&E KERN | 2 | [11 empty] | √ | √
METCALF 115 kV (TPD limit 337 MW based on injection transfer limit assessment) | PG&E GBA | 0
METCALF 230 kV (TPD limit 2305 MW based on injection transfer limit assessment) | PG&E GBA | 0
METCALF 500 kV (TPD limit 3000 MW based on injection transfer limit assessment) | PG&E GBA | 0
MIDSUN SW STA 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
Midsun-Midway 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
MIDWAY 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
MIDWAY 230 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
MIDWAY 500 kV | PG&E KERN | 2 | [8 empty] | √ |  |  |  | √
Midway-Temblor 115 kV line | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
MILLBRAE 115 kV (TPD limit 276 MW based on injection transfer limit assessment) | PG&E GBA | 0
MILPITAS 115 kV (TPD limit 354 MW based on injection transfer limit assessment) | PG&E GBA | 0
MI-WUK 115 kV | PG&E GBA | 4 |  | √ |  |  |  | √ | √ | √
MONTA VISTA 115 kV (TPD limit 268 MW based on injection transfer limit assessment) | PG&E GBA | 0
MONTA VISTA 230 kV (TPD limit 504 MW based on injection transfer limit assessment) | PG&E GBA | 0
MONTA VISTA 60 kV (TPD limit 268 MW based on injection transfer limit assessment) | PG&E GBA | 0
MONTAGUE 115 kV (TPD limit 356 MW based on injection transfer limit assessment) | PG&E GBA | 0
MORAGA 115 kV | PG&E GBA | 1 | √
MORAGA 230 kV | PG&E GBA | 1 | √
MORGAN HILL 115 kV (TPD limit 0 MW based on injection transfer limit assessment) | PG&E GBA | 0
MORRO BAY SW STA 115 kV | PG&E KERN | 2 | [11 empty] | √ | √
MORRO BAY SW STA 230 kV | PG&E KERN | 2 | [11 empty] | √ | √
MOSHER 60 kV (TPD limit 142 MW based on injection transfer limit assessment) | PG&E GBA | 0
MOSS LANDING PP 115 kV (TPD limit 750 MW based on injection transfer limit assessment) | PG&E GBA | 0
MOSS LANDING PP 230 kV (TPD limit 724 MW based on injection transfer limit assessment) | PG&E GBA | 0
MOSS LANDING PP 500 kV (TPD limit 433 MW based on injection transfer limit assessment) | PG&E GBA | 0
MOUNTAIN VIEW 115 kV (TPD limit 176 MW based on injection transfer limit assessment) | PG&E GBA | 0
MT EDEN 115 kV | PG&E GBA | 1 | √
MUSTANG SW STA 230 kV | PG&E FRESNO | 4 | [9 empty] | √ |  | √ | √ |  |  | √
NAPA 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
NEWARK 115 kV (TPD limit 815 MW based on injection transfer limit assessment) | PG&E GBA | 0
NEWARK 230 kV (TPD limit 150 MW based on injection transfer limit assessment) | PG&E GBA | 0
NEWARK 60 kV | PG&E GBA | 1 |  |  | √
NORD 115 kV | PG&E NGBA | 1 | √
NORTECH 115 kV (TPD limit 0 MW based on injection transfer limit assessment) | PG&E GBA | 0
NORTH DUBLIN 230 kV | PG&E GBA | 2 | √ |  | √
NORTH TOWER 115 kV | PG&E NGBA | 1 | √
NOTRE DAME 115 kV | PG&E NGBA | 1 | √
OAKLAND C (OAKLAND PP) 115 kV | PG&E GBA | 1 | √
OAKLAND D 115 kV | PG&E GBA | 1 | √
OAKLAND J 115 kV | PG&E GBA | 1 | √
OAKLAND L 115 kV | PG&E GBA | 1 | √
OAKLAND X 115 kV | PG&E GBA | 1 | √
OCEANO 115 kV | PG&E KERN | 2 | [11 empty] | √ | √
OLD RIVER 70 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
OLEUM PP 115 kV | PG&E GBA | 1 | √
OLIVE SWITCHING STATION 115 kV | PG&E FRESNO | 4 | [8 empty] | √ | √ |  | √ | √
OLIVEHURST 115 kV | PG&E NGBA | 1 | √
ORCHARD 500 kV | PG&E FRESNO | 1 | [12 empty] | √
OREGON TRAIL 60 kV | PG&E NGBA | 1 | √
ORLAND B 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
ORO LOMA 115 kV | PG&E FRESNO | 3 |  |  |  | √ | [7 empty] | √ |  |  | √
ORO LOMA 70 kV | PG&E FRESNO | 3 |  |  |  | √ | [7 empty] | √ |  |  | √
OROSI 70 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
PACIFICA 60 kV (TPD limit 68 MW based on injection transfer limit assessment) | PG&E GBA | 0
PADRE FLAT SW STA 230 kV | PG&E FRESNO | 1 |  |  |  | √
PALERMO 115 kV | PG&E NGBA | 1 | √
PALERMO 230 kV | PG&E NGBA | 1 | √
PALO ALTO SW STA 115 kV (TPD limit 455 MW based on injection transfer limit assessment) | PG&E GBA | 0
PANAMA 70 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
PANOCHE 115 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
PANOCHE 230 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
Panoche-Schindler #2 115 kV Line | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
PARADISE 115 kV | PG&E NGBA | 1 | √
PARKWAY 230 kV | PG&E NGBA | 1 | √
PASO ROBLES 70 kV | PG&E KERN | 2 | [11 empty] | √ | √
PAUL SWEET 115 kV (TPD limit 240 MW based on injection transfer limit assessment) | PG&E GBA | 0
PEABODY 230 kV | PG&E NGBA | 3 | √ |  | √ |  | √
PEACHTON 60 kV | PG&E NGBA | 1 | √
PEASE 115 kV | PG&E NGBA | 1 | √
PEASE 60 kV | PG&E NGBA | 1 | √
PETALUMA A 60 kV | PG&E NGBA | 1 | √
PIERCY 115 kV (TPD limit 354 MW based on injection transfer limit assessment) | PG&E GBA | 0
PINEDALE 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
PIT #1 PH 230 kV | PG&E NGBA | 1 | √
PIT #1 PH 60 kV | PG&E NGBA | 1 | √
PIT #3 PH 230 kV | PG&E NGBA | 1 | √
Pit1-Cottonwood 230 kV Line | PG&E NGBA | 1 | √
PITTSBURG PP 115 kV | PG&E GBA | 1 | √
PITTSBURG PP 230 kV | PG&E GBA | 1 | √
PLACER 115 kV | PG&E NGBA | 1 | √
PLACER 60 kV | PG&E NGBA | 1 | √
PLACERVILLE 115 kV | PG&E NGBA | 1 | √
PLAINFIELD 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
PLEASANT GROVE 115 kV | PG&E NGBA | 1 | √
POLE LINE 230 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
POTTER VALLEY PH 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
PRUNEDALE 115 kV (TPD limit 110 MW based on injection transfer limit assessment) | PG&E GBA | 0
PUEBLO 115 kV | PG&E NGBA | 1 | √
PUTAH CREEK 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
QUINTO SW STA 230 kV | PG&E FRESNO | 1 |  |  |  | √
RADUM 60 kV | PG&E GBA | 2 | √ |  | √
Rancho Seco-Bellota 230kV Line #1 | PG&E GBA | 1 | [5 empty] | √
RAVENSWOOD 115 kV (TPD limit 682 MW based on injection transfer limit assessment) | PG&E GBA | 0
RAVENSWOOD 230 kV (TPD limit 1259 MW based on injection transfer limit assessment) | PG&E GBA | 0
RED BLUFF 60 kV | PG&E NGBA | 1 | √
REDBUD 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
REDWOOD CITY 60 kV (TPD limit 111 MW based on injection transfer limit assessment) | PG&E GBA | 0
REEDLEY 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
REEDLEY 70 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
Reedley-Dinbua 70 kV Line | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
RICHMOND R 115 kV | PG&E GBA | 1 | √
Rio Dell 60 kV Tap | PG&E NGBA | 1 | √
RIO OSO 115 kV | PG&E NGBA | 1 | √
RIO OSO 230 kV | PG&E NGBA | 1 | √
RIPON 115 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
RIVERBANK 115 kV | PG&E GBA | 4 |  | √ |  |  |  | √ | √ | √
ROB ROY 115 kV (TPD limit 172 MW based on injection transfer limit assessment) | PG&E GBA | 0
ROCK CREEK PH 230 kV | PG&E NGBA | 1 | √
ROSSMOOR 230 kV | PG&E GBA | 1 | √
ROUND MTN 230 kV | PG&E NGBA | 1 | √
ROUND MTN 500 kV | PG&E NGBA | 1 | √
SALADO 115 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
SALADO 60 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
SALINAS 115 kV (TPD limit 654 MW based on injection transfer limit assessment) | PG&E GBA | 0
SALINAS 60 kV (TPD limit 106 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN BENITO 115 kV (TPD limit 199 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN FRAN A (POTRERO PP) 115 kV (TPD limit 3 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN FRAN A (POTRERO PP) 230 kV (TPD limit 437 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN FRAN AIRPORT 115 kV (TPD limit 183 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN FRAN H (MARTIN) 115 kV (TPD limit 932 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN FRAN H (MARTIN) 230 kV (TPD limit 840 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN FRAN P (HUNTERS POINT) 115 kV (TPD limit 694 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN FRAN W (BAYSHORE) 115 kV (TPD limit 4 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN FRAN X (MISSION) 115 kV (TPD limit 396 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN FRAN Y (LARKIN) 115 kV (TPD limit 3 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN FRAN Z (EMBARCADERO) 230 kV (TPD limit 837 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN JOSE A 115 kV (TPD limit 176 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN JOSE B 115 kV (TPD limit 162 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN LEANDRO U 115 kV | PG&E GBA | 1 | √
SAN LUIS OBISPO 115 kV | PG&E KERN | 2 | [11 empty] | √ | √
SAN LUIS OBISPO 70 kV | PG&E KERN | 2 | [11 empty] | √ | √
SAN MATEO 115 kV (TPD limit 1322 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN MATEO 230 kV (TPD limit 1190 MW based on injection transfer limit assessment) | PG&E GBA | 0
SAN MIGUEL 70 kV | PG&E KERN | 2 | [11 empty] | √ | √
SAN PABLO 115 kV | PG&E GBA | 1 | √
SAN RAFAEL 115 kV | PG&E NGBA | 1 | √
SAN RAMON 230 kV | PG&E GBA | 1 | √
SAN RAMON 60 kV | PG&E GBA | 2 | √ |  | √
SANGER 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
SANTA MARIA 115 kV | PG&E KERN | 2 | [11 empty] | √ | √
SANTA NELLA 70 kV | PG&E FRESNO | 1 |  |  |  | √
SANTA ROSA A 115 kV | PG&E NGBA | 1 | √
SANTA TERESA 115 kV (TPD limit 184 MW based on injection transfer limit assessment) | PG&E GBA | 0
SARATOGA 230 kV (TPD limit 103 MW based on injection transfer limit assessment) | PG&E GBA | 0
SCHINDLER 115 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
SCHINDLER 70 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
SCHULTE SW STA 115 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
SEMITROPIC 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
Semitropic-Midway #2 115 kV Line | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
SERRAMONTE 115 kV (TPD limit 107 MW based on injection transfer limit assessment) | PG&E GBA | 0
SHAFTER 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
SHEPHERD 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
SILVERADO 115 kV | PG&E NGBA | 1 | √
SISQUOC 115 kV | PG&E KERN | 2 | [11 empty] | √ | √
SMARTVILLE SW STA 60 kV | PG&E NGBA | 1 | √
SMYRNA 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
Smyrna-Alpaugh 115 kV Line | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
SNEATH LANE 60 kV (TPD limit 143 MW based on injection transfer limit assessment) | PG&E GBA | 0
SOBRANTE 115 kV | PG&E GBA | 1 | √
SOBRANTE 230 kV | PG&E GBA | 1 | √
SOLAR SW STA 230 kV | PG&E KERN | 3 | [9 empty] | √ |  | √ | √
SOLEDAD 115 kV (TPD limit 121 MW based on injection transfer limit assessment) | PG&E GBA | 0
SOLEDAD 60 kV (TPD limit 30 MW based on injection transfer limit assessment) | PG&E GBA | 0
SONOMA A 115 kV | PG&E NGBA | 1 | √
SPAULDING #1 PH 60 kV | PG&E NGBA | 1 | √
SPENCE 60 kV (TPD limit 204 MW based on injection transfer limit assessment) | PG&E GBA | 0
SPI-Lincoln 60 kV tap | PG&E GBA | 1 | √
STAFFORD 60 kV | PG&E NGBA | 1 | √
STAGG 230 kV (TPD limit 257 MW based on injection transfer limit assessment) | PG&E GBA | 0
STANISLAUS PH 115 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
STELLING 115 kV (TPD limit 243 MW based on injection transfer limit assessment) | PG&E GBA | 0
STOCKDALE 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
STOCKDALE 230 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
STOCKTON A 115 kV | PG&E GBA | 2 |  | √ |  |  |  | √
STOCKTON A 60 kV | PG&E GBA | 1 | [5 empty] | √
STONE 115 kV (TPD limit 155 MW based on injection transfer limit assessment) | PG&E GBA | 0
SUISUN 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
SUTTER HOME SWITCHING STATION 60 kV (TPD limit 36 MW based on injection transfer limit assessment) | PG&E GBA | 0
SWIFT 115 kV (TPD limit 239 MW based on injection transfer limit assessment) | PG&E GBA | 0
SYCAMORE CREEK 115 kV | PG&E NGBA | 1 | √
TABLE MOUNTAIN 115 kV | PG&E NGBA | 1 | √
TABLE MOUNTAIN 230 kV | PG&E NGBA | 1 | √
TABLE MOUNTAIN 500 kV | PG&E NGBA | 1 | √
TABLE MOUNTAIN 60 kV | PG&E NGBA | 1 | √
TAFT 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
Taft-Cuyama #1 70 kV Line | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
TASSAJARA 230 kV | PG&E GBA | 1 | √
TEJON 70 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
TEMBLOR 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
TEMPLETON 230 kV | PG&E KERN | 2 | [11 empty] | √ | √
TEMPLETON 70 kV | PG&E KERN | 2 | [11 empty] | √ | √
TESLA 115 kV (TPD limit 145 MW based on injection transfer limit assessment) | PG&E GBA | 0
TESLA 230 kV (TPD limit 1025 MW based on injection transfer limit assessment) | PG&E GBA | 0
TESLA 500 kV (TPD limit 3000 MW based on injection transfer limit assessment) | PG&E GBA | 0
TESORO 230 kV | PG&E GBA | 1 | √
TEVIS 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
TIDEWATER 230 kV | PG&E GBA | 1 | √
TIGER CREEK PH 230 kV | PG&E GBA | 1 | [5 empty] | √
TIVY VALLEY 70 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
TRACY 115 kV | PG&E GBA | 2 |  | √ | [5 empty] | √
TRANQUILLITY SW STA 230 kV | PG&E FRESNO | 2 |  |  |  | √ | [7 empty] | √
TRIMBLE 115 kV (TPD limit 213 MW based on injection transfer limit assessment) | PG&E GBA | 0
TRINITY 115 kV | PG&E NGBA | 1 | √
TRINITY 60 kV | PG&E NGBA | 1 | √
TULUCAY 230 kV | PG&E NGBA | 2 | √ |  |  |  | √
TULUCAY 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
TUPMAN 115 kV | PG&E KERN | 4 | [8 empty] | √ | √ |  | √ | √
UKIAH 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
UNIONPGAE 70 kV | PG&E GBA | 2 | [11 empty] | √ | √
VACA DIXON 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
VACA DIXON 230 kV | PG&E NGBA | 3 | √ |  | √ |  | √
VACA DIXON 500 kV | PG&E NGBA | 1 | √
VACA DIXON 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
VACAVILLE 115 kV | PG&E NGBA | 2 | √ |  |  |  | √
VALLECITOS 60 kV | PG&E GBA | 2 | √ |  | √
VALLEY HOME 115 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
VALLEY SPRINGS 230 kV | PG&E GBA | 1 | [5 empty] | √
VALLEY SPRINGS 60 kV | PG&E GBA | 1 | [5 empty] | √
Vasco-Herdlyn 60 kV line | PG&E GBA | 1 |  |  |  | √
Vasco-Las Positas 60 kV Line | PG&E GBA | 2 | √ |  | √
VASONA 230 kV (TPD limit 44 MW based on injection transfer limit assessment) | PG&E GBA | 0
VIERRA 115 kV | PG&E GBA | 3 |  | √ |  |  |  |  | √ | √
VINEYARD 230 kV | PG&E GBA | 1 |  |  | √
WAHTOKE 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
WAUKENA SW STA 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
WEBER 230 kV | PG&E GBA | 1 | [5 empty] | √
WEBER 60 kV | PG&E GBA | 1 | [5 empty] | √
WEIMAR 60 kV | PG&E NGBA | 1 | √
WEST FRESNO 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
WEST SACRAMENTO 115 kV | PG&E NGBA | 1 | √
WESTPARK 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
WHEELER RIDGE 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
WHEELER RIDGE 230 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
WHEELER RIDGE 70 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
WHISMAN 115 kV (TPD limit 120 MW based on injection transfer limit assessment) | PG&E GBA | 0
WILLITS A 60 kV | PG&E NGBA | 2 | √ |  |  |  | √
WILSON 115 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
WILSON 230 kV | PG&E FRESNO | 3 | [11 empty] | √ |  | √ | √
WINDSOR 60 kV | PG&E NGBA | 1 | √
WITCO SW STA 115 kV | PG&E KERN | 5 | [8 empty] | √ | √ | √ | √ | √
WOLFE 115 kV (TPD limit 247 MW based on injection transfer limit assessment) | PG&E GBA | 0
WOODLAND 115 kV | PG&E NGBA | 1 | √
WOODWARD 115 kV | PG&E FRESNO | 2 | [11 empty] | √ |  |  | √
WYANDOTTE 115 kV | PG&E NGBA | 1 | √

## Southern_Substation_List_Matrix
CAISO PUBLIC
SCE Northern Interconnection Area | TPD ZONE
SCE Metro Interconnection Area | TPD ZONE
SCE North of Lugo Interconnection Area | TPD ZONE
SCE Eastern Interconnection Area | MERCHANT ZONE
SCE East of Pisgah Interconnection Area | TPD ZONE
SDG&E Interconnection Area | TPD ZONE
|  |  | SCE Northern Interconnection Area Constraints | [8 empty] | SCE Metro Interconnection Area Constraints |  | SCE North of Lugo (NOL) Interconnection Area Constraints |  |  |  |  | SCE Eastern Interconnection Area Constraints | [7 empty] | East of Pisgah Interconnection Area Constraints |  |  |  | SDG&E Interconnection Area Constraints | [11 empty] | SunZia Area Constraint
POI Name/Short Description (Point of Delivery to CAISO-Controlled Grid for WDATs, etc.) & kV | Interconnection Study Area | Number of Constraints | Antelope-Neenach Area Deliverability Constraint | Antelope-Vincent Area Deliverability Constraint | Moorpark-Pardee Area Deliverability Constraint | North of Magunden Area Deliverability Constraint | Pardee-Sylmar Area Deliverability Constraint | Sylmar-Rinaldi Area Deliverability Constraint | South of Magunden Area Deliverability Constraint | Vincent-Lugo Area Deliverability Constraint | Windhub Area Deliverability Constraint | Hinson - Del Amo Area Deliverability Constraint | SCE Metro Area Deliverability Default Constraint | Calcite to Lugo Area Constraint | Control to Inyokern Constraint | Kramer to Victor Area Constraint | Lugo Transformer Constraint | Victor to Lugo Area Constraint | Colorado River 500/230 kV Area Deliverability Constraint | DCRT Area Deliverability Constraint | Devers-Red Bluff Area Deliverability Constraint | Eagle Mountain Area Deliverability Constraint | Etiwanda-Rancho Vista Area Deliverability Constraint | Mira Loma-Mesa Area Deliverability Constraint | Red Bluff 500/230 kV Area Deliverability Constraint | Serrano-Alberhill-Valley Area Deliverability Constraint | GLW - VEA Area Deliverability Constraints | Sloan Canyon - Eldorado Area Constraint | Lugo – Victorville Area Deliverability Constraint | Eldorado - McCullough Constraint | Capistrano-San Onofre 230 kV Deliverability Constraints | Chicarita 138 kV Deliverability Constraints | El Cajon 69 kV Deliverability Constraints | Miguel 69 kV Deliverability Constraints | Encina-San Luis Rey Deliverability Constraints | San Luis Rey-San Onofre Deliverability Constraints | Ocean Ranch 69 kV Deliverability Constraints | Otay Mesa 230 kV Deliverability Constraints | Silvergate-Bay Boulevard Deliverability Constraints | Silvergate-Old Town 230 kV Deliverability Constraints | Talega 230 kV Deliverability Constraints | Trabuco-Capistrano 138 kV Deliverability Constraints | Pinal Central - Palo Verde Deliverability Constraint
Transmission Plan Capability |  |  | 0 | 6638 | 849 | 1323 | 3038 | 3177 | 1011 | 7030 | 775 | 2700 | 13500 | 541 | 0 | 938 | 1940 | 1339 | 346 | 1850 | 4903 | 0 | 4604 | 20763 | 1281 | 5581 | 3706 | 4333 | 8669 | 5953 | 1314 | 224 | 406 | 231 | 3723.787 | 3988.037 | 194 | 975 | 3070.787 | 1276.187 | 1018 | 501 | 2131
Allocated TPD |  |  | 0 | 4887 | 849 | 1323 | 3038 | 3177 | 1011 | 4787 | 775 | 460 | 6000 | 541 | 0 | 323 | 865 | 324 | 346 | 1753 | 4903 | 0 | 4104 | 16562 | 1246 | 5581 | 2776 | 3153 | 5830 | 4773 | 1007 | 224 | 112 | 0 | 2150.1 | 2164.35 | 28 | 0 | 1597.1 | 554.1 | 866 | 257 | 2131
Available TPD |  |  | 0 | 1751 | 0 | 0 | 0 | 0 | 0 | 2243 | 0 | 2240 | 7500 | 0 | 0 | 615 | 1075 | 1015 | 0 | 97 | 0 | 0 | 500 | 4201 | 35 | 0 | 930 | 1180 | 2839 | 1180 | 307 | 0 | 294 | 231 | 1573.687 | 1823.687 | 166 | 975 | 1473.687 | 722.087 | 152 | 244 | 0
1-Number of POI behind Constraint |  |  | 2 | 32 | 14 | 12 | 42 | 45 | 17 | 8 | 3 | 6 | 43 | 3 | 3 | 19 | 24 | 22 | 1 | 3 | 12 | 6 | 26 | 273 | 1 | 31 | 27 | 38 | 74 | 41 | 53 | 4 | 23 | 15 | 136 | 153 | 9 | 1 | 29 | 54 | 49 | 6 | 1
Alamitos Substation 230 kV | SCE Metro | 2 | [9 empty] | √ | √
Alberhill 115 kV | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Alberhill 500 kV | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Alpine Substation 69 kV | SDGE | 6 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  |  | √
Antelope – Magunden #2 230 kV line | SCE Northern | 4 |  | √ |  |  | √ | √ | √
Antelope - Ritter Ranch #1 66 kV | SCE Northern | 3 |  | √ |  |  | √ | √
Antelope 66 kV Substation | SCE Northern | 1 |  | √
Antelope Substation 230 kV | SCE Northern | 1 |  | √
Antelope Substation 500 kV | SCE Northern | 2 |  | √ | [5 empty] | √
ArcoGen Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Artesian Substation 230 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Artesian Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Ash Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Avocado Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ | √ |  |  |  | √
Bailey Substation 230 kV | SCE Northern | 6 | √ | √ |  |  | √ | √ | √ | [19 empty] | √
Baker 115 kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Banning – Maraschino 115 kV (El Casco) | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Barre Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Barrett Substation 69 kV | SDGE | 6 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  |  | √
Basilone Substation 69 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ |  |  |  |  | √
Batiquitos Substation 138 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Bay Boulevard Substation 230 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Bay Boulevard Substation 69 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Beatty Substation 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Beatty Substation 230 kV (future) | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Bernardo Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Big Creek Substation 230 kV | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Bliss 66kV Substation | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Bloomington-Colton-Colton Cement 66 kV line (Vista Subtrans) | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Blythe 161kV - Colorado River 230kV | SCE Eastern | 2 | [19 empty] | √ |  | √
BlytheSC 161 kV Substation 161 kV | SCE Eastern | 3 | [19 empty] | √ |  | √ | [11 empty] | √
Bond Tap 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Border - Border Tap 69 kV | SDGE | 6 | [21 empty] | √ | [9 empty] | √ | √ | √ |  |  | √ | √
Border Substation 69 kV | SDGE | 7 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  | √ | √
Borrego Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Boulevard East Substation 138 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Boulevard East Substation 69 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Bruin 66kV | SCE Northern | 2 |  |  |  |  | √ | √
Cabrillo Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Calcite Substation 230kV | SCE NOL | 3 | [11 empty] | √ |  |  | √ | [6 empty] | √
Cameron Substation 69 kV | SDGE | 6 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  |  | √
Cannon Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Capistrano Substation 138 kV | SDGE | 3 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √
Capistrano Substation 230 kV | SDGE | 3 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √
Capitan 66 kV | SCE Northern | 4 |  |  | √ |  |  | √ | [20 empty] | √ |  | √
Cardiff 66 kV (San Bernardino) | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Carlton Hills Substation 138 kV | SDGE | 4 | [21 empty] | √ | [7 empty] | √ |  |  | √ | √
Carpinteria Substation 66 kV | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Carrizo Gorge Switchyard 138 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Casa Diablo Substation 33 kV | SCE NOL | 5 | [12 empty] | √ | √ | √ | √ | [5 empty] | √
Center Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Charleston Substation 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Chevmain Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Chicarita Substation 138 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Chino Substation 230 kV | SCE Metro | 2 | [10 empty] | √ | [10 empty] | √
Chollas West Substation 69 kV | SDGE | 5 | [21 empty] | √ | [8 empty] | √ |  | √ | √ |  |  |  | √
Cielo Azul Substation 500 kV | SCE Eastern | 5 | [17 empty] | √ | √ |  |  | √ |  | √ |  |  | √
Clairemont Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Colorado River – Delaney 500 kV Line | SCE Eastern | 5 | [17 empty] | √ | √ |  |  | √ |  | √ |  |  | √
Colorado River – Palo Verde 500 kV Line | SCE Eastern | 4 | [18 empty] | √ |  |  | √ |  | √ |  |  | √
Colorado River Substation 230 kV | SCE Eastern | 4 | [16 empty] | √ |  | √ |  |  | √ |  | √
Colorado River Substation 500 kV | SCE Eastern | 3 | [18 empty] | √ |  |  | √ |  | √
Control Substation 55 kV | SCE NOL | 5 | [12 empty] | √ | √ | √ | √ | [5 empty] | √
Control Substation 115 kV | SCE NOL | 5 | [12 empty] | √ | √ | √ | √ | [5 empty] | √
Coolwater Substation 115 kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Coolwater Substation 230 kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Coronado Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Creelman Substation 69 kV | SDGE | 6 | [21 empty] | √ | [6 empty] | √ |  | √ |  | √ | √ |  |  |  |  | √
Crestwood Substation 69 kV | SDGE | 6 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  |  | √
Del Amo Substation 500 kV | SCE Metro | 1 | [10 empty] | √
Del Amo Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Del Mar Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Del Sur 66kV (System ID is Antelope 220/66) | SCE Northern | 3 |  | √ |  |  | √ | √
Delaney Substation 500 kV | SCE Eastern | 5 | [17 empty] | √ | √ |  |  | √ |  | √ |  |  | √
Descanso Substation 69 kV | SDGE | 6 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  |  | √
Desert View Substation 230 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Devers Substation 230 kV | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Devers Substation 500 kV | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Devers-Garnet 115 kV Line Tap | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Devers-San Bernardino line 230 kV | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Division Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Doublet Substation 138 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Dunhill 138 kV Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Dunn Siding 115 kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Eagle Mountain Substation 230 kV | SCE Eastern | 4 | [19 empty] | √ | √ | √ |  | √
Eagle Rock Substation 230 kV | SCE Metro | 2 | [5 empty] | √ |  |  |  |  | √
Eastgate Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
ECO Substation 138 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
ECO Substation 230 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
ECO Substation 500 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
El Cajon Substation 69 kV | SDGE | 4 | [21 empty] | √ | [8 empty] | √ |  | √ | √
El Casco Substation 230 kV | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
El Nido Substation 230 kV | SCE Metro | 2 | [9 empty] | √ | √
El Segundo Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Eldorado Substation 230 kV | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Eldorado Substation 230 kV (SCE portion) | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Eldorado Substation 500 kV | SCE EOP | 3 | [21 empty] | √ |  |  |  |  | √ | √
Elizabeth Lake Substation 66 kV | SCE Northern | 3 |  |  |  |  | √ | √ | [20 empty] | √
Elliot Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Ellis Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Encina Substation 138 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Encina Substation 230 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Encinitas Substation 69 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √
Esco Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Escondido Substation 230 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Escondido Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Etiwanda Substation 230 kV | SCE Metro | 2 | [20 empty] | √ | √
Etiwanda-Ameron 66 kV Line | SCE Metro | 2 | [20 empty] | √ | √
Etiwanda-Randall 66 kV Line | SCE Metro | 2 | [20 empty] | √ | √
Felicita Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Friars Substation 138 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Gamebird Substation 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Gamebird Substation 230 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Garfield Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Genesee Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Glencliff Substation 69 kV | SDGE | 6 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  |  | √
Goleta Substation 230 kV | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Goodrich Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Gould Substation 230k kV | SCE Metro | 1 | [10 empty] | √
Granite Substation 69 kV | SDGE | 4 | [21 empty] | √ | [8 empty] | √ |  | √ | √
Grant Hill Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Growers Substation 66 kV | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Harborgen Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Harry Allen – Sloan Canyon 500 kV | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Sloan Canyon - Eldorado 500 kV | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Harry Allen Substation 500 kV | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Harvard 33 kV Bus/Gale 115 kV Bus | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Hassayampa Substation 500 kV | SDGE | 3 | [18 empty] | √ |  |  | √ |  |  |  |  | √
Highgrove 115 kV (Vista) | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Hinson Substation 230 kV | SCE Metro | 2 | [9 empty] | √ | √
Hoodoo Wash - Hassayampa 500 kV Line | SDGE | 4 | [21 empty] | √ |  |  |  |  | √ | [5 empty] | √ | √
Hoodoo Wash - North Gila 500 kV | SDGE | 4 | [21 empty] | √ |  |  |  |  | √ | [5 empty] | √ | √
Hoodoo Wash Switchyard 500 kV | SDGE | 4 | [18 empty] | √ |  |  | √ |  |  |  |  | √ | [6 empty] | √
Huntington Beach Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Imperial Beach Substation 69 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Imperial Valley Substation 230 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Imperial Valley Substation 500 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Indigo 115 kV (Devers) | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Innovation – Desert View 230 kV Line | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Innovation Substation 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Innovation Substation 230 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Inyokern 33 kV Bus/Inyokern 115 kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Inyokern Substation 115 kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
IS Tap 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Isla Vista Substation 66 kV | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Ivanpah Substation 115 kV | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Ivanpah Substation 230 kV | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Jackass (DOE) Substation 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Jamacha - Miguel 69 kV | SDGE | 5 | [21 empty] | √ | [8 empty] | √ |  | √ | √ |  |  |  | √
Jamacha Substation 69 kV | SDGE | 5 | [21 empty] | √ | [8 empty] | √ |  | √ | √ |  |  |  | √
Japanese Mesa Substation 69 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ |  |  |  |  | √
Johanna Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Johnnie Corner Substation 230 kV (future) | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Julian Hinds Substation 230 kV | SCE Eastern | 4 | [19 empty] | √ | √ | √ |  | √
Kearny 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Kettner Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Kramer Junction Substation 230kV | SCE NOL | 3 | [13 empty] | √ |  | √ | [5 empty] | √
Kramer Substation 115 kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Kramer Substation 230kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Kramer-Victor #1 230 kV line | SCE NOL | 3 | [13 empty] | √ |  | √ | [5 empty] | √
Kramer-Victor No.1 220 kV T/L | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Kyocera Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
La Cienega Substation 230 kV | SCE Metro | 2 | [9 empty] | √ | √
La Fresa Substation 230 kV | SCE Metro | 2 | [9 empty] | √ | √
La Jolla Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Laguna Bell Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Laguna Nigel Substation 138 kV | SDGE | 3 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √
Lake Hodges Metering Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Las Pulgas Substation 69 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ |  |  |  |  | √
Lathrop Substation 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Lathrop Substation 230 kV(future) | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Lewis Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Lighthipe Substation 230 kV | SCE Metro | 2 | [9 empty] | √ | √
Lilac Substation 69 kV | SDGE | 6 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ | √ |  |  |  | √
Little Rock - Sparkle - Wilsona 66 kV | SCE Northern | 3 |  | √ |  |  | √ | √
Los Coches Substation 138 kV | SDGE | 5 | [21 empty] | √ | [7 empty] | √ | √ |  | √ | √
Los Coches Substation 69 kV | SDGE | 4 | [21 empty] | √ | [8 empty] | √ |  | √ | √
Loveland - Alpine 69 kV | SDGE | 6 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  |  | √
Loveland Substation 69 kV | SDGE | 6 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  |  | √
Lugo Substation 230 kV | SCE NOL | 2 | [14 empty] | √ | [6 empty] | √
Lugo Substation 500 kV | SCE Metro | 2 | [10 empty] | √ | [10 empty] | √
Lugo-Pisgah No.2 230 kV T/L | SCE NOL | 3 | [11 empty] | √ |  |  | √ | [6 empty] | √
Magunden Substation 230 kV | SCE Northern | 4 |  | √ |  |  | √ | √ | √
Mandalay Switchyard 230kV | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Margarita Substation 138 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √ | √
Mascot Substation 66 kV | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Melrose Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ | √ |  |  |  | √
Merchant Substation 230 kV | SCE EOP | 3 | [21 empty] | √ |  |  |  |  | √ | √
Mercury Switch 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Mesa Heights Substation 69 kV | SDGE | 2 | [21 empty] | √ | [11 empty] | √
Mesa Rim Substation 69 kV | SDGE | 2 | [21 empty] | √ | [11 empty] | √
Mesa Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Mesa Substation 500 kV | SCE Metro | 1 | [10 empty] | √
Miguel Substation 230 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Miguel Substation 500 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Miguel Substation 69 kV | SDGE | 7 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  | √ | √
Mira Loma Substation 230 kV | SCE Metro | 2 | [10 empty] | √ | [10 empty] | √
Mira Loma Substation 500 kV | SCE Metro | 2 | [10 empty] | √ | [10 empty] | √
Mira Sorrento Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Mirage Substation 115 kV | SCE Eastern | 4 | [19 empty] | √ | √ | √ |  | √
Mirage Substation 220 kV | SCE Eastern | 4 | [19 empty] | √ | √ | √ |  | √
Miramar GT Switchyard 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Miramar Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Mission Substation 138 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Mission Substation 230 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Mission Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Mohave 500kV | SCE EOP | 3 | [21 empty] | √ |  |  |  |  | √ | √
Monserate Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ | √ |  |  |  | √
Montgomery Substation 69 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Moorpark 230 kV | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Moorpark Substation 66 kV | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Morro Hill Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ | √ |  |  |  | √
Mountain Pass 115 kV | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Murray Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Narrows Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
National City Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Naval Station Metering Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Neenach 66 kV | SCE Northern | 4 | √ | √ |  |  | √ | √
New Sub - North Gila - IV (Proposed) Substation 500 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
New Sub - Suncrest - Ocotillo (Proposed) Substation 500 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √
North City Metering Substation 138 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
North Gila Substation 500 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
North Island Metering Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
North Oaks 66 kV | SCE Northern | 3 |  |  |  |  | √ | √ | [20 empty] | √
North of SONGS 230 kV | SCE Metro | 1 | [10 empty] | √
North of SONGS 500 kV | SCE Metro | 1 | [10 empty] | √
Oak Grove Substation, 66KV | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Ocean Ranch Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ | √ |  |  |  | √
Oceanside Substation 69 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ |  |  |  |  | √
Ocotillo Express Substation 500 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √
Octol Substation 66 kV | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Old Town Substation 230 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Olinda Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Olivenhain Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Ormond Beach Substation 230 kV | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Otay Lake Substation 69 kV | SDGE | 6 | [21 empty] | √ | [9 empty] | √ | √ | √ |  |  | √ | √
Otay Mesa Substation 230 kV | SDGE | 6 | [21 empty] | √ | [10 empty] | √ | √ |  | √ | √ | √
Otay Substation 69 kV | SDGE | 6 | [21 empty] | √ | [9 empty] | √ | √ | √ |  |  | √ | √
Pacific Beach Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Pahrump Substation 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Pahrump Substation 230 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Pala Substation 69 kV | SDGE | 6 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ | √ |  |  |  | √
Palo Verde Substation 500 kV | SCE Eastern | 4 | [18 empty] | √ |  |  | √ |  | √ |  |  | √
Palomar Airport Substation 138 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Palomar Energy Substation 230 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Paradise Substation 69 kV | SDGE | 5 | [21 empty] | √ | [8 empty] | √ |  | √ | √ |  |  |  | √
Pardee Substation 230 kV | SCE Northern | 3 |  |  |  |  | √ | √ | [20 empty] | √
Pastoria Substation 230kV | SCE Northern | 5 |  | √ |  |  | √ | √ | √ | [19 empty] | √
Pauda Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Penasquitos Substation 138 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Penasquitos Substation 230 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Penasquitos Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Pendleton Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ | √ |  |  |  | √
Pete Heinrich 345 kV | SunZia | 4 | [18 empty] | √ |  |  | √ |  | √ |  |  | √ | [13 empty] | √
Pico Substation 138 kV | SDGE | 3 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √
Pisgah Substation 230 kV Bus | SCE NOL | 3 | [11 empty] | √ |  |  | √ | [6 empty] | √
Piute Substation 66 kV | SCE Northern | 3 |  | √ |  |  | √ | √
Poco 33 kV line/Tortilla 115 kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Point Loma Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Pomerado Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Poplar-Terra Bella 70 kV line | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Poway Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Primm Substation 230 kV | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Proctor Valley Substation 138 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Q1806 Switchyard Substation 138 kV | SDGE | 3 | [21 empty] | √ | [16 empty] | √ | √
Quartz Hill Substation 66 kV | SCE Northern | 3 |  | √ |  |  | √ | √
Rancho Carmel Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Rancho Mission Viejo Substation 138 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √ | √
Rancho Santa Fe Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Rancho Vista Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Rancho Vista Substation 500 kV | SCE Metro | 1 | [10 empty] | √
Ransburg Substation 115 kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Rector 230 kV | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Red Bluff Substation 230 kV | SCE Eastern | 5 | [18 empty] | √ |  | √ | √ | √ | √
Red Bluff Substation 500 kV | SCE Eastern | 4 | [18 empty] | √ |  | √ | √ |  | √
Redondo 230 kV | SCE Metro | 1 | [10 empty] | √
Rincon Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Rio Hondo Substation 230kV | SCE Metro | 1 | [10 empty] | √
Roadway Substation 115kV | SCE NOL | 3 | [14 empty] | √ | √ | [5 empty] | √
Rosamond 66kV | SCE Northern | 3 |  | √ |  |  | √ | √
Rosamond/CalCement circuit 66kV | SCE Northern | 3 |  | √ |  |  | √ | √
Rose Canyon Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Royal Substation 66 kV | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Salt Creek Substation 69 kV | SDGE | 7 | [21 empty] | √ | [8 empty] | √ | √ | √ | √ |  |  | √ | √
Sampson Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
San Bernardino 230 kV | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
San Luis Rey Substation 230 kV | SDGE | 2 | [21 empty] | √ | [11 empty] | √
San Luis Rey Substation 69 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ |  |  |  |  | √
San Marcos Substation 69 kV | SDGE | 6 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ | √ |  |  |  | √
San Mateo Substation 69 kV | SDGE | 3 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √
San Miguel 66 kV | SCE Northern | 3 |  |  | √ |  |  | √ | [20 empty] | √
San Onofre Substation 230 kV | SCE Metro | 1 | [10 empty] | √
San Ysidro Substation 69 kV | SDGE | 6 | [21 empty] | √ | [9 empty] | √ | √ | √ |  |  | √ | √
Sandlot Substation 230 kV | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Sandy Substation 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Santa Clara - Gonzales 66 kV line | SCE Northern | 1 | [26 empty] | √
Santa Clara Substation 230 kV | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Santa Ysabel Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Santee Substation 138 kV | SDGE | 4 | [21 empty] | √ | [7 empty] | √ |  |  | √ | √
Santiago Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Saugus Substation 230 kV | SCE Northern | 1 | [26 empty] | √
SC / Gonzales 66kV | SCE Northern | 3 |  |  | √ |  | √ | √
Scripps Substation 69 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √
Serrano Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Serrano Substation 500 kV | SCE Metro | 1 | [10 empty] | √
Shadowridge Substation 138 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Silvergate Substation 230 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Silvergate Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Skylark 115 kV (Valley) | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Sloan Canyon Substation 230 kV | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Sloan Canyon Substation 500 kV (future) | SCE EOP | 4 | [21 empty] | √ |  |  |  | √ | √ | √
Spring Valley Substation 69 kV | SDGE | 5 | [21 empty] | √ | [8 empty] | √ |  | √ | √ |  |  |  | √
Springville 230 kV | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Station B Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Station F Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Streamview Substation 69 kV | SDGE | 5 | [21 empty] | √ | [8 empty] | √ |  | √ | √ |  |  |  | √
Stuart Substation 69 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ |  |  |  |  | √ |  |  |  |  | √
Suncrest Substation 230 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √
Suncrest Substation 500 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √
Sunnyside Substation 69 kV | SDGE | 6 | [21 empty] | √ | [8 empty] | √ |  | √ | √ |  |  | √ | √
Sweetwater Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Sycamore Canyon Substation 138 kV | SDGE | 4 | [21 empty] | √ | [7 empty] | √ |  |  | √ | √
Sycamore Canyon Substation 230 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √
Sycamore Canyon Substation 69 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √
Sylmar – Gould 230 kV line | SCE Northern | 3 |  |  |  |  | √ | √ | [20 empty] | √
Sylmar Substation 230 kV | SCE Northern | 1 | [26 empty] | √
Talega Substation 138 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √ | √
Talega Substation 230 kV | SDGE | 3 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √
Telegraph Canyon Substation 138 kV | SDGE | 5 | [21 empty] | √ | [10 empty] | √ | √ |  |  | √ | √
Thousandaire Substation 138 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Torrey Pines Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Tortilla 115 kV Bus | SCE NOL | 4 | [13 empty] | √ | √ | √ | [5 empty] | √
Trabuco - Capistrano Line 138 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √ | √
Trabuco Substation 138 kV | SDGE | 4 | [21 empty] | √ | [6 empty] | √ | [9 empty] | √ | √
Trout Canyon Substation 230 kV | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Trout Canyon Substation 500 kV (future) | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Tule 66kV | SCE Northern | 4 |  |  |  | √ | √ | √ | √
UCM Substation 69 kV | SDGE | 3 | [21 empty] | √ | [10 empty] | √ | √
Urban Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Valley Center Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Valley Substation 138 kV (VEA) | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Valley Substation 500 kV | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Valley Switch 138 kV (VEA) | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Valley Switch 230 kV (future) | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Vestal Substation 230 kV | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Vestal Substation 66 kV | SCE Northern | 5 |  | √ |  | √ | √ | √ | √
Victor Substation 115 kV | SCE NOL | 3 | [14 empty] | √ | √ | [5 empty] | √
Victor Substation 230 kV | SCE NOL | 3 | [14 empty] | √ | √ | [5 empty] | √
Viejo Substation 230 kV | SCE Metro | 2 | [10 empty] | √ | [10 empty] | √
Villa Park Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Vincent Substation 230 kV | SCE Northern | 1 | [7 empty] | √
Vincent Substation 500 kV | SCE Northern | 1 | [7 empty] | √
Vine Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Vista Substation 138 kV (VEA) | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Vista Substation 230 kV | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Vista Substation 230 kV (VEA future) | SCE EOP | 5 | [21 empty] | √ |  |  | √ | √ | √ | √
Wabash Canyon Substation 69 kV | SDGE | 4 | [21 empty] | √ | [10 empty] | √ | √ |  |  |  | √
Wakefield 66 kV bus | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Wakefield 66/16 KV | SCE Northern | 4 |  |  | √ |  | √ | √ | [20 empty] | √
Walnut Substation 230 kV | SCE Metro | 1 | [10 empty] | √
Warne Substation 230 kV | SCE Northern | 5 |  | √ |  |  | √ | √ | √ | [19 empty] | √
Warners Substation 69 kV | SDGE | 5 | [21 empty] | √ | [6 empty] | √ |  |  |  | √ | √ |  |  |  |  | √
Whirlwind Substation 230 kV | SCE Northern | 2 |  | √ | [5 empty] | √
Whirlwind Substation 500 kV | SCE Northern | 2 |  | √ | [5 empty] | √
Whirlwind-Windhub 500 kV line | SCE Northern | 3 |  | √ | [5 empty] | √ | √
Wildlife Substation 230 kV | SCE Eastern | 3 | [20 empty] | √ | √ |  | √
Windhub Substation 230 kV | SCE Northern | 3 |  | √ | [5 empty] | √ | √
Windhub Substation 500 kV | SCE Northern | 3 |  | √ | [5 empty] | √ | √