## Summary
|  |  |  | CA |  | NWPP | Total |  |  |  | CA | WECC |  |  |  | CA | WECC
|  |  |  | California Independent System Operator |  | PacifiCorp
| Capacity Savings in CAISO and PacifiCorp in 2020 | [6 empty] | Capacity Savings in California and Rest of Region in 2030 |  |  |  |  | Capacity Savings in California and Rest of Region in 2020-Regional
|  |  |  | ISO | PacifiCorp |  | ISO+PAC Total |  |  |  | California | Rest of Region |  |  |  | California | Rest of Region
1 | Capacity Requirement |  | [1] | 115% |  | 113% |  | Subregion Capacity Requirement |  | [1] | 115-116.1% | 75-116.1 | Subregion Capacity Requirement |  | [1] | 115-116.1% | 75-116.1
2 | Non-Coincident Peak (MW) |  | [2] | 47009.5734 |  | 13234 | 60243.5734 | Sum of BA Non-Coincident Peaks (MW) |  | [2] | 57187.7934 | 85302.4117 | Sum of BA Non-Coincident Peaks (MW) |  | [2] | 59688.3171 | 75829
3 | Median Coincidence Factor |  | [3] | 99.66% |  | 92.19% |  | BA Coincidence Factor (Coincidence with subregion peak) |  | [3] | 99.23% | 94.21% | BA Coincidence Factor (Coincidence with subregion peak) |  | [3] | 99.29% | 94.02%
4 | BA's Share of Regional Market Peak (MW) |  | [4] | 46849.3135 |  | 12200.751 | 59050.0645 | Sum of BA Peak Loads Coincident with Subregion Peak (MW) |  | [4] | 56746.8797 | 80363.8576 | Sum of BA Peak Loads Coincident with Subregion Peak (MW) |  | [4] | 59262.3515 | 71294.7587
5 | Potential Capacity Savings (MW) |  | [5] | 184.2989 |  | 1167.5714 | 1351.8702 | Potential Savings: Sharing Within Subregions (MW) |  | [5] | 507.9696 | 5702.5701 | Potential Savings: Sharing Within Subregions (MW) |  | [5] | 490.7092 | 5235.6054
6 | Maximum Transmission Import Capability (MW) |  | [6] | 982 |  | 776 |  | Savings Already Captured (Estimated) (MW) |  | [6] | 0 | 4480.5615 | Savings Already Captured (Estimated) (MW) |  | [6] | 0 | 4136.1659
7 | Savings w/ Current Transmission (MW) |  | [7] | 184.2989 |  | 776 | 960.2989 | Incremental Savings w/ Current Transmission: Sharing Within Subregions (MW) |  | [7] | 362.8633 | 604.195 | Incremental Savings w/ Current Transmission: Sharing Within Subregions (MW) |  | [7] | 353.0665 | 532.5591
8 | Percentage of Total Savings |  | [8] | 0.392% |  | 5.864% |  | Savings Requiring Transmission Upgrades (MW) |  | [8] | 145.1063 | 617.8136 | Savings Requiring Transmission Upgrades (MW) |  | [8] | 137.6427 | 566.8804
9 | Savings Requiring Transmission Upgrades (MW) |  | [9] | 0 |  | 391.5714 | 391.5714 | Average Coincidence Factor (Coincident with WECC-PMAs peak) |  | [9] | 98.11% | 96.33% | Average Coincidence Factor (Coincident with WECC-PMAs peak) |  | [9] | 98.09% | 96.34%
| Percentage of Total Savings |  | [10] | 0% |  | 2.959% |  | Estimated Load During WECC Peak (MW) |  | [10] | 55676.3992 | 77414.8823 | Estimated Load During WECC Peak (MW) |  | [10] | 58128.8245 | 68688.674
10 | Avoided Cost of Capacity Savings ($/kW-yr) |  | [11] | 35 |  | 39 |  | Potential Savings: Sharing Across Subregions (MW) |  | [11] | 1231.0526 | 3384.7811 | Potential Savings: Sharing Across Subregions (MW) |  | [11] | 1303.556 | 2990.6333
11 | [7 empty] | Incremental Savings w/ Current Transmission: Sharing Across Subregions (MW) |  | [12] | 1231.0526 | 2060.3654 | Incremental Savings w/ Current Transmission: Sharing Across Subregions (MW) |  | [12] | 1303.556 | 1855.8177
12 | Total $ Savings w/Current Transmission ($ million/year) |  | [12] | 6.4505 |  | 30.264 | 36.7145 | Savings Requiring Transmission Upgrades (MW) |  | [13] | 0 | 1324.4157 | Savings Requiring Transmission Upgrades (MW) |  | [13] | 0 | 1134.8156
13 | Total $ Savings Requiring Transmission Upgrades |  | [13] | 0 |  | 15.2713 | 15.2713 | Total Savings Requiring Transmission Upgrades ( =[8] + [13]) (MW) |  | [14] | 145.1063 | 1942.2293 | Total Savings Requiring Transmission Upgrades ( =[8] + [13]) (MW) |  | [14] | 137.6427 | 1701.696
14 | [7 empty] | Percentage of Non-Coincident Peak Load |  | [15] | 0.2537% | 2.277% | Percentage of Non-Coincident Peak Load |  | [15] | 0.2306% | 2.244%
15 | Sources and Notes: | [6 empty] | Total Savings w/Current Transmission (=[7] + [12]) (MW) |  | [16] | 1593.9159 | 2664.5604 | Total Savings w/Current Transmission (=[7] + [12]) (MW) |  | [16] | 1656.6226 | 2388.3768
| [1] | Based on PacifiCorp 2014 IRP and CAISO published reserve margins. | [5 empty] | Percentage of Non-Coincident Peak Load |  | [17] | 2.787% | 3.124% | Percentage of Non-Coincident Peak Load |  | [17] | 2.775% | 3.15%
16 | [2] | Forecast 2020 Non-Coincident Peak Loads. ISO from 2015 IEPR, equal to CEC 'Mid Baseline Case.' PacifiCorp from 2015 LAR Peak and Energy forecast, PACE + PACW coincident peak. | [5 empty] | Avoided Cost of Capacity Savings ($/kW-yr) |  | [18] | 75 | 100 | Avoided Cost of Capacity Savings ($/kW-yr) |  | [18] | 35 | 35
| [3] | Median of annual coincidence factors calculated based on 4CP of hourly load profiles from 2006 to 2014.
17 | [4] | [2] * [3] | [5 empty] | Total Avoided Cost w/Current Transmission ($ million/yr) |  | [19] | 119.5437 | 266.456 | Total Avoided Cost w/Current Transmission ($ million/yr) |  | [19] | 57.9818 | 83.5932
18 | [5] | [1] * ([2] - [4]) | [5 empty] | Total Avoided Cost Requiring Transmission Upgrades ($ million/yr) |  | [20] | 10.883 | 194.2229 | Total Avoided Cost Requiring Transmission Upgrades ($ million/yr) |  | [20] | 4.8175 | 59.5594
| [6] | Contracted import capability for the ISO and PacifiCorp.
19 | [7] | Minimum of [5] and [6]
20 | [8] | [7] / [2] | [5 empty] | Sources and Notes: |  |  |  |  | Sources and Notes:
| [9] | [5] - [7] | [5 empty] | [1] | Capacity requirement based on WECC-determined reserve margin levels as reported in 2015 NERC LTRA |  |  |  | [1] | Capacity requirement based on WECC-determined reserve margin levels as reported in 2015 NERC LTRA
| [10] | [9] / [2] | [5 empty] | [2] | Sum of forecast BA Non-Coincident Peak Loads in 2030 |  |  |  | [2] | Sum of forecast BA Non-Coincident Peak Loads in 2020-Regional
| [11] | ISO's value reflects 2012-2016 weighted-average contract prices. High end of PacifiCorp rang reflects capacity cost net of energy margins for two units as reported in the 2015 IRP. The low end reflects the fact that these units are not expected to come online before 2020. | [5 empty] | [3] | [4] / [2] |  |  |  | [3] | [4] / [2]
| [12] | [11] * [7] | [5 empty] | [4] | Sum of forecast BA Coincident Peak Loads in 2030 |  |  |  | [4] | Sum of forecast BA Coincident Peak Loads in 2020-Regional
[8 empty] | [5] | Sum of potential savings from sharing within subregions [Approximately [1] * ([2] - [4])] |  |  |  | [5] | Sum of potential savings from sharing within subregions [Approximately [1] * ([2] - [4])]
[8 empty] | [6] | Capacity savings already achieved by Bas based on internal reserve margins |  |  |  | [6] | Capacity savings already achieved by Bas based on internal reserve margins
[8 empty] | [7] | Savings achievable with current transmission into each BA |  |  |  | [7] | Savings achievable with current transmission into each BA
[8 empty] | [8] | Savings requiring additional transmission based on within-subregion transmission limits in WECC LAR zonal model. |  |  |  | [8] | Savings requiring additional transmission based on within-subregion transmission limits in WECC LAR zonal model.
[8 empty] | [9] | [10] / [4] |  |  |  | [9] | [10] / [4]
[8 empty] | [10] | Sum of shares of the coincident peak [Approximately [4] * [9]]. |  |  |  | [10] | Sum of shares of the coincident peak [Approximately [4] * [9]].
[8 empty] | [11] | Sum of potential savings from sharing across subregions [Approximately [1] * ([4] - [10])]. California savings California subregion savings. |  |  |  | [11] | Sum of potential savings from sharing across subregions [Approximately [1] * ([4] - [10])]. California savings California subregion savings.
[8 empty] | [12] | Savings achievable with current transmission into each subregion |  |  |  | [12] | Savings achievable with current transmission into each subregion
[8 empty] | [13] | Savings requiring additional transmission based on across-subregion transmission limits in WECC LAR zonal model. |  |  |  | [13] | Savings requiring additional transmission based on across-subregion transmission limits in WECC LAR zonal model.
[8 empty] | [14] | [8] + [13] |  |  |  | [14] | [8] + [13]
[8 empty] | [15] | [14] / [2] |  |  |  | [15] | [14] / [2]
[8 empty] | [16] | [7] + [12] |  |  |  | [16] | [7] + [12]
[8 empty] | [17] | [16] / [2] |  |  |  | [17] | [16] / [2]
[8 empty] | [18] | Assumed avoided cost of $75/kW-yr in California and $100/kW-yr in Rest of Region |  |  |  | [18] | Assumed avoided cost of $35/kW-yr in California and $35/kW-yr in Rest of Region
[8 empty] | [19] | [16] * [18] |  |  |  | [19] | [16] * [18]
[8 empty] | [20] | [14] * [18] |  |  |  | [20] | [14] * [18]

## 2030 Regional ISO
[6 empty] | 1 | 2 | 3 | [9 empty] | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Multi-Year Peak Loads by BAA for WECC without BPA and WAPA
| Within-Subregion Geographic Indicator | Within-Subregion Geographic Indicator | Balancing Authority Area |  | WECC Subregion | BAA Planning Reserve Margin | NERC Planning Reserve Reference Level | Non-Coincident Peak Load | 2006 CF | 2007 CF | 2008 CF | 2009 CF | 2010 CF | 2011 CF | 2012 CF | 2013 CF | 2014 CF | Median Coincidence Factor | Share of Coincident Peak | Potential Regionalization Capacity Savings | Capacity Savings Already Captured - Within or Across Sub-Regions | Capacity Savings Already Captured | Potential Capacity Savings from Market Integration | Import Limit | Incremental Capacity Savings with current Tx | Incremental Capacity Savings Requiring Tx Upgrades
[6 empty] | % | % | MW | [9 empty] | % | MW | MW | MW | MW | MW | MW | MW | MW | bar: 2006 CF to 2014 CF
[6 empty] | [1] | [2] | [3] | [9 empty] | [4] | [5] | [6] | [7] | [8] | [9] | [10] | [11] | [12]
California | CA |  | [a] | California Independent System Operator | CA | 115% | 115% | 43982.2198 | 100% | 99.91% | 100% | 99.94% | 100% | 100% | 100% | 99.85% | 99.95% | 100% | 43982.2198 | 0 | 0 | 0 | 0 | 3638.6717 | 0 | 0
California | CA |  | [b] | Los Angeles Dept of Water & Power | CA | 115% | 115% | 6435.8549 | 99.31% | 98.94% | 99.9% | 99.99% | 91.84% | 95.5% | 95.52% | 92.69% | 95.9% | 95.9% | 6171.9078 | 303.5391 | 0 | 0 | 303.5391 | 3750 | 303.5391 | 0
Northwest Power Pool | WECC |  | [c] | Avista Corp | NWPP | 104% | 115.4% | 2490.3509 | 96.04% | 88.5% | 80.56% | 80.06% | 82.97% | 85.94% | 97.95% | 89.14% | 86.8% | 86.8% | 2161.7036 | 379.259 | 283.9 | 283.9 | 95.359 | 150.8082 | 0 | 95.359
Northwest Power Pool | CA |  | [d] | Balancing Authority of Northern California | NWPP | 115.4% | 115.4% | 4843.6708 | 97.4% | 98.51% | 98.17% | 93.51% | 87.12% | 83.01% | 97.6% | 98.58% | 89.97% | 97.4% | 4717.9288 | 145.1063 | 0 | 0 | 145.1063 | 0 | 0 | 145.1063
Northwest Power Pool | WECC |  | [e] | Idaho Power Co | NWPP | 115.4% | 115.4% | 4615.5766 | 99.9% | 98.34% | 93.9% | 91.19% | 93.56% | 95.67% | 92.49% | 99.65% | 97.79% | 95.67% | 4415.4936 | 230.8959 | 0 | 0 | 230.8959 | 1695.8049 | 230.8959 | 0
Northwest Power Pool | WECC |  | [f] | Nevada Power Co | NWPP | 112% | 115.4% | 9116.5799 | 96.92% | 100% | 98.56% | 99.31% | 93.25% | 100% | 95.54% | 99.6% | 84.8% | 98.56% | 8985.1 | 151.7277 | 309.9637 | 151.7277 | 0 | 500 | 0 | 0
Northwest Power Pool | WECC |  | [g] | Northwestern Energy | NWPP | 110% | 115.4% | 2072.7 | 96.88% | 94.59% | 84.58% | 79.63% | 85.9% | 92.54% | 91.77% | 97.63% | 89.2% | 91.77% | 1902.0554 | 196.9238 | 111.9258 | 111.9258 | 84.998 | 460.333 | 84.998 | 0
Northwest Power Pool | WECC |  | [h] | PacifiCorp | NWPP | 113% | 115.4% | 13861.2616 | 99.89% | 97.17% | 99.93% | 99.81% | 98.5% | 99.55% | 97.62% | 99.89% | 99% | 99.55% | 13798.9245 | 71.937 | 332.6703 | 71.937 | 0 | 1046.5898 | 0 | 0
Northwest Power Pool | WECC |  | [i] | Portland General Electric | NWPP | 108% | 115.4% | 4273.9209 | 99.45% | 87.88% | 86.49% | 96.25% | 94.54% | 92.06% | 89.61% | 90.55% | 87.37% | 90.55% | 3870.2269 | 465.8629 | 316.2701 | 316.2701 | 149.5927 | 244.9083 | 0 | 149.5927
Northwest Power Pool | WECC |  | [j] | PUD No 1 of Chelan County | NWPP | 84% | 115.4% | 813.075 | 69.54% | 69.37% | 61.44% | 66.56% | 66.45% | 74.73% | 74.96% | 70.52% | 69.34% | 69.37% | 564.0686 | 287.3534 | 255.3056 | 255.3056 | 32.0478 | 47.8332 | 0 | 32.0478
Northwest Power Pool | WECC |  | [k] | PUD No 1 of Douglas County | NWPP | 77% | 115.4% | 499.3613 | 64.95% | 64.54% | 55.97% | 63.23% | 58.51% | 60.8% | 66.81% | 62.22% | 64.57% | 63.23% | 315.7621 | 211.8735 | 191.7547 | 191.7547 | 20.1188 | 25.6459 | 0 | 20.1188
Northwest Power Pool | WECC |  | [l] | PUD No 2 of Grant County | NWPP | 115.4% | 115.4% | 992.0947 | 97.08% | 94.78% | 94.75% | 94.43% | 96.03% | 99.06% | 98.49% | 94.06% | 96.93% | 96.03% | 952.711 | 45.4488 | 0 | 0 | 45.4488 | 55.7945 | 45.4488 | 0
Northwest Power Pool | WECC |  | [m] | Puget Sound Energy Inc | NWPP | 83% | 115.4% | 5500.5383 | 71.49% | 65.64% | 62.1% | 70.66% | 68.22% | 68.66% | 69.52% | 69.88% | 67.5% | 68.66% | 3776.9076 | 1989.0698 | 1782.1744 | 1782.1744 | 206.8954 | 336.5287 | 0 | 206.8954
Northwest Power Pool | WECC |  | [n] | Seattle City Light | NWPP | 87% | 115.4% | 1937.535 | 77.45% | 68.92% | 67.88% | 76.91% | 70.84% | 72.23% | 72.06% | 73.61% | 70.88% | 72.06% | 1396.245 | 624.6486 | 550.2599 | 550.2599 | 74.3887 | 119.4197 | 0 | 74.3887
Northwest Power Pool | WECC |  | [o] | Tacoma Power | NWPP | 75% | 115.4% | 1067.3143 | 66.28% | 59.55% | 58.44% | 61.79% | 60.86% | 64.01% | 64.83% | 63.49% | 60.55% | 61.79% | 659.51 | 470.6061 | 431.195 | 431.195 | 39.4112 | 67.2796 | 0 | 39.4112
Northwest Power Pool | CA |  | [p] | Turlock Irrigation District | NWPP | 115.4% | 115.4% | 750.4102 | 99.47% | 98.5% | 97.79% | 94.67% | 92.05% | 91.52% | 97.19% | 98.9% | 92.57% | 97.19% | 729.3069 | 24.3533 | 0 | 0 | 24.3533 | 111.3283 | 24.3533 | 0
Rocky Mountain Reserve Sharing Group | WECC |  | [q] | Public Service Co of Colorado | RMRSG | 113.9% | 113.9% | 9755.9217 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 9755.9217 | 0 | 0 | 0 | 0 | 1046.455 | 0 | 0
Southwest Reserve Sharing Group | WECC |  | [r] | Arizona Public Service Co | SRSG | 115% | 116.1% | 9698.9099 | 99.48% | 99.6% | 99.79% | 99.85% | 99.01% | 100% | 99.83% | 99.83% | 99.26% | 99.79% | 9678.2724 | 23.9601 | 106.688 | 23.9601 | 0 | 1199.1678 | 0 | 0
Southwest Reserve Sharing Group | WECC |  | [s] | El Paso Electric | SRSG | 110% | 116.1% | 2249.1157 | 93.28% | 90.45% | 89.49% | 94.67% | 93.55% | 94.38% | 91.4% | 90.94% | 91.7% | 91.7% | 2062.5191 | 216.6387 | 137.1961 | 137.1961 | 79.4426 | 760.9355 | 79.4426 | 0
Southwest Reserve Sharing Group | CA |  | [t] | Imperial Irrigation District | SRSG | 116.1% | 116.1% | 1175.6378 | 96.47% | 90.22% | 94.14% | 99.74% | 89.86% | 99.65% | 97.53% | 98.03% | 97.44% | 97.44% | 1145.5164 | 34.9709 | 0 | 0 | 34.9709 | 147.4289 | 34.9709 | 0
Southwest Reserve Sharing Group | WECC |  | [u] | Public Service Co of New Mexico | SRSG | 112% | 116.1% | 3181.9884 | 96.43% | 96.94% | 98.25% | 93.51% | 97.99% | 89.68% | 92.97% | 89.85% | 89.76% | 93.51% | 2975.4803 | 239.756 | 130.4615 | 130.4615 | 109.2944 | 1148.8404 | 109.2944 | 0
Southwest Reserve Sharing Group | WECC |  | [v] | Salt River Project | SRSG | 116.1% | 116.1% | 9313.1155 | 99.54% | 99.36% | 99.92% | 99.36% | 99.19% | 99.75% | 99.87% | 100% | 99.93% | 99.75% | 9290.0483 | 26.781 | 0 | 0 | 26.781 | 961.1537 | 26.781 | 0
Southwest Reserve Sharing Group | WECC |  | [w] | Tucson Electric Power Co | SRSG | 115% | 116.1% | 3863.052 | 99.1% | 97.87% | 99.56% | 98.44% | 99.54% | 98.63% | 97.77% | 98.29% | 90.35% | 98.44% | 3802.9075 | 69.8278 | 42.4936 | 42.4936 | 27.3342 | 457.877 | 27.3342 | 0
|  |  |  | Total Within Sub-Regions |  |  |  | 142490.2051 | [10 empty] | 137110.7373 | 6210.5396 | 4982.2587 | 4480.5615 | 1729.9781 | 17972.8044 | 967.0583 | 762.9198
California |  | CA |  | CA | WECC | 115% | 115% | 50154.1276 | 99.77% | 99.02% | 97.87% | 93.35% | 97.81% | 93.66% | 99.8% | 99.53% | 96.86% | 97.87% | 49083.6471 | 1231.0526 |  |  | 1231.0526 | 10104.5312 | 1231.0526 | 0
Northwest Power Pool |  | WECC |  | NWPP | WECC | 115.4% | 115.4% | 48245.944 | 99.85% | 93.7% | 93.91% | 99.24% | 99.11% | 99.39% | 98.87% | 96.86% | 98.55% | 98.87% | 47701.4389 | 628.3589 |  |  | 628.3589 | 12609.4688 | 628.3589 | 0
Rocky Mountain Reserve Sharing Group |  | WECC |  | RMRSG | WECC | 113.9% | 113.9% | 9755.9217 | 95.11% | 79.61% | 77.94% | 85.9% | 93.01% | 90.67% | 71.54% | 83.61% | 67.62% | 83.61% | 8157.3841 | 1820.7344 |  |  | 1820.7344 | 496.3187 | 496.3187 | 1324.4157
Southwest Reserve Sharing Group |  | WECC |  | SRSG | WECC | 116.1% | 116.1% | 28954.7439 | 98.31% | 97.65% | 94.7% | 99.56% | 94.06% | 99.22% | 97.22% | 96.37% | 94.34% | 97.22% | 28148.8113 | 935.6877 |  |  | 935.6877 | 5573.4702 | 935.6877 | 0
|  |  |  | Total Across Sub-Regions |  |  |  | 137110.7373 | [10 empty] | 133091.2814 | 4615.8336 |  |  | 4615.8336 | 28783.7889 | 3291.4179 | 1324.4157
Sources and Notes:
|  |  | [1] | Based on Utility IRPs. If no source available, uses an import-adjusted Margin.
|  |  | [2] | NERC Reference Margin Level from 2015 LTRA
|  |  | [3] | 2030 Non-coincident peak loads based on Brattle analysis of CEC and WECC LAR data
|  |  | [4] | Median coincidence factor from 2006-2014
|  |  | [5] | [4] * [3]
|  |  | [6] | MAX( [2] x [3] x (1- [4]), 0 )
|  |  | [7] | ([2] - [1]) x [3]
|  |  | [8] | MIN([6],[7])
|  |  | [9] | [2] x (1- [4]) x [3] - [8]
|  |  | [10] | Based on analysis using 2015 WECC LAR zonal flow limits
|  |  | [11] | MAX(MIN([10] - [8],[9]), 0)
|  |  | [12] | [9] - [11]

## 2020 Regional ISO
[6 empty] | 1 | 2 | 3 | [9 empty] | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Multi-Year Peak Loads by BAA for WECC without BPA and WAPA
| Within-Subregion Geographic Indicator | Within-Subregion Geographic Indicator | Balancing Authority Area |  | WECC Subregion | BAA Planning Reserve Margin | NERC Planning Reserve Reference Level | Non-Coincident Peak Load | 2006 CF | 2007 CF | 2008 CF | 2009 CF | 2010 CF | 2011 CF | 2012 CF | 2013 CF | 2014 CF | Median Coincidence Factor | Share of Coincident Peak | Potential Regionalization Capacity Savings | Capacity Savings Already Captured - Within or Across Sub-Regions | Capacity Savings Already Captured | Potential Capacity Savings from Market Integration | Import Limit | Incremental Capacity Savings with current Tx | Incremental Capacity Savings Requiring Tx Upgrades
[6 empty] | % | % | MW | [9 empty] | % | MW | MW | MW | MW | MW | MW | MW | MW | bar: 2006 CF to 2014 CF
[6 empty] | [1] | [2] | [3] | [9 empty] | [4] | [5] | [6] | [7] | [8] | [9] | [10] | [11] | [12]
California | CA |  | [a] | California Independent System Operator | CA | 115% | 115% | 47009.5734 | 100% | 99.91% | 100% | 99.94% | 100% | 100% | 100% | 99.85% | 99.95% | 100% | 47009.5734 | 0 | 0 | 0 | 0 | 3638.6717 | 0 | 0
California | CA |  | [b] | Los Angeles Dept of Water & Power | CA | 115% | 115% | 6359.2093 | 99.31% | 98.94% | 99.9% | 99.99% | 91.84% | 95.5% | 95.52% | 92.69% | 95.9% | 95.9% | 6098.4057 | 299.9242 | 0 | 0 | 299.9242 | 3750 | 299.9242 | 0
Northwest Power Pool | WECC |  | [c] | Avista Corp | NWPP | 104% | 115.4% | 2311 | 96.04% | 88.5% | 80.56% | 80.06% | 82.97% | 85.94% | 97.95% | 89.14% | 86.8% | 86.8% | 2006.0213 | 351.9454 | 263.454 | 263.454 | 88.4914 | 150.8082 | 0 | 88.4914
Northwest Power Pool | CA |  | [d] | Balancing Authority of Northern California | NWPP | 115.4% | 115.4% | 4594.5343 | 97.4% | 98.51% | 98.17% | 93.51% | 87.12% | 83.01% | 97.6% | 98.58% | 89.97% | 97.4% | 4475.2599 | 137.6427 | 0 | 0 | 137.6427 | 0 | 0 | 137.6427
Northwest Power Pool | WECC |  | [e] | Idaho Power Co | NWPP | 115.4% | 115.4% | 4006 | 99.9% | 98.34% | 93.9% | 91.19% | 93.56% | 95.67% | 92.49% | 99.65% | 97.79% | 95.67% | 3832.3418 | 200.4016 | 0 | 0 | 200.4016 | 1695.8049 | 200.4016 | 0
Northwest Power Pool | WECC |  | [f] | Nevada Power Co | NWPP | 112% | 115.4% | 8402 | 96.92% | 100% | 98.56% | 99.31% | 93.25% | 100% | 95.54% | 99.6% | 84.8% | 98.56% | 8280.8259 | 139.8349 | 285.668 | 139.8349 | 0 | 500 | 0 | 0
Northwest Power Pool | WECC |  | [g] | Northwestern Energy | NWPP | 110% | 115.4% | 1880 | 96.88% | 94.59% | 84.58% | 79.63% | 85.9% | 92.54% | 91.77% | 97.63% | 89.2% | 91.77% | 1725.2203 | 178.6157 | 101.52 | 101.52 | 77.0957 | 460.333 | 77.0957 | 0
Northwest Power Pool | WECC |  | [h] | PacifiCorp | NWPP | 113% | 115.4% | 13234 | 99.89% | 97.17% | 99.93% | 99.81% | 98.5% | 99.55% | 97.62% | 99.89% | 99% | 99.55% | 13174.4839 | 68.6816 | 317.616 | 68.6816 | 0 | 1046.5898 | 0 | 0
Northwest Power Pool | WECC |  | [i] | Portland General Electric | NWPP | 108% | 115.4% | 3753 | 99.45% | 87.88% | 86.49% | 96.25% | 94.54% | 92.06% | 89.61% | 90.55% | 87.37% | 90.55% | 3398.5097 | 409.0818 | 277.722 | 277.722 | 131.3598 | 244.9083 | 0 | 131.3598
Northwest Power Pool | WECC |  | [j] | PUD No 1 of Chelan County | NWPP | 84% | 115.4% | 733 | 69.54% | 69.37% | 61.44% | 66.56% | 66.45% | 74.73% | 74.96% | 70.52% | 69.34% | 69.37% | 508.5168 | 259.0536 | 230.162 | 230.162 | 28.8916 | 47.8332 | 0 | 28.8916
Northwest Power Pool | WECC |  | [k] | PUD No 1 of Douglas County | NWPP | 77% | 115.4% | 393 | 64.95% | 64.54% | 55.97% | 63.23% | 58.51% | 60.8% | 66.81% | 62.22% | 64.57% | 63.23% | 248.5064 | 166.7456 | 150.912 | 150.912 | 15.8336 | 25.6459 | 0 | 15.8336
Northwest Power Pool | WECC |  | [l] | PUD No 2 of Grant County | NWPP | 115.4% | 115.4% | 855 | 97.08% | 94.78% | 94.75% | 94.43% | 96.03% | 99.06% | 98.49% | 94.06% | 96.93% | 96.03% | 821.0586 | 39.1684 | 0 | 0 | 39.1684 | 55.7945 | 39.1684 | 0
Northwest Power Pool | WECC |  | [m] | Puget Sound Energy Inc | NWPP | 83% | 115.4% | 5157 | 71.49% | 65.64% | 62.1% | 70.66% | 68.22% | 68.66% | 69.52% | 69.88% | 67.5% | 68.66% | 3541.0194 | 1864.8417 | 1670.868 | 1670.868 | 193.9737 | 336.5287 | 0 | 193.9737
Northwest Power Pool | WECC |  | [n] | Seattle City Light | NWPP | 87% | 115.4% | 1830 | 77.45% | 68.92% | 67.88% | 76.91% | 70.84% | 72.23% | 72.06% | 73.61% | 70.88% | 72.06% | 1318.7521 | 589.9801 | 519.72 | 519.72 | 70.2601 | 119.4197 | 0 | 70.2601
Northwest Power Pool | WECC |  | [o] | Tacoma Power | NWPP | 75% | 115.4% | 1031 | 66.28% | 59.55% | 58.44% | 61.79% | 60.86% | 64.01% | 64.83% | 63.49% | 60.55% | 61.79% | 637.0708 | 454.5942 | 416.524 | 416.524 | 38.0702 | 67.2796 | 0 | 38.0702
Northwest Power Pool | CA |  | [p] | Turlock Irrigation District | NWPP | 115.4% | 115.4% | 676 | 99.47% | 98.5% | 97.79% | 94.67% | 92.05% | 91.52% | 97.19% | 98.9% | 92.57% | 97.19% | 656.9892 | 21.9384 | 0 | 0 | 21.9384 | 111.3283 | 21.9384 | 0
Rocky Mountain Reserve Sharing Group | WECC |  | [q] | Public Service Co of Colorado | RMRSG | 113.9% | 113.9% | 8740 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 8740 | 0 | 0 | 0 | 0 | 1046.455 | 0 | 0
Southwest Reserve Sharing Group | WECC |  | [r] | Arizona Public Service Co | SRSG | 115% | 116.1% | 7654 | 99.48% | 99.6% | 99.79% | 99.85% | 99.01% | 100% | 99.83% | 99.83% | 99.26% | 99.79% | 7637.7137 | 18.9083 | 84.194 | 18.9083 | 0 | 1199.1678 | 0 | 0
Southwest Reserve Sharing Group | WECC |  | [s] | El Paso Electric | SRSG | 110% | 116.1% | 1944 | 93.28% | 90.45% | 89.49% | 94.67% | 93.55% | 94.38% | 91.4% | 90.94% | 91.7% | 91.7% | 1782.7171 | 187.2494 | 118.584 | 118.584 | 68.6654 | 760.9355 | 68.6654 | 0
Southwest Reserve Sharing Group | CA |  | [t] | Imperial Irrigation District | SRSG | 116.1% | 116.1% | 1049 | 96.47% | 90.22% | 94.14% | 99.74% | 89.86% | 99.65% | 97.53% | 98.03% | 97.44% | 97.44% | 1022.1232 | 31.2039 | 0 | 0 | 31.2039 | 147.4289 | 31.2039 | 0
Southwest Reserve Sharing Group | WECC |  | [u] | Public Service Co of New Mexico | SRSG | 112% | 116.1% | 2935 | 96.43% | 96.94% | 98.25% | 93.51% | 97.99% | 89.68% | 92.97% | 89.85% | 89.76% | 93.51% | 2744.5212 | 221.1459 | 120.335 | 120.335 | 100.8109 | 1148.8404 | 100.8109 | 0
Southwest Reserve Sharing Group | WECC |  | [v] | Salt River Project | SRSG | 116.1% | 116.1% | 7431 | 99.54% | 99.36% | 99.92% | 99.36% | 99.19% | 99.75% | 99.87% | 100% | 99.93% | 99.75% | 7412.5945 | 21.3688 | 0 | 0 | 21.3688 | 961.1537 | 21.3688 | 0
Southwest Reserve Sharing Group | WECC |  | [w] | Tucson Electric Power Co | SRSG | 115% | 116.1% | 3540 | 99.1% | 97.87% | 99.56% | 98.44% | 99.54% | 98.63% | 97.77% | 98.29% | 90.35% | 98.44% | 3484.8851 | 63.9883 | 38.94 | 38.94 | 25.0483 | 457.877 | 25.0483 | 0
|  |  |  | Total Within Sub-Regions |  |  |  | 135517.3171 | [10 empty] | 130557.1102 | 5726.3146 | 4596.219 | 4136.1659 | 1590.1487 | 17972.8044 | 885.6257 | 704.523
California |  | CA |  | CA | WECC | 115% | 115% | 53107.9791 | 99.77% | 99.02% | 97.87% | 93.35% | 97.81% | 93.66% | 99.8% | 99.53% | 96.86% | 97.87% | 51974.4521 | 1303.556 |  |  | 1303.556 | 10104.5312 | 1303.556 | 0
Northwest Power Pool |  | WECC |  | NWPP | WECC | 115.4% | 115.4% | 44624.5762 | 99.85% | 93.7% | 93.91% | 99.24% | 99.11% | 99.39% | 98.87% | 96.86% | 98.55% | 98.87% | 44120.9419 | 581.194 |  |  | 581.194 | 12609.4688 | 581.194 | 0
Rocky Mountain Reserve Sharing Group |  | WECC |  | RMRSG | WECC | 113.9% | 113.9% | 8740 | 95.11% | 79.61% | 77.94% | 85.9% | 93.01% | 90.67% | 71.54% | 83.61% | 67.62% | 83.61% | 7307.9242 | 1631.1343 |  |  | 1631.1343 | 496.3187 | 496.3187 | 1134.8156
Southwest Reserve Sharing Group |  | WECC |  | SRSG | WECC | 116.1% | 116.1% | 24084.5549 | 98.31% | 97.65% | 94.7% | 99.56% | 94.06% | 99.22% | 97.22% | 96.37% | 94.34% | 97.22% | 23414.1802 | 778.305 |  |  | 778.305 | 5573.4702 | 778.305 | 0
|  |  |  | Total Across Sub-Regions |  |  |  | 130557.1102 | [10 empty] | 126817.4985 | 4294.1893 |  |  | 4294.1893 | 28783.7889 | 3159.3737 | 1134.8156
Sources and Notes:
|  |  | [1] | Based on Utility IRPs. If no source available, uses an import-adjusted Margin.
|  |  | [2] | NERC Reference Margin Level from 2015 LTRA
|  |  | [3] | 2020 Non-coincident peak loads based on Brattle analysis of CEC and WECC LAR data
|  |  | [4] | Median coincidence factor from 2006-2014
|  |  | [5] | [4] * [3]
|  |  | [6] | MAX( [2] x [3] x (1- [4]), 0 )
|  |  | [7] | ([2] - [1]) x [3]
|  |  | [8] | MIN([6],[7])
|  |  | [9] | [2] x (1- [4]) x [3] - [8]
|  |  | [10] | Based on analysis using 2015 WECC LAR zonal flow limits
|  |  | [11] | MAX(MIN([10] - [8],[9]), 0)
|  |  | [12] | [9] - [11]

## 2020 CAISO+PAC
|  |  |  | 1 | 2 | [9 empty] | 3 | 4 | 5 | 6 | 7 | 8
Multi-Year Peak Loads by BAA for CAISO-PAC
| Balancing Area Authority |  | WECC Subregion | Planning Reserve Margin | Non-Coincident Peak Load | 2006 CF | 2007 CF | 2008 CF | 2009 CF | 2010 CF | 2011 CF | 2012 CF | 2013 CF | 2014 CF | Median Coincidence Factor | Share of Coincident Peak | Potential Regionalization Capacity Savings | Import Limit | Incremental Capacity Savings with current Tx | Incremental Capacity Savings Requiring Tx Upgrades
|  |  |  | % | MW | [9 empty] | % | MW | MW | MW | MW | MW | bar: 2006 CF to 2014 CF
|  |  |  | [1] | [2] | [9 empty] | [3] | [4] | [5] | [6] | [7] | [8]
California | California Independent System Operator |  | CA | 115% | 47009.5734 | 100% | 100% | 99.62% | 100% | 99.66% | 99.52% | 100% | 99.65% | 99.19% | 99.66% | 46849.3135 | 184.2989 | 982 | 184.2989 | 0
Southwest Reserve Sharing Group | PacifiCorp |  | NWPP | 113% | 13234 | 98.9% | 91.88% | 90.81% | 88.16% | 95.91% | 92.19% | 95.64% | 97.51% | 87.77% | 92.19% | 12200.751 | 1167.5714 | 776 | 776 | 391.5714
| Total |  |  |  | 60243.5734 | [10 empty] | 59050.0645 | 1351.8702 | 1758 | 960.2989 | 391.5714
Sources and Notes:
| [1] | Based on PacifiCorp 2014 IRP and CAISO published RM.
| [2] | 2020 Non-coincident peak loads based on Brattle analysis of CEC and WECC LAR data
| [3] | Median coincidence factor from 2006-2014
| [4] | [2] * [3]
| [5] | [1] * ([2] - [4])
| [6] | Import limits as reported in E3's PacifiCorp Market Integration Study Report
| [7] | MAX([5],[6])
| [8] | [5] - [7]

## 2014
|  |  | 1 | 2 | 3 | 4
Non-Coincident Peak Loads CAISO-PAC
|  | Sub-Region | 2014 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 44395.25 | 53028.2425 | 44036.75 | 0.99192
Northwest Power Pool | PacifiCorp | NWPP | 10244.025 | 53028.2425 | 8991.4925 | 0.87773
Non-Coincident Peak Loads WECC (no BPA and WAPA)
|  | Sub-Region | 2014 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 44395.25 | 50397.0325 | 44375 | 0.99954
California | Los Angeles Dept of Water & Power | CA | 6279.57 | 50397.0325 | 6022.0325 | 0.95899
Northwest Power Pool | Avista Corp | NWPP | 2332 | 35229.9075 | 2024.25 | 0.86803
Northwest Power Pool | Balancing Authority of Northern California | NWPP | 2946.25 | 35229.9075 | 2650.75 | 0.8997
Northwest Power Pool | Idaho Power Co | NWPP | 3548.25 | 35229.9075 | 3469.75 | 0.97788
Northwest Power Pool | Nevada Power Co | NWPP | 5784.75 | 35229.9075 | 4905.25 | 0.84796
Northwest Power Pool | Northwestern Energy | NWPP | 1740.5 | 35229.9075 | 1552.5 | 0.89199
Northwest Power Pool | PacifiCorp | NWPP | 10244.025 | 35229.9075 | 10141.6575 | 0.99001
Northwest Power Pool | Portland General Electric | NWPP | 3820.75 | 35229.9075 | 3338 | 0.87365
Northwest Power Pool | PUD No 1 of Chelan County | NWPP | 711 | 35229.9075 | 493 | 0.69339
Northwest Power Pool | PUD No 1 of Douglas County | NWPP | 377.5 | 35229.9075 | 243.75 | 0.6457
Northwest Power Pool | PUD No 2 of Grant County | NWPP | 715.5 | 35229.9075 | 693.5 | 0.96925
Northwest Power Pool | Puget Sound Energy Inc | NWPP | 4813 | 35229.9075 | 3249 | 0.67505
Northwest Power Pool | Seattle City Light | NWPP | 1850.75 | 35229.9075 | 1311.75 | 0.70877
Northwest Power Pool | Tacoma Power | NWPP | 995 | 35229.9075 | 602.5 | 0.60553
Northwest Power Pool | Turlock Irrigation District | NWPP | 598.75 | 35229.9075 | 554.25 | 0.92568
Rocky Mountain Reserve Sharing Group | Public Service Co of Colorado | RMRSG | 7393 | 7393 | 7393 | 1
Southwest Reserve Sharing Group | Arizona Public Service Co | SRSG | 7103.5 | 21303.5 | 7051.25 | 0.99264
Southwest Reserve Sharing Group | El Paso Electric | SRSG | 1750.75 | 21303.5 | 1605.5 | 0.91704
Southwest Reserve Sharing Group | Imperial Irrigation District | SRSG | 975.75 | 21303.5 | 950.75 | 0.97438
Southwest Reserve Sharing Group | Public Service Co of New Mexico | SRSG | 1943.75 | 21303.5 | 1744.75 | 0.89762
Southwest Reserve Sharing Group | Salt River Project | SRSG | 6787.25 | 21303.5 | 6782.5 | 0.9993
Southwest Reserve Sharing Group | Tucson Electric Power Co | SRSG | 3507.25 | 21303.5 | 3168.75 | 0.90349
California | CA | WECC | 50397.0325 | 108630.7725 | 48813.76 | 0.96858
Northwest Power Pool | NWPP | WECC | 35229.9075 | 108630.7725 | 34718.7625 | 0.98549
Rocky Mountain Reserve Sharing Group | RMRSG | WECC | 7393 | 108630.7725 | 4999.5 | 0.67625
Southwest Reserve Sharing Group | SRSG | WECC | 21303.5 | 108630.7725 | 20098.75 | 0.94345
Source: 4 CP Non-Coincident and Coincident Peak Loads calculated using FERC Form 714 data obtained via ABB's GridView

## 2013
|  |  | 1 | 2 | 3 | 4
Non-Coincident Peak Loads CAISO-PAC
|  | Sub-Region | 2013 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 44759 | 54778.315 | 44603 | 0.99651
Northwest Power Pool | PacifiCorp | NWPP | 10435.5375 | 54778.315 | 10175.315 | 0.97506
Non-Coincident Peak Loads WECC (no BPA and WAPA)
|  | Sub-Region | 2013 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 44759 | 50115.2825 | 44693.5 | 0.99854
California | Los Angeles Dept of Water & Power | CA | 5849.2875 | 50115.2825 | 5421.7825 | 0.92691
Northwest Power Pool | Avista Corp | NWPP | 2248.75 | 37576.7175 | 2004.5 | 0.89138
Northwest Power Pool | Balancing Authority of Northern California | NWPP | 2982.5 | 37576.7175 | 2940.25 | 0.98583
Northwest Power Pool | Idaho Power Co | NWPP | 3769 | 37576.7175 | 3755.75 | 0.99648
Northwest Power Pool | Nevada Power Co | NWPP | 6059.25 | 37576.7175 | 6035.25 | 0.99604
Northwest Power Pool | Northwestern Energy | NWPP | 1717 | 37576.7175 | 1676.25 | 0.97627
Northwest Power Pool | PacifiCorp | NWPP | 10435.5375 | 37576.7175 | 10423.7175 | 0.99887
Northwest Power Pool | Portland General Electric | NWPP | 3877.5 | 37576.7175 | 3511.25 | 0.90554
Northwest Power Pool | PUD No 1 of Chelan County | NWPP | 685.25 | 37576.7175 | 483.25 | 0.70522
Northwest Power Pool | PUD No 1 of Douglas County | NWPP | 352 | 37576.7175 | 219 | 0.62216
Northwest Power Pool | PUD No 2 of Grant County | NWPP | 665.25 | 37576.7175 | 625.75 | 0.94062
Northwest Power Pool | Puget Sound Energy Inc | NWPP | 4758.25 | 37576.7175 | 3325 | 0.69879
Northwest Power Pool | Seattle City Light | NWPP | 1835.25 | 37576.7175 | 1351 | 0.73614
Northwest Power Pool | Tacoma Power | NWPP | 973.75 | 37576.7175 | 618.25 | 0.63492
Northwest Power Pool | Turlock Irrigation District | NWPP | 614.25 | 37576.7175 | 607.5 | 0.98901
Rocky Mountain Reserve Sharing Group | Public Service Co of Colorado | RMRSG | 7656.25 | 7656.25 | 7656.25 | 1
Southwest Reserve Sharing Group | Arizona Public Service Co | SRSG | 7092.46 | 21193.085 | 7080.335 | 0.99829
Southwest Reserve Sharing Group | El Paso Electric | SRSG | 1728.25 | 21193.085 | 1571.75 | 0.90945
Southwest Reserve Sharing Group | Imperial Irrigation District | SRSG | 977.25 | 21193.085 | 958 | 0.9803
Southwest Reserve Sharing Group | Public Service Co of New Mexico | SRSG | 2061.75 | 21193.085 | 1852.5 | 0.89851
Southwest Reserve Sharing Group | Salt River Project | SRSG | 6634.75 | 21193.085 | 6634.75 | 1
Southwest Reserve Sharing Group | Tucson Electric Power Co | SRSG | 3149.75 | 21193.085 | 3095.75 | 0.98286
California | CA | WECC | 50115.2825 | 113102.195 | 49878.1975 | 0.99527
Northwest Power Pool | NWPP | WECC | 37576.7175 | 113102.195 | 36398.16 | 0.96864
Rocky Mountain Reserve Sharing Group | RMRSG | WECC | 7656.25 | 113102.195 | 6401.75 | 0.83615
Southwest Reserve Sharing Group | SRSG | WECC | 21193.085 | 113102.195 | 20424.0875 | 0.96371
Source: 4 CP Non-Coincident and Coincident Peak Loads calculated using FERC Form 714 data obtained via ABB's GridView

## 2012
|  |  | 1 | 2 | 3 | 4
Non-Coincident Peak Loads CAISO-PAC
|  | Sub-Region | 2012 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 46283.5 | 55628.145 | 46283.5 | 1
Northwest Power Pool | PacifiCorp | NWPP | 9770.515 | 55628.145 | 9344.645 | 0.95641
Non-Coincident Peak Loads WECC (no BPA and WAPA)
|  | Sub-Region | 2012 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 46283.5 | 51794.645 | 46283.5 | 1
California | Los Angeles Dept of Water & Power | CA | 5769.43 | 51794.645 | 5511.145 | 0.95523
Northwest Power Pool | Avista Corp | NWPP | 2021.5 | 35381.1325 | 1980 | 0.97947
Northwest Power Pool | Balancing Authority of Northern California | NWPP | 2905.5 | 35381.1325 | 2835.75 | 0.97599
Northwest Power Pool | Idaho Power Co | NWPP | 3558.75 | 35381.1325 | 3291.5 | 0.9249
Northwest Power Pool | Nevada Power Co | NWPP | 6178.5 | 35381.1325 | 5903 | 0.95541
Northwest Power Pool | Northwestern Energy | NWPP | 1764.25 | 35381.1325 | 1619 | 0.91767
Northwest Power Pool | PacifiCorp | NWPP | 9770.515 | 35381.1325 | 9538.1325 | 0.97622
Northwest Power Pool | Portland General Electric | NWPP | 3613.5 | 35381.1325 | 3238 | 0.89608
Northwest Power Pool | PUD No 1 of Chelan County | NWPP | 659 | 35381.1325 | 494 | 0.74962
Northwest Power Pool | PUD No 1 of Douglas County | NWPP | 337.5 | 35381.1325 | 225.5 | 0.66815
Northwest Power Pool | PUD No 2 of Grant County | NWPP | 662.5 | 35381.1325 | 652.5 | 0.98491
Northwest Power Pool | Puget Sound Energy Inc | NWPP | 4524.75 | 35381.1325 | 3145.75 | 0.69523
Northwest Power Pool | Seattle City Light | NWPP | 1779 | 35381.1325 | 1282 | 0.72063
Northwest Power Pool | Tacoma Power | NWPP | 907.75 | 35381.1325 | 588.5 | 0.64831
Northwest Power Pool | Turlock Irrigation District | NWPP | 604.5 | 35381.1325 | 587.5 | 0.97188
Rocky Mountain Reserve Sharing Group | Public Service Co of Colorado | RMRSG | 7861.5 | 7861.5 | 7861.5 | 1
Southwest Reserve Sharing Group | Arizona Public Service Co | SRSG | 7301 | 21286.75 | 7288.75 | 0.99832
Southwest Reserve Sharing Group | El Paso Electric | SRSG | 1683.5 | 21286.75 | 1538.75 | 0.91402
Southwest Reserve Sharing Group | Imperial Irrigation District | SRSG | 981.75 | 21286.75 | 957.5 | 0.9753
Southwest Reserve Sharing Group | Public Service Co of New Mexico | SRSG | 2009.75 | 21286.75 | 1868.5 | 0.92972
Southwest Reserve Sharing Group | Salt River Project | SRSG | 6712.75 | 21286.75 | 6704 | 0.9987
Southwest Reserve Sharing Group | Tucson Electric Power Co | SRSG | 2996 | 21286.75 | 2929.25 | 0.97772
California | CA | WECC | 51794.645 | 112992.6225 | 51692.8025 | 0.99803
Northwest Power Pool | NWPP | WECC | 35381.1325 | 112992.6225 | 34981.82 | 0.98871
Rocky Mountain Reserve Sharing Group | RMRSG | WECC | 7861.5 | 112992.6225 | 5623.75 | 0.71535
Southwest Reserve Sharing Group | SRSG | WECC | 21286.75 | 112992.6225 | 20694.25 | 0.97217
Source: 4 CP Non-Coincident and Coincident Peak Loads calculated using FERC Form 714 data obtained via ABB's GridView

## 2011
|  |  | 1 | 2 | 3 | 4
Non-Coincident Peak Loads CAISO-PAC
|  | Sub-Region | 2011 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 44883.25 | 53326.11 | 44669 | 0.99523
Northwest Power Pool | PacifiCorp | NWPP | 9390.2575 | 53326.11 | 8657.11 | 0.92192
Non-Coincident Peak Loads WECC (no BPA and WAPA)
|  | Sub-Region | 2011 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 44883.25 | 50438.3825 | 44883.25 | 1
California | Los Angeles Dept of Water & Power | CA | 5816.635 | 50438.3825 | 5555.1325 | 0.95504
Northwest Power Pool | Avista Corp | NWPP | 2134.75 | 34230.5275 | 1834.5 | 0.85935
Northwest Power Pool | Balancing Authority of Northern California | NWPP | 2799.5 | 34230.5275 | 2324 | 0.83015
Northwest Power Pool | Idaho Power Co | NWPP | 3293 | 34230.5275 | 3150.25 | 0.95665
Northwest Power Pool | Nevada Power Co | NWPP | 5917.25 | 34230.5275 | 5917.25 | 1
Northwest Power Pool | Northwestern Energy | NWPP | 1666.5 | 34230.5275 | 1542.25 | 0.92544
Northwest Power Pool | PacifiCorp | NWPP | 9390.2575 | 34230.5275 | 9348.0275 | 0.9955
Northwest Power Pool | Portland General Electric | NWPP | 3563.25 | 34230.5275 | 3280.5 | 0.92065
Northwest Power Pool | PUD No 1 of Chelan County | NWPP | 626.25 | 34230.5275 | 468 | 0.74731
Northwest Power Pool | PUD No 1 of Douglas County | NWPP | 338 | 34230.5275 | 205.5 | 0.60799
Northwest Power Pool | PUD No 2 of Grant County | NWPP | 662.5 | 34230.5275 | 656.25 | 0.99057
Northwest Power Pool | Puget Sound Energy Inc | NWPP | 4559.5 | 34230.5275 | 3130.75 | 0.68664
Northwest Power Pool | Seattle City Light | NWPP | 1737.5 | 34230.5275 | 1255 | 0.7223
Northwest Power Pool | Tacoma Power | NWPP | 925.25 | 34230.5275 | 592.25 | 0.6401
Northwest Power Pool | Turlock Irrigation District | NWPP | 574.75 | 34230.5275 | 526 | 0.91518
Rocky Mountain Reserve Sharing Group | Public Service Co of Colorado | RMRSG | 7764.75 | 7764.75 | 7764.75 | 1
Southwest Reserve Sharing Group | Arizona Public Service Co | SRSG | 7165.5 | 21051.5 | 7165.5 | 1
Southwest Reserve Sharing Group | El Paso Electric | SRSG | 1695 | 21051.5 | 1599.75 | 0.94381
Southwest Reserve Sharing Group | Imperial Irrigation District | SRSG | 987.25 | 21051.5 | 983.75 | 0.99645
Southwest Reserve Sharing Group | Public Service Co of New Mexico | SRSG | 1982 | 21051.5 | 1777.5 | 0.89682
Southwest Reserve Sharing Group | Salt River Project | SRSG | 6560.75 | 21051.5 | 6544.5 | 0.99752
Southwest Reserve Sharing Group | Tucson Electric Power Co | SRSG | 3022 | 21051.5 | 2980.5 | 0.98627
California | CA | WECC | 50438.3825 | 109188.1775 | 47240.4275 | 0.9366
Northwest Power Pool | NWPP | WECC | 34230.5275 | 109188.1775 | 34020.5 | 0.99386
Rocky Mountain Reserve Sharing Group | RMRSG | WECC | 7764.75 | 109188.1775 | 7040 | 0.90666
Southwest Reserve Sharing Group | SRSG | WECC | 21051.5 | 109188.1775 | 20887.25 | 0.9922
Source: 4 CP Non-Coincident and Coincident Peak Loads calculated using FERC Form 714 data obtained via ABB's GridView

## 2010
|  |  | 1 | 2 | 3 | 4
Non-Coincident Peak Loads CAISO-PAC
|  | Sub-Region | 2010 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 46860 | 55720.2575 | 46700.25 | 0.99659
Northwest Power Pool | PacifiCorp | NWPP | 9405.0275 | 55720.2575 | 9020.0075 | 0.95906
Non-Coincident Peak Loads WECC (no BPA and WAPA)
|  | Sub-Region | 2010 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 46860 | 52422.75 | 46860 | 1
California | Los Angeles Dept of Water & Power | CA | 6057.25 | 52422.75 | 5562.75 | 0.91836
Northwest Power Pool | Avista Corp | NWPP | 2170 | 34013.7425 | 1800.5 | 0.82972
Northwest Power Pool | Balancing Authority of Northern California | NWPP | 2931.75 | 34013.7425 | 2554 | 0.87115
Northwest Power Pool | Idaho Power Co | NWPP | 3226.25 | 34013.7425 | 3018.5 | 0.93561
Northwest Power Pool | Nevada Power Co | NWPP | 6027.75 | 34013.7425 | 5621 | 0.93252
Northwest Power Pool | Northwestern Energy | NWPP | 1691 | 34013.7425 | 1452.5 | 0.85896
Northwest Power Pool | PacifiCorp | NWPP | 9405.0275 | 34013.7425 | 9264.2425 | 0.98503
Northwest Power Pool | Portland General Electric | NWPP | 3601.75 | 34013.7425 | 3405.25 | 0.94544
Northwest Power Pool | PUD No 1 of Chelan County | NWPP | 585 | 34013.7425 | 388.75 | 0.66453
Northwest Power Pool | PUD No 1 of Douglas County | NWPP | 352.5 | 34013.7425 | 206.25 | 0.58511
Northwest Power Pool | PUD No 2 of Grant County | NWPP | 661.25 | 34013.7425 | 635 | 0.9603
Northwest Power Pool | Puget Sound Energy Inc | NWPP | 4766.25 | 34013.7425 | 3251.5 | 0.68219
Northwest Power Pool | Seattle City Light | NWPP | 1817.5 | 34013.7425 | 1287.5 | 0.70839
Northwest Power Pool | Tacoma Power | NWPP | 979.25 | 34013.7425 | 596 | 0.60863
Northwest Power Pool | Turlock Irrigation District | NWPP | 578.75 | 34013.7425 | 532.75 | 0.92052
Rocky Mountain Reserve Sharing Group | Public Service Co of Colorado | RMRSG | 7539.75 | 7539.75 | 7539.75 | 1
Southwest Reserve Sharing Group | Arizona Public Service Co | SRSG | 6996 | 20699 | 6926.5 | 0.99007
Southwest Reserve Sharing Group | El Paso Electric | SRSG | 1611.75 | 20699 | 1507.75 | 0.93547
Southwest Reserve Sharing Group | Imperial Irrigation District | SRSG | 991 | 20699 | 890.5 | 0.89859
Southwest Reserve Sharing Group | Public Service Co of New Mexico | SRSG | 1982 | 20699 | 1942.25 | 0.97994
Southwest Reserve Sharing Group | Salt River Project | SRSG | 6478 | 20699 | 6425.5 | 0.9919
Southwest Reserve Sharing Group | Tucson Electric Power Co | SRSG | 3020.25 | 20699 | 3006.5 | 0.99545
California | CA | WECC | 52422.75 | 111463.12 | 51272.25 | 0.97805
Northwest Power Pool | NWPP | WECC | 34013.7425 | 111463.12 | 33709.62 | 0.99106
Rocky Mountain Reserve Sharing Group | RMRSG | WECC | 7539.75 | 111463.12 | 7012.5 | 0.93007
Southwest Reserve Sharing Group | SRSG | WECC | 20699 | 111463.12 | 19468.75 | 0.94056
Source: 4 CP Non-Coincident and Coincident Peak Loads calculated using FERC Form 714 data obtained via ABB's GridView

## 2009
|  |  | 1 | 2 | 3 | 4
Non-Coincident Peak Loads CAISO-PAC
|  | Sub-Region | 2009 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 45267.415 | 53540.535 | 45267.415 | 1
Northwest Power Pool | PacifiCorp | NWPP | 9384.4525 | 53540.535 | 8273.12 | 0.88158
Non-Coincident Peak Loads WECC (no BPA and WAPA)
|  | Sub-Region | 2009 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 45267.415 | 50908.2025 | 45238.4525 | 0.99936
California | Los Angeles Dept of Water & Power | CA | 5670.25 | 50908.2025 | 5669.75 | 0.99991
Northwest Power Pool | Avista Corp | NWPP | 2250 | 35465.795 | 1801.25 | 0.80056
Northwest Power Pool | Balancing Authority of Northern California | NWPP | 2841 | 35465.795 | 2656.5 | 0.93506
Northwest Power Pool | Idaho Power Co | NWPP | 3317.25 | 35465.795 | 3025 | 0.9119
Northwest Power Pool | Nevada Power Co | NWPP | 5960.75 | 35465.795 | 5919.5 | 0.99308
Northwest Power Pool | Northwestern Energy | NWPP | 1756.5 | 35465.795 | 1398.75 | 0.79633
Northwest Power Pool | PacifiCorp | NWPP | 9384.4525 | 35465.795 | 9366.295 | 0.99807
Northwest Power Pool | Portland General Electric | NWPP | 3984 | 35465.795 | 3834.75 | 0.96254
Northwest Power Pool | PUD No 1 of Chelan County | NWPP | 609.25 | 35465.795 | 405.5 | 0.66557
Northwest Power Pool | PUD No 1 of Douglas County | NWPP | 349.5 | 35465.795 | 221 | 0.63233
Northwest Power Pool | PUD No 2 of Grant County | NWPP | 650.5 | 35465.795 | 614.25 | 0.94427
Northwest Power Pool | Puget Sound Energy Inc | NWPP | 5111.75 | 35465.795 | 3612 | 0.70661
Northwest Power Pool | Seattle City Light | NWPP | 1848.25 | 35465.795 | 1421.5 | 0.76911
Northwest Power Pool | Tacoma Power | NWPP | 1041 | 35465.795 | 643.25 | 0.61792
Northwest Power Pool | Turlock Irrigation District | NWPP | 577 | 35465.795 | 546.25 | 0.94671
Rocky Mountain Reserve Sharing Group | Public Service Co of Colorado | RMRSG | 7225.25 | 7225.25 | 7225.25 | 1
Southwest Reserve Sharing Group | Arizona Public Service Co | SRSG | 7242.1 | 20932.2 | 7230.95 | 0.99846
Southwest Reserve Sharing Group | El Paso Electric | SRSG | 1566.25 | 20932.2 | 1482.75 | 0.94669
Southwest Reserve Sharing Group | Imperial Irrigation District | SRSG | 978.5 | 20932.2 | 976 | 0.99745
Southwest Reserve Sharing Group | Public Service Co of New Mexico | SRSG | 1895.25 | 20932.2 | 1772.25 | 0.9351
Southwest Reserve Sharing Group | Salt River Project | SRSG | 6620 | 20932.2 | 6577.5 | 0.99358
Southwest Reserve Sharing Group | Tucson Electric Power Co | SRSG | 2938.5 | 20932.2 | 2892.75 | 0.98443
California | CA | WECC | 50908.2025 | 109769.27 | 47524.0025 | 0.93352
Northwest Power Pool | NWPP | WECC | 35465.795 | 109769.27 | 35197.6925 | 0.99244
Rocky Mountain Reserve Sharing Group | RMRSG | WECC | 7225.25 | 109769.27 | 6206.5 | 0.859
Southwest Reserve Sharing Group | SRSG | WECC | 20932.2 | 109769.27 | 20841.075 | 0.99565
Source: 4 CP Non-Coincident and Coincident Peak Loads calculated using FERC Form 714 data obtained via ABB's GridView

## 2008
|  |  | 1 | 2 | 3 | 4
Non-Coincident Peak Loads CAISO-PAC
|  | Sub-Region | 2008 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 46192.5 | 54620.05 | 46019.25 | 0.99625
Northwest Power Pool | PacifiCorp | NWPP | 9471.66 | 54620.05 | 8600.8 | 0.90806
Non-Coincident Peak Loads WECC (no BPA and WAPA)
|  | Sub-Region | 2008 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 46192.5 | 52146.25 | 46192.5 | 1
California | Los Angeles Dept of Water & Power | CA | 5960 | 52146.25 | 5953.75 | 0.99895
Northwest Power Pool | Avista Corp | NWPP | 2328.75 | 35274.97 | 1876 | 0.80558
Northwest Power Pool | Balancing Authority of Northern California | NWPP | 3065.5 | 35274.97 | 3009.25 | 0.98165
Northwest Power Pool | Idaho Power Co | NWPP | 3490.25 | 35274.97 | 3277.25 | 0.93897
Northwest Power Pool | Nevada Power Co | NWPP | 5893.75 | 35274.97 | 5808.75 | 0.98558
Northwest Power Pool | Northwestern Energy | NWPP | 1796.25 | 35274.97 | 1519.25 | 0.84579
Northwest Power Pool | PacifiCorp | NWPP | 9471.66 | 35274.97 | 9464.72 | 0.99927
Northwest Power Pool | Portland General Electric | NWPP | 4036.75 | 35274.97 | 3491.5 | 0.86493
Northwest Power Pool | PUD No 1 of Chelan County | NWPP | 630.25 | 35274.97 | 387.25 | 0.61444
Northwest Power Pool | PUD No 1 of Douglas County | NWPP | 372.5 | 35274.97 | 208.5 | 0.55973
Northwest Power Pool | PUD No 2 of Grant County | NWPP | 618.5 | 35274.97 | 586 | 0.94745
Northwest Power Pool | Puget Sound Energy Inc | NWPP | 5141 | 35274.97 | 3192.75 | 0.62104
Northwest Power Pool | Seattle City Light | NWPP | 1889.25 | 35274.97 | 1282.5 | 0.67884
Northwest Power Pool | Tacoma Power | NWPP | 1000.25 | 35274.97 | 584.5 | 0.58435
Northwest Power Pool | Turlock Irrigation District | NWPP | 600 | 35274.97 | 586.75 | 0.97792
Rocky Mountain Reserve Sharing Group | Public Service Co of Colorado | RMRSG | 7918.5 | 7918.5 | 7918.5 | 1
Southwest Reserve Sharing Group | Arizona Public Service Co | SRSG | 7049.5 | 20788 | 7034.5 | 0.99787
Southwest Reserve Sharing Group | El Paso Electric | SRSG | 1512.75 | 20788 | 1353.75 | 0.89489
Southwest Reserve Sharing Group | Imperial Irrigation District | SRSG | 972.75 | 20788 | 915.75 | 0.9414
Southwest Reserve Sharing Group | Public Service Co of New Mexico | SRSG | 1928.5 | 20788 | 1894.75 | 0.9825
Southwest Reserve Sharing Group | Salt River Project | SRSG | 6578.75 | 20788 | 6573.75 | 0.99924
Southwest Reserve Sharing Group | Tucson Electric Power Co | SRSG | 3028.75 | 20788 | 3015.5 | 0.99563
California | CA | WECC | 52146.25 | 110016.6025 | 51033.25 | 0.97866
Northwest Power Pool | NWPP | WECC | 35274.97 | 110016.6025 | 33125.6025 | 0.93907
Rocky Mountain Reserve Sharing Group | RMRSG | WECC | 7918.5 | 110016.6025 | 6172 | 0.77944
Southwest Reserve Sharing Group | SRSG | WECC | 20788 | 110016.6025 | 19685.75 | 0.94698
Source: 4 CP Non-Coincident and Coincident Peak Loads calculated using FERC Form 714 data obtained via ABB's GridView

## 2007
|  |  | 1 | 2 | 3 | 4
Non-Coincident Peak Loads CAISO-PAC
|  | Sub-Region | 2007 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 48363.885 | 57301.135 | 48363.885 | 1
Northwest Power Pool | PacifiCorp | NWPP | 9726.75 | 57301.135 | 8937.25 | 0.91883
Non-Coincident Peak Loads WECC (no BPA and WAPA)
|  | Sub-Region | 2007 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 48363.885 | 54271.7225 | 48318.435 | 0.99906
California | Los Angeles Dept of Water & Power | CA | 6017.2375 | 54271.7225 | 5953.2875 | 0.98937
Northwest Power Pool | Avista Corp | NWPP | 2145 | 35526 | 1898.25 | 0.88497
Northwest Power Pool | Balancing Authority of Northern California | NWPP | 3061.5 | 35526 | 3016 | 0.98514
Northwest Power Pool | Idaho Power Co | NWPP | 3473.5 | 35526 | 3415.75 | 0.98337
Northwest Power Pool | Nevada Power Co | NWPP | 6261.25 | 35526 | 6261.25 | 1
Northwest Power Pool | Northwestern Energy | NWPP | 1714.75 | 35526 | 1622 | 0.94591
Northwest Power Pool | PacifiCorp | NWPP | 9726.75 | 35526 | 9451.5 | 0.9717
Northwest Power Pool | Portland General Electric | NWPP | 3657.75 | 35526 | 3214.25 | 0.87875
Northwest Power Pool | PUD No 1 of Chelan County | NWPP | 587.75 | 35526 | 407.75 | 0.69375
Northwest Power Pool | PUD No 1 of Douglas County | NWPP | 337.75 | 35526 | 218 | 0.64545
Northwest Power Pool | PUD No 2 of Grant County | NWPP | 570.25 | 35526 | 540.5 | 0.94783
Northwest Power Pool | Puget Sound Energy Inc | NWPP | 4735.5 | 35526 | 3108.5 | 0.65642
Northwest Power Pool | Seattle City Light | NWPP | 1763.75 | 35526 | 1215.5 | 0.68916
Northwest Power Pool | Tacoma Power | NWPP | 949.25 | 35526 | 565.25 | 0.59547
Northwest Power Pool | Turlock Irrigation District | NWPP | 600.5 | 35526 | 591.5 | 0.98501
Rocky Mountain Reserve Sharing Group | Public Service Co of Colorado | RMRSG | 8085.25 | 8085.25 | 8085.25 | 1
Southwest Reserve Sharing Group | Arizona Public Service Co | SRSG | 7579.25 | 20971.75 | 7549 | 0.99601
Southwest Reserve Sharing Group | El Paso Electric | SRSG | 1503 | 20971.75 | 1359.5 | 0.90452
Southwest Reserve Sharing Group | Imperial Irrigation District | SRSG | 989.5 | 20971.75 | 892.75 | 0.90222
Southwest Reserve Sharing Group | Public Service Co of New Mexico | SRSG | 1999.25 | 20971.75 | 1938 | 0.96936
Southwest Reserve Sharing Group | Salt River Project | SRSG | 6691 | 20971.75 | 6648 | 0.99357
Southwest Reserve Sharing Group | Tucson Electric Power Co | SRSG | 2640.75 | 20971.75 | 2584.5 | 0.9787
California | CA | WECC | 54271.7225 | 113943.8325 | 53738.3325 | 0.99017
Northwest Power Pool | NWPP | WECC | 35526 | 113943.8325 | 33289.5 | 0.93705
Rocky Mountain Reserve Sharing Group | RMRSG | WECC | 8085.25 | 113943.8325 | 6436.75 | 0.79611
Southwest Reserve Sharing Group | SRSG | WECC | 20971.75 | 113943.8325 | 20479.25 | 0.97652
Source: 4 CP Non-Coincident and Coincident Peak Loads calculated using FERC Form 714 data obtained via ABB's GridView

## 2006
|  |  | 1 | 2 | 3 | 4
Non-Coincident Peak Loads CAISO-PAC
|  | Sub-Region | 2006 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 49948 | 59145.5825 | 49948 | 1
Northwest Power Pool | PacifiCorp | NWPP | 9299.8675 | 59145.5825 | 9197.5825 | 0.989
Non-Coincident Peak Loads WECC (no BPA and WAPA)
|  | Sub-Region | 2006 Non-Coincident Peak Load | Regional Coincident Peak | Share of Coincident Peak | Coincidence Factor
|  |  | MW | MW | MW
|  |  | [1] | [2] | [3] | [4]
California | California Independent System Operator | CA | 49948 | 55951.75 | 49948 | 1
California | Los Angeles Dept of Water & Power | CA | 6045.25 | 55951.75 | 6003.75 | 0.99314
Northwest Power Pool | Avista Corp | NWPP | 2091 | 36099.19 | 2008.25 | 0.96043
Northwest Power Pool | Balancing Authority of Northern California | NWPP | 3255 | 36099.19 | 3170.5 | 0.97404
Northwest Power Pool | Idaho Power Co | NWPP | 3353 | 36099.19 | 3349.75 | 0.99903
Northwest Power Pool | Nevada Power Co | NWPP | 5954.5 | 36099.19 | 5771.25 | 0.96922
Northwest Power Pool | Northwestern Energy | NWPP | 1642 | 36099.19 | 1590.75 | 0.96879
Northwest Power Pool | PacifiCorp | NWPP | 9299.8675 | 36099.19 | 9289.94 | 0.99893
Northwest Power Pool | Portland General Electric | NWPP | 3702.25 | 36099.19 | 3681.75 | 0.99446
Northwest Power Pool | PUD No 1 of Chelan County | NWPP | 563 | 36099.19 | 391.5 | 0.69538
Northwest Power Pool | PUD No 1 of Douglas County | NWPP | 326 | 36099.19 | 211.75 | 0.64954
Northwest Power Pool | PUD No 2 of Grant County | NWPP | 573.25 | 36099.19 | 556.5 | 0.97078
Northwest Power Pool | Puget Sound Energy Inc | NWPP | 4820.5 | 36099.19 | 3446 | 0.71486
Northwest Power Pool | Seattle City Light | NWPP | 1797 | 36099.19 | 1391.75 | 0.77449
Northwest Power Pool | Tacoma Power | NWPP | 953.5 | 36099.19 | 632 | 0.66282
Northwest Power Pool | Turlock Irrigation District | NWPP | 610.75 | 36099.19 | 607.5 | 0.99468
Rocky Mountain Reserve Sharing Group | Public Service Co of Colorado | RMRSG | 7687.25 | 7687.25 | 7687.25 | 1
Southwest Reserve Sharing Group | Arizona Public Service Co | SRSG | 7582.5 | 20827.5 | 7543.25 | 0.99482
Southwest Reserve Sharing Group | El Paso Electric | SRSG | 1442.5 | 20827.5 | 1345.5 | 0.93276
Southwest Reserve Sharing Group | Imperial Irrigation District | SRSG | 992 | 20827.5 | 957 | 0.96472
Southwest Reserve Sharing Group | Public Service Co of New Mexico | SRSG | 1841.25 | 20827.5 | 1775.5 | 0.96429
Southwest Reserve Sharing Group | Salt River Project | SRSG | 6678 | 20827.5 | 6647.25 | 0.9954
Southwest Reserve Sharing Group | Tucson Electric Power Co | SRSG | 2582.25 | 20827.5 | 2559 | 0.991
California | CA | WECC | 55951.75 | 119654.285 | 55823 | 0.9977
Northwest Power Pool | NWPP | WECC | 36099.19 | 119654.285 | 36043.535 | 0.99846
Rocky Mountain Reserve Sharing Group | RMRSG | WECC | 7687.25 | 119654.285 | 7311.5 | 0.95112
Southwest Reserve Sharing Group | SRSG | WECC | 20827.5 | 119654.285 | 20476.25 | 0.98314
Source: 4 CP Non-Coincident and Coincident Peak Loads calculated using FERC Form 714 data obtained via ABB's GridView