## Description
*CAISO Public*
2024 Summer Loads and Resources Assessment Report
Description | In addition to the probabilistic assessment, the multi-hour stack analysis provides an additional perspective on the amount of capacity the CAISO expects to be available for summer 2024, considering an 18.5 percent reserve margin. The new multi-hour approach focuses on a reasonable expectation of resource availability during every hour of the peak day in each of the summer months. For many resource types, the Net Qualifying Capacity (NQC) provides a reasonable estimation of the contribution/availability of those resources every hour.
Data Sources
Existing and New resources | - Existing resources are based on CAISO Master Control Area Generating Capability List on OASIS as of February 16, 2024 and the 2024 NQC list published on February 13, 2024. - Expected new resources are resources not on the NQC list, but are expected to be online by June 30, 2024. The NQC of an expected resource (excluding wind, solar, and battery) is based upon technology factors in the 2024 NQC list. - Existing and new resources contracted under the Strategic Reliability Reserve (SRR) program are excluded from this stack analysis.
Demand | Load profile used in this analysis is based on the CEC’s 2023 IEPR 1-in-2 planning forecast for CAISO for a peak day in each summer month of 2024.
Energy storage | Battery storage resources are assumed to be capable of one 4-hour cycle per day, but also are capable of spreading out their discharge energy across more than four hours. Hence, the base scenario assumes these resources can discharge for five (5) continuous hours, at 45 percent of full available capacity for the 1st and 5th hour, and 90 percent of full available capacity from 2nd through 4th hours.
Nuclear | Nuclear capacity within the CAISO footprint is included in the model, and capacity outside the CAISO footprint (Palo Verde dynamic import) is included as imports.
Wind and Solar | Wind and solar profiles are derived based on eight (8) years of historical generation data (2016 – 2023) for the five (5) highest load days using exceedance methodology. Solar profiles are calculated using a 70 percent exceedance level. Wind profiles are calculated using an 80 percent exceedance level for summer, and 65% exceedance level for non-summer months.
Demand Response | Demand response capacity is sourced from the 2024 NQC list and the CIRA database
Resource Adequacy Imports | Import capacity, including the contribution of tie generators, is based on average historical intertie monthly RA showings from CIRA from 2016 through 2023.
Other Renewables | Includes existing and expected resources from Biogas, Biomass, Geothermal and Waste to Power fuel categories
Other | Includes non-demand response resources clasified as "Other" such as qualified facilities etc.

## Summary
*CAISO Public* |  | Assessment of CAISO System Requirement against Available and Expected NQC capacity for Summer 2024
Select scenario |  |  | Total System Requirements for the CAISO System, 18.5% PRM | [13 empty] | Total System Supply for the CAISO System | [12 empty] | Total System Surplus/(Deficiency) for the CAISO System, 18.5% PRM
Year | 2024 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Month | 9 |  | 1 | 26977.71 | 26629.32 | 27560.73 | 28284.765 | 30338.37 | 34180.14 | 36609.39 | 35333.145 | 36167.385 | 30876.36 | 26750.19 | 28230.255 | 1 | 40806.9373 | 41629.5554 | 41362.6699 | 42817.8545 | 43832.7476 | 44638.0955 | 46879.8146 | 46643.3653 | 45628.9329 | 41823.7817 | 41405.0934 | 41676.7085 | 1 | 13829.2273 | 15000.2354 | 13801.9399 | 14533.0895 | 13494.3776 | 10457.9555 | 10270.4246 | 11310.2203 | 9461.5479 | 10947.4217 | 14654.9034 | 13446.4535
|  |  | 2 | 25970.46 | 25565.19 | 25581.78 | 26304.63 | 28226.7 | 31803.03 | 34647.03 | 33189.48 | 32951.295 | 28473.18 | 25687.245 | 27109.245 | 2 | 40706.6483 | 41701.974 | 41195.1374 | 42573.4923 | 44035.0067 | 44380.2042 | 46623.9822 | 46648.464 | 45362.5511 | 41774.8214 | 41398.0089 | 41683.0229 | 2 | 14736.1883 | 16136.784 | 15613.3574 | 16268.8623 | 15808.3067 | 12577.1742 | 11976.9522 | 13458.984 | 12411.2561 | 13301.6414 | 15710.7639 | 14573.7779
Scenario Summary |  |  | 3 | 25228.65 | 24762.945 | 24587.565 | 25225.095 | 27004.965 | 30064.635 | 32688.225 | 31440.42 | 31228.305 | 27217.08 | 24887.37 | 26445.645 | 3 | 40753.3247 | 41703.1491 | 41229.7106 | 42395.4546 | 43849.8853 | 44083.66 | 46623.1834 | 46481.8458 | 45337.2723 | 41769.2677 | 41396.2498 | 41739.3906 | 3 | 15524.6747 | 16940.2041 | 16642.1456 | 17170.3596 | 16844.9203 | 14019.025 | 13934.9584 | 15041.4258 | 14108.9673 | 14552.1877 | 16508.8798 | 15293.7456
Total requirement | 54476.82 |  | 4 | 24990.465 | 24556.755 | 23903.82 | 24531.87 | 26192.055 | 29000.505 | 31574.325 | 30395.25 | 30170.1 | 26402.985 | 24762.945 | 26250.12 | 4 | 40639.9544 | 41403.2066 | 41173.4083 | 42289.7861 | 43685.0535 | 43783.5765 | 46499.906 | 46290.1397 | 45246.1703 | 41742.7563 | 41392.3694 | 41694.6489 | 4 | 15649.4894 | 16846.4516 | 17269.5883 | 17757.9161 | 17492.9985 | 14783.0715 | 14925.581 | 15894.8897 | 15076.0703 | 15339.7713 | 16629.4244 | 15444.5289
Total NQC | 59494.3003 |  | 5 | 25694.355 | 25309.23 | 24228.51 | 24650.37 | 26100.81 | 28815.645 | 31312.44 | 30253.05 | 29959.17 | 26337.81 | 25422.99 | 26769.15 | 5 | 40613.7111 | 41378.3543 | 41074.0533 | 42089.2088 | 43373.7633 | 43640.0151 | 46331.2129 | 46146.8545 | 45200.431 | 41730.8508 | 41392.8316 | 41666.0166 | 5 | 14919.3561 | 16069.1243 | 16845.5433 | 17438.8388 | 17272.9533 | 14824.3701 | 15018.7729 | 15893.8045 | 15241.261 | 15393.0408 | 15969.8416 | 14896.8666
Surplus/(Shortfall) | 5017.4803 |  | 6 | 27401.94 | 27144.795 | 25219.17 | 25534.38 | 26852.1 | 29706.765 | 32137.2 | 31267.41 | 30866.88 | 27164.94 | 26995.485 | 28604.715 | 6 | 40650.3199 | 41344.0346 | 41119.4826 | 41839.6863 | 43087.5094 | 43440.6564 | 46094.8743 | 45963.0352 | 45117.7114 | 41718.7704 | 41373.5167 | 41724.3109 | 6 | 13248.3799 | 14199.2396 | 15900.3126 | 16305.3063 | 16235.4094 | 13733.8914 | 13957.6743 | 14695.6252 | 14250.8314 | 14553.8304 | 14378.0317 | 13119.5959
|  |  | 7 | 30403.545 | 29959.17 | 27207.6 | 26852.1 | 27648.42 | 30725.865 | 33484.545 | 32982.105 | 32863.605 | 29265.945 | 29146.26 | 31331.4 | 7 | 40671.2395 | 41408.7999 | 41082.0326 | 41708.3738 | 42887.0427 | 43290.2627 | 45898.5632 | 45842.5476 | 45060.2016 | 41714.4162 | 41577.8146 | 41754.4823 | 7 | 10267.6945 | 11449.6299 | 13874.4326 | 14856.2738 | 15238.6227 | 12564.3977 | 12414.0182 | 12860.4426 | 12196.5966 | 12448.4712 | 12431.5546 | 10423.0823
|  |  | 8 | 31765.11 | 31169.055 | 29252.91 | 27205.23 | 28735.065 | 32357.61 | 35284.56 | 34660.065 | 34460.985 | 30857.4 | 29454.36 | 32935.89 | 8 | 41922.7455 | 43875.1268 | 41004.5331 | 42252.0258 | 44513.2689 | 45301.6484 | 46740.3726 | 45937.6461 | 45118.4843 | 41719.4341 | 45481.8593 | 43681.494 | 8 | 10157.6355 | 12706.0718 | 11751.6231 | 15046.7958 | 15778.2039 | 12944.0384 | 11455.8126 | 11277.5811 | 10657.4993 | 10862.0341 | 16027.4993 | 10745.604
|  |  | 9 | 30889.395 | 30100.185 | 29211.435 | 26866.32 | 29371.41 | 33191.85 | 36538.29 | 36014.52 | 35664.945 | 31269.78 | 28930.59 | 32400.27 | 9 | 45336.3039 | 49032.798 | 43519.3563 | 46759.6555 | 50226.3107 | 50550.8683 | 51241.8306 | 49863.6021 | 47893.9855 | 43476.3079 | 51016.1487 | 47879.2763 | 9 | 14446.9089 | 18932.613 | 14307.9213 | 19893.3355 | 20854.9007 | 17359.0183 | 14703.5406 | 13849.0821 | 12229.0405 | 12206.5279 | 22085.5587 | 15479.0063
|  |  | 10 | 28944.81 | 28180.485 | 27952.965 | 25990.605 | 29152.185 | 33547.35 | 37307.355 | 36529.995 | 36592.8 | 31090.845 | 27790.62 | 30641.73 | 10 | 47290.4462 | 51814.5495 | 49203.0688 | 52599.8424 | 54608.3356 | 54787.9836 | 55614.4934 | 55149.2285 | 54229.4917 | 49691.0268 | 52954.6354 | 50439.354 | 10 | 18345.6362 | 23634.0645 | 21250.1038 | 26609.2374 | 25456.1506 | 21240.6336 | 18307.1384 | 18619.2335 | 17636.6917 | 18600.1818 | 25164.0154 | 19797.624
|  |  | 11 | 27070.14 | 26372.175 | 26258.415 | 25060.38 | 29089.38 | 34244.13 | 38372.67 | 37282.47 | 37741.065 | 30980.64 | 26971.785 | 28827.495 | 11 | 48863.0045 | 52323.2555 | 52638.1046 | 54992.0594 | 56970.7237 | 57206.1218 | 58356.0312 | 58046.3255 | 57318.6955 | 53409.0963 | 53266.7358 | 51282.0555 | 11 | 21792.8645 | 25951.0805 | 26379.6896 | 29931.6794 | 27881.3437 | 22961.9918 | 19983.3612 | 20763.8555 | 19577.6305 | 22428.4563 | 26294.9508 | 22454.5605
|  |  | 12 | 25688.43 | 25213.245 | 24899.22 | 24858.93 | 29083.455 | 35433.87 | 40192.83 | 38514.87 | 39389.4 | 31119.285 | 26893.575 | 27067.77 | 12 | 49099.4914 | 52580.292 | 53523.3608 | 56602.7552 | 58241.4341 | 58209.9921 | 59625.0544 | 59672.4324 | 58611.126 | 54812.399 | 53428.697 | 51685.5158 | 12 | 23411.0614 | 27367.047 | 28624.1408 | 31743.8252 | 29157.9791 | 22776.1221 | 19432.2244 | 21157.5624 | 19221.726 | 23693.114 | 26535.122 | 24617.7458
|  |  | 13 | 25290.27 | 24837.6 | 24388.485 | 25284.345 | 29918.88 | 36974.37 | 42213.255 | 40485.525 | 41886.195 | 32394.345 | 27702.93 | 26586.66 | 13 | 48731.2528 | 52471.1557 | 53671.6918 | 56838.249 | 58735.9682 | 58710.2778 | 60235.8708 | 60389.5292 | 59519.1011 | 55303.1797 | 53403.7436 | 51526.7565 | 13 | 23440.9828 | 27633.5557 | 29283.2068 | 31553.904 | 28817.0882 | 21735.9078 | 18022.6158 | 19904.0042 | 17632.9061 | 22908.8347 | 25700.8136 | 24940.0965
|  |  | 14 | 25612.59 | 25042.605 | 24632.595 | 26260.785 | 31409.61 | 39609.81 | 45156.795 | 43882.92 | 45024.075 | 34482.315 | 29241.06 | 26997.855 | 14 | 48008.245 | 52256.5925 | 53398.4239 | 57063.0446 | 58719.4473 | 58891.5155 | 60390.788 | 60469.6502 | 59646.2362 | 55473.3054 | 53039.8219 | 50360.4478 | 14 | 22395.655 | 27213.9875 | 28765.8289 | 30802.2596 | 27309.8373 | 19281.7055 | 15233.993 | 16586.7302 | 14622.1612 | 20990.9904 | 23798.7619 | 23362.5928
|  |  | 15 | 26583.105 | 25921.875 | 25492.905 | 27782.325 | 33347.085 | 42555.72 | 49309.035 | 47468.73 | 49114.695 | 36979.11 | 31280.445 | 28302.54 | 15 | 46769.0228 | 51210.0843 | 53545.7591 | 56964.7967 | 58760.3028 | 58776.1665 | 60327.9085 | 60067.9505 | 59299.1231 | 55407.0423 | 51487.2326 | 48669.6035 | 15 | 20185.9178 | 25288.2093 | 28052.8541 | 29182.4717 | 25413.2178 | 16220.4465 | 11018.8735 | 12599.2205 | 10184.4281 | 18427.9323 | 20206.7876 | 20367.0635
|  |  | 16 | 28412.745 | 27573.765 | 26758.485 | 29806.305 | 35769.225 | 45551.4 | 52341.45 | 50901.675 | 52691.025 | 39599.145 | 33671.775 | 30302.82 | 16 | 44984.4647 | 48537.3087 | 52441.0783 | 57020.3519 | 58452.286 | 58693.8661 | 59989.6239 | 59799.7529 | 58932.746 | 55057.2323 | 51438.8988 | 49886.0737 | 16 | 16571.7197 | 20963.5437 | 25682.5933 | 27214.0469 | 22683.061 | 13142.4661 | 7648.1739 | 8898.0779 | 6241.721 | 15458.0873 | 17767.1238 | 19583.2537
|  |  | 17 | 30994.86 | 29891.625 | 28396.155 | 31876.5 | 37856.01 | 47657.145 | 54392.685 | 52448.1 | 53994.525 | 41903.97 | 35456.385 | 32612.385 | 17 | 44699.7247 | 47136.6447 | 50273.3177 | 56203.8056 | 57983.2738 | 57955.5285 | 59714.8005 | 58759.925 | 57305.6396 | 58295.3439 | 50962.1331 | 50992.101 | 17 | 13704.8647 | 17245.0197 | 21877.1627 | 24327.3056 | 20127.2638 | 10298.3835 | 5322.1155 | 6311.825 | 3311.1146 | 16391.3739 | 15505.7481 | 18379.716
|  |  | 18 | 34090.08 | 32645.565 | 30729.42 | 34228.725 | 39650.1 | 49344.585 | 54799.14 | 53394.915 | 54476.82 | 43660.14 | 36660.345 | 35045.19 | 18 | 47172.6113 | 47699.728 | 49536.3642 | 58791.2617 | 61103.7752 | 61007.4072 | 63489.4584 | 62065.5085 | 59494.3003 | 59912.4691 | 50475.3864 | 50669.8081 | 18 | 13082.5313 | 15054.163 | 18806.9442 | 24562.5367 | 21453.6752 | 11662.8222 | 8690.3184 | 8670.5935 | 5017.4803 | 16252.3291 | 13815.0414 | 15624.6181
|  |  | 19 | 34534.455 | 33911.145 | 32790.135 | 35930.385 | 40675.125 | 49653.87 | 54290.775 | 52797.675 | 54118.95 | 43826.04 | 35641.245 | 34934.985 | 19 | 47239.6043 | 47717.7648 | 48636.5487 | 58944.2334 | 62562.8223 | 63295.1569 | 65613.7659 | 63753.0458 | 60039.7734 | 53186.7092 | 50499.9262 | 50689.3773 | 19 | 12705.1493 | 13806.6198 | 15846.4137 | 23013.8484 | 21887.6973 | 13641.2869 | 11322.9909 | 10955.3708 | 5920.8234 | 9360.6692 | 14858.6812 | 15754.3923
|  |  | 20 | 34255.98 | 33566.31 | 34030.83 | 36602.28 | 40700.01 | 48602.775 | 53018.085 | 50643.345 | 52130.52 | 41591.13 | 34707.465 | 34684.95 | 20 | 47250.2568 | 47859.3454 | 47932.892 | 53046.236 | 57149.8255 | 59040.3139 | 61060.1263 | 58462.6556 | 55568.1434 | 50867.7066 | 45987.6814 | 46160.5425 | 20 | 12994.2768 | 14293.0354 | 13902.062 | 16443.956 | 16449.8155 | 10437.5389 | 8042.0413 | 7819.3106 | 3437.6234 | 9276.5766 | 11280.2164 | 11475.5925
|  |  | 21 | 33236.88 | 32384.865 | 33879.15 | 36310.77 | 39653.655 | 46327.575 | 50248.74 | 47961.69 | 48567.225 | 39388.215 | 33136.155 | 33913.515 | 21 | 43932.2163 | 44573.6331 | 48055.3063 | 50237.47 | 52709.6137 | 54879.5057 | 56656.2426 | 55773.9184 | 54636.9397 | 46349.9217 | 41457.9001 | 41617.0869 | 21 | 10695.3363 | 12188.7681 | 14176.1563 | 13926.7 | 13055.9587 | 8551.9307 | 6407.5026 | 7812.2284 | 6069.7147 | 6961.7067 | 8321.7451 | 7703.5719
|  |  | 22 | 31967.745 | 31102.695 | 32503.365 | 34584.225 | 38133.3 | 44164.95 | 47985.39 | 45514.665 | 46006.44 | 37578.72 | 31871.76 | 32766.435 | 22 | 40735.5998 | 41260.2806 | 44883.0072 | 46253.6445 | 48076.2026 | 49131.7563 | 51458.6889 | 51397.809 | 50055.2204 | 41829.9254 | 41452.7339 | 41635.7752 | 22 | 8767.8548 | 10157.5856 | 12379.6422 | 11669.4195 | 9942.9026 | 4966.8063 | 3473.2989 | 5883.144 | 4048.7804 | 4251.2054 | 9580.9739 | 8869.3402
|  |  | 23 | 30198.54 | 29427.105 | 30736.53 | 32215.41 | 35277.45 | 40547.145 | 43701.615 | 41781.915 | 42440.775 | 35119.845 | 30230.535 | 31209.345 | 23 | 40731.1284 | 41306.8581 | 41458.3346 | 42566.2243 | 43741.8345 | 44640.3357 | 47012.8898 | 46905.0183 | 45519.7891 | 41817.3427 | 41467.8955 | 41644.9352 | 23 | 10532.5884 | 11879.7531 | 10721.8046 | 10350.8143 | 8464.3845 | 4093.1907 | 3311.2748 | 5123.1033 | 3079.0141 | 6697.4977 | 11237.3605 | 10435.5902
|  |  | 24 | 28501.62 | 27902.01 | 28962.585 | 30003.015 | 32307.84 | 36693.525 | 39562.41 | 37933.035 | 39027.975 | 32927.595 | 28699.515 | 29839.485 | 24 | 40799.3247 | 41249.3839 | 41421.5436 | 42781.9129 | 43833.9506 | 44594.6398 | 47017.0174 | 46804.3817 | 45584.6676 | 41838.4351 | 41462.2789 | 41627.0768 | 24 | 12297.7047 | 13347.3739 | 12458.9586 | 12778.8979 | 11526.1106 | 7901.1148 | 7454.6074 | 8871.3467 | 6556.6926 | 8910.8401 | 12762.7639 | 11787.5918
[29 empty] | Min | 8767.8548 | 10157.5856 | 10721.8046 | 10350.8143 | 8464.3845 | 4093.1907 | 3311.2748 | 5123.1033 | 3079.0141 | 4251.2054 | 8321.7451 | 7703.5719

## Monthly Data
*CAISO Public* | YEAR | MONTH | HOUR (PDT) | Load | Natural Gas | Nuclear | Hydro | Battery Storage | Other Renewables | Other | Demand Response | Liquidated Damages | Total Resources | Maximum Imports | Minimum Imports | Average Imports | Total Resources plus Max Imports | Total Resources plus Min Imports | Total Resources plus Avg Imports | Capacity for 20% PRM | PRM Max Import | PRM Min Import | PRM Avg Import | Load+18.5%PRM | Solar Factor | Wind Factor | Solar | Wind | Battery | PRM required
January 2024
| 2024 | 1 | 1 | 22766 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 37746.7385 | 3909.01 | 1505.7 | 3060.1988 | 41655.7485 | 39252.4385 | 40806.9373 |  | 82.97% | 72.42% | 79.25% | 26977.71 | 0.00025 | 0.087819 | 4.4312 | 553.0574 |  | 18.5%
| 2024 | 1 | 2 | 21916 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 37646.4496 | 3909.01 | 1505.7 | 3060.1988 | 41555.4596 | 39152.1496 | 40706.6483 |  | 89.61% | 78.65% | 85.74% | 25970.46 | 0.000257 | 0.071875 | 4.5553 | 452.6443 |  | 18.5%
| 2024 | 1 | 3 | 21290 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 37693.126 | 3909.01 | 1505.7 | 3060.1988 | 41602.136 | 39198.826 | 40753.3247 |  | 95.41% | 84.12% | 91.42% | 25228.65 | 0.000264 | 0.079267 | 4.6793 | 499.1966 |  | 18.5%
| 2024 | 1 | 4 | 21089 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 37579.7556 | 3909.01 | 1505.7 | 3060.1988 | 41488.7656 | 39085.4556 | 40639.9544 |  | 96.73% | 85.34% | 92.71% | 24990.465 | 0.000307 | 0.061144 | 5.4415 | 385.0641 |  | 18.5%
| 2024 | 1 | 5 | 21683 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 37553.5123 | 3909.01 | 1505.7 | 3060.1988 | 41462.5223 | 39059.2123 | 40613.7111 |  | 91.22% | 80.14% | 87.31% | 25694.355 | 0.000324 | 0.056929 | 5.7428 | 358.5195 |  | 18.5%
| 2024 | 1 | 6 | 23124 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 37590.1212 | 3909.01 | 1505.7 | 3060.1988 | 41499.1312 | 39095.8212 | 40650.3199 |  | 79.46% | 69.07% | 75.79% | 27401.94 | 0.000337 | 0.062705 | 5.9732 | 394.8979 |  | 18.5%
| 2024 | 1 | 7 | 25657 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 37611.0408 | 3909.01 | 1505.7 | 3060.1988 | 41520.0508 | 39116.7408 | 40671.2395 |  | 61.83% | 52.46% | 58.52% | 30403.545 | 0.000772 | 0.064803 | 13.6835 | 408.1073 |  | 18.5%
| 2024 | 1 | 8 | 26806 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 38862.5468 | 3909.01 | 1505.7 | 3060.1988 | 42771.5568 | 40368.2468 | 41922.7455 |  | 59.56% | 50.59% | 56.39% | 31765.11 | 0.073076 | 0.060029 | 1295.2546 | 378.0422 |  | 18.5%
| 2024 | 1 | 9 | 26067 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 42276.1051 | 3909.01 | 1505.7 | 3060.1988 | 46185.1151 | 43781.8051 | 45336.3039 |  | 77.18% | 67.96% | 73.92% | 30889.395 | 0.26275 | 0.068222 | 4657.2161 | 429.639 |  | 18.5%
| 2024 | 1 | 10 | 24426 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 44230.2474 | 3909.01 | 1505.7 | 3060.1988 | 48139.2574 | 45735.9474 | 47290.4462 |  | 97.08% | 87.24% | 93.61% | 28944.81 | 0.38064 | 0.046728 | 6746.7172 | 294.2802 |  | 18.5%
| 2024 | 1 | 11 | 22844 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 45802.8058 | 3909.01 | 1505.7 | 3060.1988 | 49711.8158 | 47308.5058 | 48863.0045 |  | 117.6% | 107.1% | 113.9% | 27070.14 | 0.47261 | 0.037587 | 8376.8456 | 236.7101 |  | 18.5%
| 2024 | 1 | 12 | 21678 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 46039.2926 | 3909.01 | 1505.7 | 3060.1988 | 49948.3026 | 47544.9926 | 49099.4914 |  | 130.4% | 119.3% | 126.5% | 25688.43 | 0.4851 | 0.039977 | 8598.2811 | 251.7616 |  | 18.5%
| 2024 | 1 | 13 | 21342 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 45671.054 | 3909.01 | 1505.7 | 3060.1988 | 49580.064 | 47176.754 | 48731.2528 |  | 132.3% | 121.1% | 128.3% | 25290.27 | 0.46295 | 0.043852 | 8205.6422 | 276.1618 |  | 18.5%
| 2024 | 1 | 14 | 21614 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 44948.0462 | 3909.01 | 1505.7 | 3060.1988 | 48857.0562 | 46453.7462 | 48008.245 |  | 126% | 114.9% | 122.1% | 25612.59 | 0.41935 | 0.051741 | 7432.949 | 325.8472 |  | 18.5%
| 2024 | 1 | 15 | 22433 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 43708.824 | 3909.01 | 1505.7 | 3060.1988 | 47617.834 | 45214.524 | 46769.0228 |  | 112.3% | 101.6% | 108.5% | 26583.105 | 0.34763 | 0.056827 | 6161.6938 | 357.8803 |  | 18.5%
| 2024 | 1 | 16 | 23977 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 41924.266 | 3909.01 | 1505.7 | 3060.1988 | 45833.276 | 43429.966 | 44984.4647 |  | 91.16% | 81.13% | 87.62% | 28412.745 | 0.24422 | 0.064498 | 4328.8295 | 406.1865 |  | 18.5%
| 2024 | 1 | 17 | 26156 | 26080.41 | 2280 | 5699.14 | 3237.6735 | 1823.74 | 34.38 | 1005.01 | 266.57 | 41639.5259 | 3909.01 | 1505.7 | 3060.1988 | 45548.5359 | 43145.2259 | 44699.7247 |  | 74.14% | 64.95% | 70.9% | 30994.86 | 0.045622 | 0.064145 | 808.639 | 403.9634 | 0.45 | 18.5%
| 2024 | 1 | 18 | 28768 | 26080.41 | 2280 | 5699.14 | 6475.347 | 1823.74 | 34.38 | 1005.01 | 266.57 | 44112.4126 | 3909.01 | 1505.7 | 3060.1988 | 48021.4226 | 45618.1126 | 47172.6113 |  | 66.93% | 58.57% | 63.98% | 34090.08 | 0.0005 | 0.069701 | 8.8624 | 438.9532 | 0.9 | 18.5%
| 2024 | 1 | 19 | 29143 | 26080.41 | 2280 | 5699.14 | 6475.347 | 1823.74 | 34.38 | 1005.01 | 266.57 | 44179.4055 | 3909.01 | 1505.7 | 3060.1988 | 48088.4155 | 45685.1055 | 47239.6043 |  | 65.01% | 56.76% | 62.1% | 34534.455 | 0.000345 | 0.080775 | 6.115 | 508.6935 | 0.9 | 18.5%
| 2024 | 1 | 20 | 28908 | 26080.41 | 2280 | 5699.14 | 6475.347 | 1823.74 | 34.38 | 1005.01 | 266.57 | 44190.058 | 3909.01 | 1505.7 | 3060.1988 | 48099.068 | 45695.758 | 47250.2568 |  | 66.39% | 58.07% | 63.45% | 34255.98 | 0.000345 | 0.082466 | 6.115 | 519.346 | 0.9 | 18.5%
| 2024 | 1 | 21 | 28048 | 26080.41 | 2280 | 5699.14 | 3237.6735 | 1823.74 | 34.38 | 1005.01 | 266.57 | 40872.0175 | 3909.01 | 1505.7 | 3060.1988 | 44781.0275 | 42377.7175 | 43932.2163 |  | 59.66% | 51.09% | 56.63% | 33236.88 | 0.000331 | 0.069744 | 5.8669 | 439.2271 | 0.45 | 18.5%
| 2024 | 1 | 22 | 26977 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 37675.401 | 3909.01 | 1505.7 | 3060.1988 | 41584.411 | 39181.101 | 40735.5998 |  | 54.15% | 45.24% | 51% | 31967.745 | 0.000345 | 0.076224 | 6.115 | 480.036 |  | 18.5%
| 2024 | 1 | 23 | 25484 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 37670.9297 | 3909.01 | 1505.7 | 3060.1988 | 41579.9397 | 39176.6297 | 40731.1284 |  | 63.16% | 53.73% | 59.83% | 30198.54 | 0.000345 | 0.075514 | 6.115 | 475.5646 |  | 18.5%
| 2024 | 1 | 24 | 24052 | 26080.41 | 2280 | 5699.14 | 0 | 1823.74 | 34.38 | 1005.01 | 266.57 | 37739.126 | 3909.01 | 1505.7 | 3060.1988 | 41648.136 | 39244.826 | 40799.3247 |  | 73.16% | 63.17% | 69.63% | 28501.62 | 0.000292 | 0.086492 | 5.1756 | 544.7004 |  | 18.5%
February 2024
| 2024 | 2 | 1 | 22472 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 38572.5354 | 3909.01 | 1625.69 | 3057.02 | 42481.5454 | 40198.2254 | 41629.5554 |  | 89.04% | 78.88% | 85.25% | 26629.32 | 0.000258 | 0.2052 | 4.573 | 1292.2924 |  | 18.5%
| 2024 | 2 | 2 | 21574 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 38644.954 | 3909.01 | 1625.69 | 3057.02 | 42553.964 | 40270.644 | 41701.974 |  | 97.25% | 86.66% | 93.3% | 25565.19 | 0.000278 | 0.21664 | 4.9275 | 1364.3566 |  | 18.5%
| 2024 | 2 | 3 | 20897 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 38646.1291 | 3909.01 | 1625.69 | 3057.02 | 42555.1391 | 40271.8191 | 41703.1491 |  | 103.6% | 92.72% | 99.57% | 24762.945 | 0.000291 | 0.21679 | 5.1579 | 1365.3012 |  | 18.5%
| 2024 | 2 | 4 | 20723 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 38346.1866 | 3909.01 | 1625.69 | 3057.02 | 42255.1966 | 39971.8766 | 41403.2066 |  | 103.9% | 92.89% | 99.79% | 24556.755 | 0.000297 | 0.16915 | 5.2643 | 1065.2523 |  | 18.5%
| 2024 | 2 | 5 | 21358 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 38321.3343 | 3909.01 | 1625.69 | 3057.02 | 42230.3443 | 39947.0243 | 41378.3543 |  | 97.73% | 87.04% | 93.74% | 25309.23 | 0.00032 | 0.16514 | 5.6719 | 1039.9924 |  | 18.5%
| 2024 | 2 | 6 | 22907 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 38287.0146 | 3909.01 | 1625.69 | 3057.02 | 42196.0246 | 39912.7046 | 41344.0346 |  | 84.21% | 74.24% | 80.49% | 27144.795 | 0.000334 | 0.15965 | 5.9201 | 1005.4246 |  | 18.5%
| 2024 | 2 | 7 | 25282 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 38351.7799 | 3909.01 | 1625.69 | 3057.02 | 42260.7899 | 39977.4699 | 41408.7999 |  | 67.16% | 58.13% | 63.79% | 29959.17 | 0.003094 | 0.16217 | 54.8404 | 1021.2695 |  | 18.5%
| 2024 | 2 | 8 | 26303 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 40818.1068 | 3909.01 | 1625.69 | 3057.02 | 44727.1168 | 42443.7968 | 43875.1268 |  | 70.05% | 61.36% | 66.81% | 31169.055 | 0.14892 | 0.14338 | 2639.5004 | 902.9364 |  | 18.5%
| 2024 | 2 | 9 | 25401 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 45975.778 | 3909.01 | 1625.69 | 3057.02 | 49884.788 | 47601.468 | 49032.798 |  | 96.39% | 87.4% | 93.03% | 30100.185 | 0.44178 | 0.13809 | 7830.4799 | 869.6281 |  | 18.5%
| 2024 | 2 | 10 | 23781 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 48757.5295 | 3909.01 | 1625.69 | 3057.02 | 52666.5395 | 50383.2195 | 51814.5495 |  | 121.5% | 111.9% | 117.9% | 28180.485 | 0.60054 | 0.13297 | 10644.4628 | 837.3967 |  | 18.5%
| 2024 | 2 | 11 | 22255 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 49266.2355 | 3909.01 | 1625.69 | 3057.02 | 53175.2455 | 50891.9255 | 52323.2555 |  | 138.9% | 128.7% | 135.1% | 26372.175 | 0.63233 | 0.12428 | 11207.8798 | 782.6858 |  | 18.5%
| 2024 | 2 | 12 | 21277 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 49523.272 | 3909.01 | 1625.69 | 3057.02 | 53432.282 | 51148.962 | 52580.292 |  | 151.1% | 140.4% | 147.1% | 25213.245 | 0.6511 | 0.11226 | 11540.6267 | 706.9753 |  | 18.5%
| 2024 | 2 | 13 | 20960 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 49414.1357 | 3909.01 | 1625.69 | 3057.02 | 53323.1457 | 51039.8257 | 52471.1557 |  | 154.4% | 143.5% | 150.3% | 24837.6 | 0.63764 | 0.13281 | 11302.0514 | 836.4143 |  | 18.5%
| 2024 | 2 | 14 | 21133 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 49199.5725 | 3909.01 | 1625.69 | 3057.02 | 53108.5825 | 50825.2625 | 52256.5925 |  | 151.3% | 140.5% | 147.3% | 25042.605 | 0.62189 | 0.14308 | 11022.8333 | 901.0692 |  | 18.5%
| 2024 | 2 | 15 | 21875 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 48153.0643 | 3909.01 | 1625.69 | 3057.02 | 52062.0743 | 49778.7543 | 51210.0843 |  | 138% | 127.6% | 134.1% | 25921.875 | 0.56027 | 0.15033 | 9930.6513 | 946.743 |  | 18.5%
| 2024 | 2 | 16 | 23269 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 45480.2887 | 3909.01 | 1625.69 | 3057.02 | 49389.2987 | 47105.9787 | 48537.3087 |  | 112.3% | 102.4% | 108.6% | 27573.765 | 0.4118 | 0.14379 | 7299.0562 | 905.5626 |  | 18.5%
| 2024 | 2 | 17 | 25225 | 26085.47 | 2280 | 5766.52 | 3237.6735 | 1827.55 | 33.55 | 1061.9 | 220.68 | 44079.6247 | 3909.01 | 1625.69 | 3057.02 | 47988.6347 | 45705.3147 | 47136.6447 |  | 90.24% | 81.19% | 86.86% | 29891.625 | 0.15112 | 0.14095 | 2678.6544 | 887.6268 | 0.45 | 18.5%
| 2024 | 2 | 18 | 27549 | 26085.47 | 2280 | 5766.52 | 6475.347 | 1827.55 | 33.55 | 1061.9 | 220.68 | 44642.708 | 3909.01 | 1625.69 | 3057.02 | 48551.718 | 46268.398 | 47699.728 |  | 76.24% | 67.95% | 73.15% | 32645.565 | 0.0053 | 0.12667 | 93.9412 | 797.7498 | 0.9 | 18.5%
| 2024 | 2 | 19 | 28617 | 26085.47 | 2280 | 5766.52 | 6475.347 | 1827.55 | 33.55 | 1061.9 | 220.68 | 44660.7448 | 3909.01 | 1625.69 | 3057.02 | 48569.7548 | 46286.4348 | 47717.7648 |  | 69.72% | 61.74% | 66.75% | 33911.145 | 0.000324 | 0.14354 | 5.7428 | 903.985 | 0.9 | 18.5%
| 2024 | 2 | 20 | 28326 | 26085.47 | 2280 | 5766.52 | 6475.347 | 1827.55 | 33.55 | 1061.9 | 220.68 | 44802.3254 | 3909.01 | 1625.69 | 3057.02 | 48711.3354 | 46428.0154 | 47859.3454 |  | 71.97% | 63.91% | 68.96% | 33566.31 | 0.0003 | 0.16609 | 5.3174 | 1045.9909 | 0.9 | 18.5%
| 2024 | 2 | 21 | 27329 | 26085.47 | 2280 | 5766.52 | 3237.6735 | 1827.55 | 33.55 | 1061.9 | 220.68 | 41516.6131 | 3909.01 | 1625.69 | 3057.02 | 45425.6231 | 43142.3031 | 44573.6331 |  | 66.22% | 57.86% | 63.1% | 32384.865 | 0.000284 | 0.15851 | 5.0338 | 998.2358 | 0.45 | 18.5%
| 2024 | 2 | 22 | 26247 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 38203.2606 | 3909.01 | 1625.69 | 3057.02 | 42112.2706 | 39828.9506 | 41260.2806 |  | 60.45% | 51.75% | 57.2% | 31102.695 | 0.000284 | 0.14649 | 5.0338 | 922.5568 |  | 18.5%
| 2024 | 2 | 23 | 24833 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 38249.8381 | 3909.01 | 1625.69 | 3057.02 | 42158.8481 | 39875.5281 | 41306.8581 |  | 69.77% | 60.57% | 66.34% | 29427.105 | 0.000284 | 0.15389 | 5.0338 | 969.1343 |  | 18.5%
| 2024 | 2 | 24 | 23546 | 26085.47 | 2280 | 5766.52 | 0 | 1827.55 | 33.55 | 1061.9 | 220.68 | 38192.3639 | 3909.01 | 1625.69 | 3057.02 | 42101.3739 | 39818.0539 | 41249.3839 |  | 78.8% | 69.11% | 75.19% | 27902.01 | 0.000264 | 0.14482 | 4.6793 | 912.0145 |  | 18.5%
March 2024
| 2024 | 3 | 2 | 21588 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 38081.8937 | 3909.01 | 2134.32 | 3113.2437 | 41990.9037 | 40216.2137 | 41195.1374 |  | 94.51% | 86.29% | 90.82% | 25581.78 | 0.00015 | 0.12328 | 2.6776 | 776.3661 |  | 18.5%
| 2024 | 3 | 3 | 20749 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 38116.4668 | 3909.01 | 2134.32 | 3113.2437 | 42025.4768 | 40250.7868 | 41229.7106 |  | 102.5% | 93.99% | 98.71% | 24587.565 | 0.000157 | 0.12875 | 2.8026 | 810.8143 |  | 18.5%
| 2024 | 3 | 4 | 20172 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 38060.1646 | 3909.01 | 2134.32 | 3113.2437 | 41969.1746 | 40194.4846 | 41173.4083 |  | 108.1% | 99.26% | 104.1% | 23903.82 | 0.00014 | 0.11986 | 2.4991 | 754.8155 |  | 18.5%
| 2024 | 3 | 5 | 20446 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 37960.8096 | 3909.01 | 2134.32 | 3113.2437 | 41869.8196 | 40095.1296 | 41074.0533 |  | 104.8% | 96.1% | 100.9% | 24228.51 | 0.00014 | 0.10408 | 2.4991 | 655.4605 |  | 18.5%
| 2024 | 3 | 6 | 21282 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 38006.2389 | 3909.01 | 2134.32 | 3113.2437 | 41915.2489 | 40140.5589 | 41119.4826 |  | 96.95% | 88.61% | 93.21% | 25219.17 | 0.000154 | 0.11125 | 2.749 | 700.6399 |  | 18.5%
| 2024 | 3 | 7 | 22960 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 37968.7889 | 3909.01 | 2134.32 | 3113.2437 | 41877.7989 | 40103.1089 | 41082.0326 |  | 82.39% | 74.67% | 78.93% | 27207.6 | 0.000167 | 0.10527 | 2.9811 | 662.9578 |  | 18.5%
| 2024 | 3 | 8 | 24686 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 37891.2893 | 3909.01 | 2134.32 | 3113.2437 | 41800.2993 | 40025.6093 | 41004.5331 |  | 69.33% | 62.14% | 66.1% | 29252.91 | 0.002932 | 0.085127 | 52.3384 | 536.1009 |  | 18.5%
| 2024 | 3 | 9 | 24651 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 40406.1125 | 3909.01 | 2134.32 | 3113.2437 | 44315.1225 | 42540.4325 | 43519.3563 |  | 79.77% | 72.57% | 76.54% | 29211.435 | 0.1452 | 0.081202 | 2591.8768 | 511.3857 |  | 18.5%
| 2024 | 3 | 10 | 23589 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 46089.825 | 3909.01 | 2134.32 | 3113.2437 | 49998.835 | 48224.145 | 49203.0688 |  | 112% | 104.4% | 108.6% | 27952.965 | 0.47056 | 0.061456 | 8399.9429 | 387.0321 |  | 18.5%
| 2024 | 3 | 11 | 22159 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 49524.8608 | 3909.01 | 2134.32 | 3113.2437 | 53433.8708 | 51659.1808 | 52638.1046 |  | 141.1% | 133.1% | 137.5% | 26258.415 | 0.66149 | 0.065736 | 11808.0278 | 413.983 |  | 18.5%
| 2024 | 3 | 12 | 21012 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 50410.1171 | 3909.01 | 2134.32 | 3113.2437 | 54319.1271 | 52544.4371 | 53523.3608 |  | 158.5% | 150.1% | 154.7% | 24899.22 | 0.71113 | 0.065603 | 12694.1217 | 413.1454 |  | 18.5%
| 2024 | 3 | 13 | 20581 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 50558.448 | 3909.01 | 2134.32 | 3113.2437 | 54467.458 | 52692.768 | 53671.6918 |  | 164.6% | 156% | 160.8% | 24388.485 | 0.71738 | 0.071418 | 12805.8318 | 449.7663 |  | 18.5%
| 2024 | 3 | 14 | 20787 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 50285.1801 | 3909.01 | 2134.32 | 3113.2437 | 54194.1901 | 52419.5001 | 53398.4239 |  | 160.7% | 152.2% | 156.9% | 24632.595 | 0.70135 | 0.073466 | 12519.6662 | 462.6639 |  | 18.5%
| 2024 | 3 | 15 | 21513 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 50432.5154 | 3909.01 | 2134.32 | 3113.2437 | 54341.5254 | 52566.8354 | 53545.7591 |  | 152.6% | 144.3% | 148.9% | 25492.905 | 0.70411 | 0.089046 | 12568.8808 | 560.7846 |  | 18.5%
| 2024 | 3 | 16 | 22581 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 49327.8346 | 3909.01 | 2134.32 | 3113.2437 | 53236.8446 | 51462.1546 | 52441.0783 |  | 135.8% | 127.9% | 132.2% | 26758.485 | 0.64433 | 0.083073 | 11501.8159 | 523.1687 |  | 18.5%
| 2024 | 3 | 17 | 23963 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 47160.0739 | 3909.01 | 2134.32 | 3113.2437 | 51069.0839 | 49294.3939 | 50273.3177 |  | 113.1% | 105.7% | 109.8% | 28396.155 | 0.52047 | 0.089933 | 9290.8565 | 566.3675 |  | 18.5%
| 2024 | 3 | 18 | 25932 | 25994.67 | 2280 | 5918.34 | 3303.8235 | 1808.01 | 35.12 | 1022.16 | 244.55 | 46423.1204 | 3909.01 | 2134.32 | 3113.2437 | 50332.1304 | 48557.4404 | 49536.3642 |  | 94.09% | 87.25% | 91.02% | 30729.42 | 0.28684 | 0.11055 | 5120.2406 | 696.2063 | 0.45 | 18.5%
| 2024 | 3 | 19 | 27671 | 25994.67 | 2280 | 5918.34 | 6607.647 | 1808.01 | 35.12 | 1022.16 | 244.55 | 45523.3049 | 3909.01 | 2134.32 | 3113.2437 | 49432.3149 | 47657.6249 | 48636.5487 |  | 78.64% | 72.23% | 75.77% | 32790.135 | 0.046628 | 0.12393 | 832.3452 | 780.4627 | 0.9 | 18.5%
| 2024 | 3 | 20 | 28718 | 25994.67 | 2280 | 5918.34 | 6607.647 | 1808.01 | 35.12 | 1022.16 | 244.55 | 44819.6482 | 3909.01 | 2134.32 | 3113.2437 | 48728.6582 | 46953.9682 | 47932.892 |  | 69.68% | 63.5% | 66.91% | 34030.83 | 0.000859 | 0.14193 | 15.3338 | 893.8174 | 0.9 | 18.5%
| 2024 | 3 | 21 | 28590 | 25994.67 | 2280 | 5918.34 | 6607.647 | 1808.01 | 35.12 | 1022.16 | 244.55 | 44942.0625 | 3909.01 | 2134.32 | 3113.2437 | 48851.0725 | 47076.3825 | 48055.3063 |  | 70.87% | 64.66% | 68.08% | 33879.15 | 0.000342 | 0.16283 | 6.105 | 1025.4606 | 0.9 | 18.5%
| 2024 | 3 | 22 | 27429 | 25994.67 | 2280 | 5918.34 | 3303.8235 | 1808.01 | 35.12 | 1022.16 | 244.55 | 41769.7634 | 3909.01 | 2134.32 | 3113.2437 | 45678.7734 | 43904.0834 | 44883.0072 |  | 66.53% | 60.06% | 63.63% | 32503.365 | 0.000184 | 0.18416 | 3.2845 | 1159.8054 | 0.45 | 18.5%
| 2024 | 3 | 23 | 25938 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 38345.0908 | 3909.01 | 2134.32 | 3113.2437 | 42254.1008 | 40479.4108 | 41458.3346 |  | 62.9% | 56.06% | 59.84% | 30736.53 | 0.00016 | 0.16504 | 2.8561 | 1039.3847 |  | 18.5%
| 2024 | 3 | 24 | 24441 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 38308.2999 | 3909.01 | 2134.32 | 3113.2437 | 42217.3099 | 40442.6199 | 41421.5436 |  | 72.73% | 65.47% | 69.48% | 28962.585 | 0.000157 | 0.15921 | 2.8026 | 1002.6473 |  | 18.5%
| 2024 | 3 | 1 | 23258 | 25994.67 | 2280 | 5918.34 | 0 | 1808.01 | 35.12 | 1022.16 | 244.55 | 38249.4262 | 3909.01 | 2134.32 | 3113.2437 | 42158.4362 | 40383.7462 | 41362.6699 |  | 81.26% | 73.63% | 77.84% | 27560.73 | 0.000157 | 0.14986 | 2.8026 | 943.7736 |  | 18.5%
April 2024
| 2024 | 4 | 2 | 22198 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 39320.4448 | 3909.01 | 2309.74 | 3253.0475 | 43229.4548 | 41630.1848 | 42573.4923 |  | 94.74% | 87.54% | 91.79% | 26304.63 | 0.000305 | 0.25821 | 5.4445 | 1626.1503 |  | 18.5%
| 2024 | 4 | 3 | 21287 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 39142.4071 | 3909.01 | 2309.74 | 3253.0475 | 43051.4171 | 41452.1471 | 42395.4546 |  | 102.2% | 94.73% | 99.16% | 25225.095 | 0.000347 | 0.22983 | 6.1942 | 1447.3629 |  | 18.5%
| 2024 | 4 | 4 | 20702 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 39036.7386 | 3909.01 | 2309.74 | 3253.0475 | 42945.7486 | 41346.4786 | 42289.7861 |  | 107.4% | 99.72% | 104.3% | 24531.87 | 0.000347 | 0.21305 | 6.1942 | 1341.6944 |  | 18.5%
| 2024 | 4 | 5 | 20802 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 38836.1613 | 3909.01 | 2309.74 | 3253.0475 | 42745.1713 | 41145.9013 | 42089.2088 |  | 105.5% | 97.8% | 102.3% | 24650.37 | 0.000347 | 0.1812 | 6.1942 | 1141.1171 |  | 18.5%
| 2024 | 4 | 6 | 21548 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 38586.6388 | 3909.01 | 2309.74 | 3253.0475 | 42495.6488 | 40896.3788 | 41839.6863 |  | 97.21% | 89.79% | 94.17% | 25534.38 | 0.00038 | 0.14148 | 6.7833 | 891.0055 |  | 18.5%
| 2024 | 4 | 7 | 22660 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 38455.3263 | 3909.01 | 2309.74 | 3253.0475 | 42364.3363 | 40765.0663 | 41708.3738 |  | 86.96% | 79.9% | 84.06% | 26852.1 | 0.00038 | 0.12063 | 6.7833 | 759.693 |  | 18.5%
| 2024 | 4 | 8 | 22958 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 38998.9783 | 3909.01 | 2309.74 | 3253.0475 | 42907.9883 | 41308.7183 | 42252.0258 |  | 86.9% | 79.93% | 84.04% | 27205.23 | 0.034638 | 0.10985 | 618.3146 | 691.8137 |  | 18.5%
| 2024 | 4 | 9 | 22672 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 43506.608 | 3909.01 | 2309.74 | 3253.0475 | 47415.618 | 45816.348 | 46759.6555 |  | 109.1% | 102.1% | 106.2% | 26866.32 | 0.29282 | 0.093796 | 5227.0595 | 590.6985 |  | 18.5%
| 2024 | 4 | 10 | 21933 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 49346.7949 | 3909.01 | 2309.74 | 3253.0475 | 53255.8049 | 51656.5349 | 52599.8424 |  | 142.8% | 135.5% | 139.8% | 25990.605 | 0.62623 | 0.07609 | 11178.7528 | 479.1921 |  | 18.5%
| 2024 | 4 | 11 | 21148 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 51739.0119 | 3909.01 | 2309.74 | 3253.0475 | 55648.0219 | 54048.7519 | 54992.0594 |  | 163.1% | 155.6% | 160% | 25060.38 | 0.75867 | 0.080572 | 13542.7468 | 507.4151 |  | 18.5%
| 2024 | 4 | 12 | 20978 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 53349.7077 | 3909.01 | 2309.74 | 3253.0475 | 57258.7177 | 55659.4477 | 56602.7552 |  | 172.9% | 165.3% | 169.8% | 24858.93 | 0.849 | 0.080292 | 15155.206 | 505.6517 |  | 18.5%
| 2024 | 4 | 13 | 21337 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 53585.2015 | 3909.01 | 2309.74 | 3253.0475 | 57494.2115 | 55894.9415 | 56838.249 |  | 169.5% | 162% | 166.4% | 25284.345 | 0.86208 | 0.080593 | 15388.801 | 507.5505 |  | 18.5%
| 2024 | 4 | 14 | 22161 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 53809.9971 | 3909.01 | 2309.74 | 3253.0475 | 57719.0071 | 56119.7371 | 57063.0446 |  | 160.5% | 153.2% | 157.5% | 26260.785 | 0.87467 | 0.080613 | 15613.4707 | 507.6764 |  | 18.5%
| 2024 | 4 | 15 | 23445 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 53711.7492 | 3909.01 | 2309.74 | 3253.0475 | 57620.7592 | 56021.4892 | 56964.7967 |  | 145.8% | 138.9% | 143% | 27782.325 | 0.8664 | 0.088448 | 15465.8806 | 557.0186 |  | 18.5%
| 2024 | 4 | 16 | 25153 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 53767.3044 | 3909.01 | 2309.74 | 3253.0475 | 57676.3144 | 56077.0444 | 57020.3519 |  | 129.3% | 122.9% | 126.7% | 29806.305 | 0.86347 | 0.10556 | 15413.6671 | 664.7873 |  | 18.5%
| 2024 | 4 | 17 | 26900 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 52950.7581 | 3909.01 | 2309.74 | 3253.0475 | 56859.7681 | 55260.4981 | 56203.8056 |  | 111.4% | 105.4% | 108.9% | 31876.5 | 0.81502 | 0.11324 | 14548.78 | 713.1281 |  | 18.5%
| 2024 | 4 | 18 | 28885 | 26027.45 | 2280 | 6045.78 | 3903.786 | 1784.44 | 46.73 | 1198.75 | 305.7 | 55538.2142 | 3909.01 | 2309.74 | 3253.0475 | 59447.2242 | 57847.9542 | 58791.2617 |  | 105.8% | 100.3% | 103.5% | 34228.725 | 0.73146 | 0.14107 | 13057.1705 | 888.4077 | 0.45 | 18.5%
| 2024 | 4 | 19 | 30321 | 26027.45 | 2280 | 6045.78 | 7807.572 | 1784.44 | 46.73 | 1198.75 | 305.7 | 55691.1859 | 3909.01 | 2309.74 | 3253.0475 | 59600.1959 | 58000.9259 | 58944.2334 |  | 96.56% | 91.29% | 94.4% | 35930.385 | 0.51111 | 0.17008 | 9123.6484 | 1071.1155 | 0.9 | 18.5%
| 2024 | 4 | 20 | 30888 | 26027.45 | 2280 | 6045.78 | 7807.572 | 1784.44 | 46.73 | 1198.75 | 305.7 | 49793.1885 | 3909.01 | 2309.74 | 3253.0475 | 53702.1985 | 52102.9285 | 53046.236 |  | 73.86% | 68.68% | 71.74% | 36602.28 | 0.173 | 0.1919 | 3088.2172 | 1208.5493 | 0.9 | 18.5%
| 2024 | 4 | 21 | 30642 | 26027.45 | 2280 | 6045.78 | 7807.572 | 1784.44 | 46.73 | 1198.75 | 305.7 | 46984.4225 | 3909.01 | 2309.74 | 3253.0475 | 50893.4325 | 49294.1625 | 50237.47 |  | 66.09% | 60.87% | 63.95% | 36310.77 | 0.009361 | 0.20974 | 167.101 | 1320.8995 | 0.9 | 18.5%
| 2024 | 4 | 22 | 29185 | 26027.45 | 2280 | 6045.78 | 3903.786 | 1784.44 | 46.73 | 1198.75 | 305.7 | 43000.597 | 3909.01 | 2309.74 | 3253.0475 | 46909.607 | 45310.337 | 46253.6445 |  | 60.73% | 55.25% | 58.48% | 34584.225 | 0.00149 | 0.21935 | 26.5976 | 1381.3634 | 0.45 | 18.5%
| 2024 | 4 | 23 | 27186 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 39313.1768 | 3909.01 | 2309.74 | 3253.0475 | 43222.1868 | 41622.9168 | 42566.2243 |  | 58.99% | 53.1% | 56.57% | 32215.41 | 0.000387 | 0.25683 | 6.9082 | 1617.4186 |  | 18.5%
| 2024 | 4 | 24 | 25319 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 39528.8654 | 3909.01 | 2309.74 | 3253.0475 | 43437.8754 | 41838.6054 | 42781.9129 |  | 71.56% | 65.25% | 68.97% | 30003.015 | 0.000387 | 0.29108 | 6.9082 | 1833.1071 |  | 18.5%
| 2024 | 4 | 1 | 23869 | 26027.45 | 2280 | 6045.78 | 0 | 1784.44 | 46.73 | 1198.75 | 305.7 | 39564.807 | 3909.01 | 2309.74 | 3253.0475 | 43473.817 | 41874.547 | 42817.8545 |  | 82.14% | 75.43% | 79.39% | 28284.765 | 0.000365 | 0.29685 | 6.5155 | 1869.4415 |  | 18.5%
May 2024
| 2024 | 5 | 2 | 23820 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 40736.2229 | 3909.01 | 2579.89 | 3298.7837 | 44645.2329 | 43316.1129 | 44035.0067 |  | 87.43% | 81.85% | 84.87% | 28226.7 | 0.000223 | 0.40752 | 4.2694 | 2566.4035 |  | 18.5%
| 2024 | 5 | 3 | 22789 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 40551.1015 | 3909.01 | 2579.89 | 3298.7837 | 44460.1115 | 43130.9915 | 43849.8853 |  | 95.09% | 89.26% | 92.42% | 27004.965 | 0.000154 | 0.37833 | 2.9484 | 2382.6032 |  | 18.5%
| 2024 | 5 | 4 | 22103 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 40386.2697 | 3909.01 | 2579.89 | 3298.7837 | 44295.2797 | 42966.1597 | 43685.0535 |  | 100.4% | 94.39% | 97.64% | 26192.055 | 0.000154 | 0.35216 | 2.9484 | 2217.7714 |  | 18.5%
| 2024 | 5 | 5 | 22026 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 40074.9795 | 3909.01 | 2579.89 | 3298.7837 | 43983.9895 | 42654.8695 | 43373.7633 |  | 99.69% | 93.66% | 96.92% | 26100.81 | 0.000154 | 0.30273 | 2.9484 | 1906.4812 |  | 18.5%
| 2024 | 5 | 6 | 22660 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 39788.7257 | 3909.01 | 2579.89 | 3298.7837 | 43697.7357 | 42368.6157 | 43087.5094 |  | 92.84% | 86.98% | 90.15% | 26852.1 | 0.000154 | 0.25727 | 2.9484 | 1620.2273 |  | 18.5%
| 2024 | 5 | 7 | 23332 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 39588.259 | 3909.01 | 2579.89 | 3298.7837 | 43497.269 | 42168.149 | 42887.0427 |  | 86.43% | 80.73% | 83.81% | 27648.42 | 0.00058 | 0.22415 | 11.1043 | 1411.6047 |  | 18.5%
| 2024 | 5 | 8 | 24249 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 41214.4852 | 3909.01 | 2579.89 | 3298.7837 | 45123.4952 | 43794.3752 | 44513.2689 |  | 86.08% | 80.6% | 83.57% | 28735.065 | 0.097837 | 0.18671 | 1873.1148 | 1175.8204 |  | 18.5%
| 2024 | 5 | 9 | 24786 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 46927.527 | 3909.01 | 2579.89 | 3298.7837 | 50836.537 | 49507.417 | 50226.3107 |  | 105.1% | 99.74% | 102.6% | 29371.41 | 0.41752 | 0.12201 | 7993.6247 | 768.3523 |  | 18.5%
| 2024 | 5 | 10 | 24601 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 51309.5518 | 3909.01 | 2579.89 | 3298.7837 | 55218.5618 | 53889.4418 | 54608.3356 |  | 124.5% | 119.1% | 122% | 29152.185 | 0.65628 | 0.091989 | 12564.6895 | 579.3123 |  | 18.5%
| 2024 | 5 | 11 | 24548 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 53671.94 | 3909.01 | 2579.89 | 3298.7837 | 57580.95 | 56251.83 | 56970.7237 |  | 134.6% | 129.2% | 132.1% | 29089.38 | 0.78126 | 0.087166 | 14957.445 | 548.945 |  | 18.5%
| 2024 | 5 | 12 | 24543 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 54942.6504 | 3909.01 | 2579.89 | 3298.7837 | 58851.6604 | 57522.5404 | 58241.4341 |  | 139.8% | 134.4% | 137.3% | 29083.455 | 0.85018 | 0.079411 | 16276.9937 | 500.1066 |  | 18.5%
| 2024 | 5 | 13 | 25248 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 55437.1845 | 3909.01 | 2579.89 | 3298.7837 | 59346.1945 | 58017.0745 | 58735.9682 |  | 135.1% | 129.8% | 132.6% | 29918.88 | 0.87664 | 0.077522 | 16783.4241 | 488.2103 |  | 18.5%
| 2024 | 5 | 14 | 26506 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 55420.6635 | 3909.01 | 2579.89 | 3298.7837 | 59329.6735 | 58000.5535 | 58719.4473 |  | 123.8% | 118.8% | 121.5% | 31409.61 | 0.87989 | 0.065022 | 16845.6271 | 409.4864 |  | 18.5%
| 2024 | 5 | 15 | 28141 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 55461.519 | 3909.01 | 2579.89 | 3298.7837 | 59370.529 | 58041.409 | 58760.3028 |  | 111% | 106.3% | 108.8% | 33347.085 | 0.87427 | 0.088591 | 16738.0499 | 557.9191 |  | 18.5%
| 2024 | 5 | 16 | 30185 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 55153.5023 | 3909.01 | 2579.89 | 3298.7837 | 59062.5123 | 57733.3923 | 58452.286 |  | 95.67% | 91.27% | 93.65% | 35769.225 | 0.8562 | 0.094603 | 16392.1716 | 595.7807 |  | 18.5%
| 2024 | 5 | 17 | 31946 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 54684.49 | 3909.01 | 2579.89 | 3298.7837 | 58593.5 | 57264.38 | 57983.2738 |  | 83.41% | 79.25% | 81.5% | 37856.01 | 0.81447 | 0.14698 | 15593.2973 | 925.6427 |  | 18.5%
| 2024 | 5 | 18 | 33460 | 25977.34 | 2280 | 6329.42 | 4413.276 | 1805.38 | 28.31 | 1388.16 | 356.94 | 57804.9914 | 3909.01 | 2579.89 | 3298.7837 | 61714.0014 | 60384.8814 | 61103.7752 |  | 84.44% | 80.47% | 82.62% | 39650.1 | 0.73122 | 0.1948 | 13999.397 | 1226.7684 | 0.45 | 18.5%
| 2024 | 5 | 19 | 34325 | 25977.34 | 2280 | 6329.42 | 8826.552 | 1805.38 | 28.31 | 1388.16 | 356.94 | 59264.0386 | 3909.01 | 2579.89 | 3298.7837 | 63173.0486 | 61843.9286 | 62562.8223 |  | 84.04% | 80.17% | 82.27% | 40675.125 | 0.56339 | 0.2359 | 10786.3438 | 1485.5928 | 0.9 | 18.5%
| 2024 | 5 | 20 | 34346 | 25977.34 | 2280 | 6329.42 | 8826.552 | 1805.38 | 28.31 | 1388.16 | 356.94 | 53851.0418 | 3909.01 | 2579.89 | 3298.7837 | 57760.0518 | 56430.9318 | 57149.8255 |  | 68.17% | 64.3% | 66.39% | 40700.01 | 0.26622 | 0.2798 | 5096.8703 | 1762.0695 | 0.9 | 18.5%
| 2024 | 5 | 21 | 33463 | 25977.34 | 2280 | 6329.42 | 8826.552 | 1805.38 | 28.31 | 1388.16 | 356.94 | 49410.83 | 3909.01 | 2579.89 | 3298.7837 | 53319.84 | 51990.72 | 52709.6137 |  | 59.34% | 55.37% | 57.52% | 39653.655 | 0.028476 | 0.2975 | 545.1804 | 1873.5476 | 0.9 | 18.5%
| 2024 | 5 | 22 | 32180 | 25977.34 | 2280 | 6329.42 | 4413.276 | 1805.38 | 28.31 | 1388.16 | 356.94 | 44777.4188 | 3909.01 | 2579.89 | 3298.7837 | 48686.4288 | 47357.3088 | 48076.2026 |  | 51.29% | 47.16% | 49.4% | 38133.3 | 0.000366 | 0.348 | 7.0072 | 2191.5857 | 0.45 | 18.5%
| 2024 | 5 | 23 | 29770 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 40443.0508 | 3909.01 | 2579.89 | 3298.7837 | 44352.0608 | 43022.9408 | 43741.8345 |  | 48.98% | 44.52% | 46.93% | 35277.45 | 0.000359 | 0.36055 | 6.8731 | 2270.6276 |  | 18.5%
| 2024 | 5 | 24 | 27264 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 40535.1669 | 3909.01 | 2579.89 | 3298.7837 | 44444.1769 | 43115.0569 | 43833.9506 |  | 63.01% | 58.14% | 60.78% | 32307.84 | 0.000335 | 0.37525 | 6.4137 | 2363.2032 |  | 18.5%
| 2024 | 5 | 1 | 25602 | 25977.34 | 2280 | 6329.42 | 0 | 1805.38 | 28.31 | 1388.16 | 356.94 | 40533.9639 | 3909.01 | 2579.89 | 3298.7837 | 44442.9739 | 43113.8539 | 43832.7476 |  | 73.59% | 68.4% | 71.21% | 30338.37 | 0.000297 | 0.37518 | 5.6861 | 2362.7277 |  | 18.5%
June 2024
| 2024 | 6 | 2 | 26838 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 40483.453 | 4691.5 | 3124.69 | 3896.7512 | 45174.953 | 43608.143 | 44380.2042 |  | 68.32% | 62.49% | 65.36% | 31803.03 | 0.000287 | 0.28799 | 5.5147 | 1813.6883 |  | 18.5%
| 2024 | 6 | 3 | 25371 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 40186.9088 | 4691.5 | 3124.69 | 3896.7512 | 44878.4088 | 43311.5988 | 44083.66 |  | 76.89% | 70.71% | 73.76% | 30064.635 | 0.000287 | 0.24091 | 5.5147 | 1517.1441 |  | 18.5%
| 2024 | 6 | 4 | 24473 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 39886.8253 | 4691.5 | 3124.69 | 3896.7512 | 44578.3253 | 43011.5153 | 43783.5765 |  | 82.15% | 75.75% | 78.91% | 29000.505 | 0.000287 | 0.19326 | 5.5147 | 1217.0606 |  | 18.5%
| 2024 | 6 | 5 | 24317 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 39743.2638 | 4691.5 | 3124.69 | 3896.7512 | 44434.7638 | 42867.9538 | 43640.0151 |  | 82.73% | 76.29% | 79.46% | 28815.645 | 0.000287 | 0.17046 | 5.5147 | 1073.4991 |  | 18.5%
| 2024 | 6 | 6 | 25069 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 39543.9051 | 4691.5 | 3124.69 | 3896.7512 | 44235.4051 | 42668.5951 | 43440.6564 |  | 76.45% | 70.2% | 73.28% | 29706.765 | 0.000287 | 0.1388 | 5.5147 | 874.1404 |  | 18.5%
| 2024 | 6 | 7 | 25929 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 39393.5114 | 4691.5 | 3124.69 | 3896.7512 | 44085.0114 | 42518.2014 | 43290.2627 |  | 70.02% | 63.98% | 66.96% | 30725.865 | 0.001717 | 0.11056 | 32.9922 | 696.2693 |  | 18.5%
| 2024 | 6 | 8 | 27306 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 41404.8972 | 4691.5 | 3124.69 | 3896.7512 | 46096.3972 | 44529.5872 | 45301.6484 |  | 68.81% | 63.08% | 65.9% | 32357.61 | 0.11167 | 0.094468 | 2145.7198 | 594.9273 |  | 18.5%
| 2024 | 6 | 9 | 28010 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 46654.1171 | 4691.5 | 3124.69 | 3896.7512 | 51345.6171 | 49778.8071 | 50550.8683 |  | 83.31% | 77.72% | 80.47% | 33191.85 | 0.39315 | 0.069148 | 7554.3965 | 435.4706 |  | 18.5%
| 2024 | 6 | 10 | 28310 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 50891.2323 | 4691.5 | 3124.69 | 3896.7512 | 55582.7323 | 54015.9223 | 54787.9836 |  | 96.34% | 90.8% | 93.53% | 33547.35 | 0.61938 | 0.051698 | 11901.4059 | 325.5764 |  | 18.5%
| 2024 | 6 | 11 | 28898 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 53309.3706 | 4691.5 | 3124.69 | 3896.7512 | 58000.8706 | 56434.0606 | 57206.1218 |  | 100.7% | 95.29% | 97.96% | 34244.13 | 0.74754 | 0.044648 | 14363.9427 | 281.1779 |  | 18.5%
| 2024 | 6 | 12 | 29902 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 54313.2408 | 4691.5 | 3124.69 | 3896.7512 | 59004.7408 | 57437.9308 | 58209.9921 |  | 97.33% | 92.09% | 94.67% | 35433.87 | 0.79875 | 0.047794 | 15348.0005 | 300.9904 |  | 18.5%
| 2024 | 6 | 13 | 31202 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 54813.5265 | 4691.5 | 3124.69 | 3896.7512 | 59505.0265 | 57938.2165 | 58710.2778 |  | 90.71% | 85.69% | 88.16% | 36974.37 | 0.82556 | 0.04543 | 15863.1738 | 286.1027 |  | 18.5%
| 2024 | 6 | 14 | 33426 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 54994.7642 | 4691.5 | 3124.69 | 3896.7512 | 59686.2642 | 58119.4542 | 58891.5155 |  | 78.56% | 73.87% | 76.18% | 39609.81 | 0.83234 | 0.053528 | 15993.4131 | 337.1011 |  | 18.5%
| 2024 | 6 | 15 | 35912 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 54879.4153 | 4691.5 | 3124.69 | 3896.7512 | 59570.9153 | 58004.1053 | 58776.1665 |  | 65.88% | 61.52% | 63.67% | 42555.72 | 0.82346 | 0.062312 | 15822.7455 | 392.4198 |  | 18.5%
| 2024 | 6 | 16 | 38440 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 54797.1148 | 4691.5 | 3124.69 | 3896.7512 | 59488.6148 | 57921.8048 | 58693.8661 |  | 54.76% | 50.68% | 52.69% | 45551.4 | 0.81074 | 0.088054 | 15578.3307 | 554.5342 |  | 18.5%
| 2024 | 6 | 17 | 40217 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 54058.7773 | 4691.5 | 3124.69 | 3896.7512 | 58750.2773 | 57183.4673 | 57955.5285 |  | 46.08% | 42.19% | 44.11% | 47657.145 | 0.75754 | 0.13312 | 14556.208 | 838.3193 |  | 18.5%
| 2024 | 6 | 18 | 41641 | 25917.43 | 2280 | 6681.72 | 4504.491 | 1832.82 | 33.9 | 1577.25 | 341.13 | 57110.656 | 4691.5 | 3124.69 | 3896.7512 | 61802.156 | 60235.346 | 61007.4072 |  | 48.42% | 44.65% | 46.51% | 49344.585 | 0.66586 | 0.18219 | 12794.5191 | 1147.3959 | 0.45 | 18.5%
| 2024 | 6 | 19 | 41902 | 25917.43 | 2280 | 6681.72 | 9008.982 | 1832.82 | 33.9 | 1577.25 | 341.13 | 59398.4057 | 4691.5 | 3124.69 | 3896.7512 | 64089.9057 | 62523.0957 | 63295.1569 |  | 52.95% | 49.21% | 51.06% | 49653.87 | 0.52747 | 0.25245 | 10135.3168 | 1589.8569 | 0.9 | 18.5%
| 2024 | 6 | 20 | 41015 | 25917.43 | 2280 | 6681.72 | 9008.982 | 1832.82 | 33.9 | 1577.25 | 341.13 | 55143.5627 | 4691.5 | 3124.69 | 3896.7512 | 59835.0627 | 58268.2527 | 59040.3139 |  | 45.89% | 42.07% | 43.95% | 48602.775 | 0.30329 | 0.26082 | 5827.775 | 1642.5557 | 0.9 | 18.5%
| 2024 | 6 | 21 | 39095 | 25917.43 | 2280 | 6681.72 | 9008.982 | 1832.82 | 33.9 | 1577.25 | 341.13 | 50982.7545 | 4691.5 | 3124.69 | 3896.7512 | 55674.2545 | 54107.4445 | 54879.5057 |  | 42.41% | 38.4% | 40.37% | 46327.575 | 0.071445 | 0.30753 | 1372.8157 | 1936.7068 | 0.9 | 18.5%
| 2024 | 6 | 22 | 37270 | 25917.43 | 2280 | 6681.72 | 4504.491 | 1832.82 | 33.9 | 1577.25 | 341.13 | 45235.0051 | 4691.5 | 3124.69 | 3896.7512 | 49926.5051 | 48359.6951 | 49131.7563 |  | 33.96% | 29.76% | 31.83% | 44164.95 | 0.00114 | 0.32462 | 21.9051 | 2044.359 | 0.45 | 18.5%
| 2024 | 6 | 23 | 34217 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 40743.5845 | 4691.5 | 3124.69 | 3896.7512 | 45435.0845 | 43868.2745 | 44640.3357 |  | 32.79% | 28.21% | 30.46% | 40547.145 | 0.000464 | 0.32876 | 8.9158 | 2070.4187 |  | 18.5%
| 2024 | 6 | 24 | 30965 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 40697.8886 | 4691.5 | 3124.69 | 3896.7512 | 45389.3886 | 43822.5786 | 44594.6398 |  | 46.58% | 41.52% | 44.02% | 36693.525 | 0.00019 | 0.32234 | 3.6509 | 2029.9877 |  | 18.5%
| 2024 | 6 | 1 | 28844 | 25917.43 | 2280 | 6681.72 | 0 | 1832.82 | 33.9 | 1577.25 | 341.13 | 40741.3443 | 4691.5 | 3124.69 | 3896.7512 | 45432.8443 | 43866.0343 | 44638.0955 |  | 57.51% | 52.08% | 54.76% | 34180.14 | 0.000274 | 0.32898 | 5.2649 | 2071.8294 |  | 18.5%
July 2024
| 2024 | 7 | 2 | 29238 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 41174.1647 | 6197.46 | 4793.19 | 5449.8175 | 47371.6247 | 45967.3547 | 46623.9822 |  | 62.02% | 57.22% | 59.46% | 34647.03 | 0.000177 | 0.33296 | 3.4011 | 2096.8437 |  | 18.5%
| 2024 | 7 | 3 | 27585 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 41173.3659 | 6197.46 | 4793.19 | 5449.8175 | 47370.8259 | 45966.5559 | 46623.1834 |  | 71.73% | 66.64% | 69.02% | 32688.225 | 0.00018 | 0.33282 | 3.4587 | 2095.9872 |  | 18.5%
| 2024 | 7 | 4 | 26645 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 41050.0885 | 6197.46 | 4793.19 | 5449.8175 | 47247.5485 | 45843.2785 | 46499.906 |  | 77.32% | 72.05% | 74.52% | 31574.325 | 0.000217 | 0.31313 | 4.1697 | 1971.9989 |  | 18.5%
| 2024 | 7 | 5 | 26424 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 40881.3954 | 6197.46 | 4793.19 | 5449.8175 | 47078.8554 | 45674.5854 | 46331.2129 |  | 78.17% | 72.85% | 75.34% | 31312.44 | 0.000224 | 0.28632 | 4.3042 | 1803.1712 |  | 18.5%
| 2024 | 7 | 6 | 27120 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 40645.0568 | 6197.46 | 4793.19 | 5449.8175 | 46842.5168 | 45438.2468 | 46094.8743 |  | 72.72% | 67.55% | 69.97% | 32137.2 | 0.000224 | 0.2488 | 4.3042 | 1566.8326 |  | 18.5%
| 2024 | 7 | 7 | 28257 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 40448.7457 | 6197.46 | 4793.19 | 5449.8175 | 46646.2057 | 45241.9357 | 45898.5632 |  | 65.08% | 60.11% | 62.43% | 33484.545 | 0.000477 | 0.21685 | 9.1656 | 1365.6602 |  | 18.5%
| 2024 | 7 | 8 | 29776 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 41290.5551 | 6197.46 | 4793.19 | 5449.8175 | 47488.0151 | 46083.7451 | 46740.3726 |  | 59.48% | 54.77% | 56.97% | 35284.56 | 0.054946 | 0.18433 | 1055.7874 | 1160.8477 |  | 18.5%
| 2024 | 7 | 9 | 30834 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 45792.0131 | 6197.46 | 4793.19 | 5449.8175 | 51989.4731 | 50585.2031 | 51241.8306 |  | 68.61% | 64.06% | 66.19% | 36538.29 | 0.30266 | 0.14329 | 5815.6888 | 902.4043 |  | 18.5%
| 2024 | 7 | 10 | 31483 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 50164.6759 | 6197.46 | 4793.19 | 5449.8175 | 56362.1359 | 54957.8659 | 55614.4934 |  | 79.02% | 74.56% | 76.65% | 37307.355 | 0.54785 | 0.089516 | 10527.0146 | 563.7413 |  | 18.5%
| 2024 | 7 | 11 | 32382 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 52906.2137 | 6197.46 | 4793.19 | 5449.8175 | 59103.6737 | 57699.4037 | 58356.0312 |  | 82.52% | 78.18% | 80.21% | 38372.67 | 0.70158 | 0.05581 | 13480.8213 | 351.4724 |  | 18.5%
| 2024 | 7 | 12 | 33918 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 54175.2369 | 6197.46 | 4793.19 | 5449.8175 | 60372.6969 | 58968.4269 | 59625.0544 |  | 78% | 73.86% | 75.79% | 40192.83 | 0.77019 | 0.047988 | 14799.1048 | 302.2121 |  | 18.5%
| 2024 | 7 | 13 | 35623 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 54786.0533 | 6197.46 | 4793.19 | 5449.8175 | 60983.5133 | 59579.2433 | 60235.8708 |  | 71.19% | 67.25% | 69.09% | 42213.255 | 0.80169 | 0.04885 | 15404.4926 | 307.6407 |  | 18.5%
| 2024 | 7 | 14 | 38107 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 54940.9705 | 6197.46 | 4793.19 | 5449.8175 | 61138.4305 | 59734.1605 | 60390.788 |  | 60.44% | 56.75% | 58.48% | 45156.795 | 0.80625 | 0.059536 | 15492.113 | 374.9375 |  | 18.5%
| 2024 | 7 | 15 | 41611 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 54878.091 | 6197.46 | 4793.19 | 5449.8175 | 61075.551 | 59671.281 | 60327.9085 |  | 46.78% | 43.4% | 44.98% | 49309.035 | 0.79947 | 0.070232 | 15361.8737 | 442.2973 |  | 18.5%
| 2024 | 7 | 16 | 44170 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 54539.8064 | 6197.46 | 4793.19 | 5449.8175 | 60737.2664 | 59332.9964 | 59989.6239 |  | 37.51% | 34.33% | 35.82% | 52341.45 | 0.77026 | 0.10566 | 14800.4883 | 665.3982 |  | 18.5%
| 2024 | 7 | 17 | 45901 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 54264.983 | 6197.46 | 4793.19 | 5449.8175 | 60462.443 | 59058.173 | 59714.8005 |  | 31.72% | 28.66% | 30.09% | 54392.685 | 0.73255 | 0.17706 | 14075.9867 | 1115.0763 |  | 18.5%
| 2024 | 7 | 18 | 46244 | 25867.94 | 2280 | 7031.69 | 4541.391 | 1837.02 | 37.18 | 1679.75 | 340.34 | 58039.6409 | 6197.46 | 4793.19 | 5449.8175 | 64237.1009 | 62832.8309 | 63489.4584 |  | 38.91% | 35.87% | 37.29% | 54799.14 | 0.66731 | 0.25437 | 12822.4193 | 1601.9106 | 0.45 | 18.5%
| 2024 | 7 | 19 | 45815 | 25867.94 | 2280 | 7031.69 | 9082.782 | 1837.02 | 37.18 | 1679.75 | 340.34 | 60163.9484 | 6197.46 | 4793.19 | 5449.8175 | 66361.4084 | 64957.1384 | 65613.7659 |  | 44.85% | 41.78% | 43.21% | 54290.775 | 0.52446 | 0.30643 | 10077.4797 | 1929.7668 | 0.9 | 18.5%
| 2024 | 7 | 20 | 44741 | 25867.94 | 2280 | 7031.69 | 9082.782 | 1837.02 | 37.18 | 1679.75 | 340.34 | 55610.3088 | 6197.46 | 4793.19 | 5449.8175 | 61807.7688 | 60403.4988 | 61060.1263 |  | 38.15% | 35.01% | 36.47% | 53018.085 | 0.28355 | 0.31841 | 5448.394 | 2005.2127 | 0.9 | 18.5%
| 2024 | 7 | 21 | 42404 | 25867.94 | 2280 | 7031.69 | 9082.782 | 1837.02 | 37.18 | 1679.75 | 340.34 | 51206.4251 | 6197.46 | 4793.19 | 5449.8175 | 57403.8851 | 55999.6151 | 56656.2426 |  | 35.37% | 32.06% | 33.61% | 50248.74 | 0.04492 | 0.34721 | 863.1378 | 2186.5853 | 0.9 | 18.5%
| 2024 | 7 | 22 | 40494 | 25867.94 | 2280 | 7031.69 | 4541.391 | 1837.02 | 37.18 | 1679.75 | 340.34 | 46008.8714 | 6197.46 | 4793.19 | 5449.8175 | 52206.3314 | 50802.0614 | 51458.6889 |  | 28.92% | 25.46% | 27.08% | 47985.39 | 0.000477 | 0.37862 | 9.1656 | 2384.3948 | 0.45 | 18.5%
| 2024 | 7 | 23 | 36879 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 41563.0723 | 6197.46 | 4793.19 | 5449.8175 | 47760.5323 | 46356.2623 | 47012.8898 |  | 29.51% | 25.7% | 27.48% | 43701.615 | 0.000261 | 0.39445 | 5.0151 | 2484.1372 |  | 18.5%
| 2024 | 7 | 24 | 33386 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 41567.1999 | 6197.46 | 4793.19 | 5449.8175 | 47764.6599 | 46360.3899 | 47017.0174 |  | 43.07% | 38.86% | 40.83% | 39562.41 | 0.00023 | 0.3952 | 4.4195 | 2488.8604 |  | 18.5%
| 2024 | 7 | 1 | 30894 | 25867.94 | 2280 | 7031.69 | 0 | 1837.02 | 37.18 | 1679.75 | 340.34 | 41429.9971 | 6197.46 | 4793.19 | 5449.8175 | 47627.4571 | 46223.1871 | 46879.8146 |  | 54.16% | 49.62% | 51.74% | 36609.39 | 0.000224 | 0.37344 | 4.3042 | 2351.773 |  | 18.5%
August 2024
| 2024 | 8 | 2 | 28008 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 40824.094 | 6480.04 | 4817.55 | 5824.37 | 47304.134 | 45641.644 | 46648.464 |  | 68.9% | 62.96% | 66.55% | 33189.48 | 0.00023 | 0.29636 | 4.4195 | 1866.3745 |  | 18.5%
| 2024 | 8 | 3 | 26532 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 40657.4758 | 6480.04 | 4817.55 | 5824.37 | 47137.5158 | 45475.0258 | 46481.8458 |  | 77.66% | 71.4% | 75.19% | 31440.42 | 0.000227 | 0.26991 | 4.3618 | 1699.814 |  | 18.5%
| 2024 | 8 | 4 | 25650 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 40465.7697 | 6480.04 | 4817.55 | 5824.37 | 46945.8097 | 45283.3197 | 46290.1397 |  | 83.02% | 76.54% | 80.47% | 30395.25 | 0.00023 | 0.23946 | 4.4195 | 1508.0503 |  | 18.5%
| 2024 | 8 | 5 | 25530 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 40322.4845 | 6480.04 | 4817.55 | 5824.37 | 46802.5245 | 45140.0345 | 46146.8545 |  | 83.32% | 76.81% | 80.76% | 30253.05 | 0.000247 | 0.21666 | 4.7461 | 1364.4384 |  | 18.5%
| 2024 | 8 | 6 | 26386 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 40138.6652 | 6480.04 | 4817.55 | 5824.37 | 46618.7052 | 44956.2152 | 45963.0352 |  | 76.68% | 70.38% | 74.19% | 31267.41 | 0.000237 | 0.1875 | 4.554 | 1180.8113 |  | 18.5%
| 2024 | 8 | 7 | 27833 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 40018.1776 | 6480.04 | 4817.55 | 5824.37 | 46498.2176 | 44835.7276 | 45842.5476 |  | 67.06% | 61.09% | 64.71% | 32982.105 | 0.000254 | 0.16832 | 4.8806 | 1059.9969 |  | 18.5%
| 2024 | 8 | 8 | 29249 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 40113.2761 | 6480.04 | 4817.55 | 5824.37 | 46593.3161 | 44930.8261 | 45937.6461 |  | 59.3% | 53.61% | 57.06% | 34660.065 | 0.019373 | 0.12508 | 372.2522 | 787.7239 |  | 18.5%
| 2024 | 8 | 9 | 30392 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 44039.2321 | 6480.04 | 4817.55 | 5824.37 | 50519.2721 | 48856.7821 | 49863.6021 |  | 66.23% | 60.76% | 64.07% | 36014.52 | 0.23659 | 0.085714 | 4546.1345 | 539.7976 |  | 18.5%
| 2024 | 8 | 10 | 30827 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 49324.8585 | 6480.04 | 4817.55 | 5824.37 | 55804.8985 | 54142.4085 | 55149.2285 |  | 81.03% | 75.63% | 78.9% | 36529.995 | 0.52271 | 0.052036 | 10043.8534 | 327.705 |  | 18.5%
| 2024 | 8 | 11 | 31462 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 52221.9555 | 6480.04 | 4817.55 | 5824.37 | 58701.9955 | 57039.5055 | 58046.3255 |  | 86.58% | 81.3% | 84.5% | 37282.47 | 0.67434 | 0.049408 | 12957.5007 | 311.1548 |  | 18.5%
| 2024 | 8 | 12 | 32502 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 53848.0624 | 6480.04 | 4817.55 | 5824.37 | 60328.1024 | 58665.6124 | 59672.4324 |  | 85.61% | 80.5% | 83.6% | 38514.87 | 0.76118 | 0.042674 | 14626.0161 | 268.7463 |  | 18.5%
| 2024 | 8 | 13 | 34165 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 54565.1592 | 6480.04 | 4817.55 | 5824.37 | 61045.1992 | 59382.7092 | 60389.5292 |  | 78.68% | 73.81% | 76.76% | 40485.525 | 0.79959 | 0.039338 | 15364.1219 | 247.7373 |  | 18.5%
| 2024 | 8 | 14 | 37032 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 54645.2802 | 6480.04 | 4817.55 | 5824.37 | 61125.3202 | 59462.8302 | 60469.6502 |  | 65.06% | 60.57% | 63.29% | 43882.92 | 0.8014 | 0.04655 | 15398.8241 | 293.1561 |  | 18.5%
| 2024 | 8 | 15 | 40058 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 54243.5805 | 6480.04 | 4817.55 | 5824.37 | 60723.6205 | 59061.1305 | 60067.9505 |  | 51.59% | 47.44% | 49.95% | 47468.73 | 0.78009 | 0.047778 | 14989.3909 | 300.8896 |  | 18.5%
| 2024 | 8 | 16 | 42955 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 53975.3829 | 6480.04 | 4817.55 | 5824.37 | 60455.4229 | 58792.9329 | 59799.7529 |  | 40.74% | 36.87% | 39.21% | 50901.675 | 0.76128 | 0.062586 | 14627.9376 | 394.1453 |  | 18.5%
| 2024 | 8 | 17 | 44260 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 52935.555 | 6480.04 | 4817.55 | 5824.37 | 59415.595 | 57753.105 | 58759.925 |  | 34.24% | 30.49% | 32.76% | 52448.1 | 0.70094 | 0.081578 | 13468.5045 | 513.7505 |  | 18.5%
| 2024 | 8 | 18 | 45059 | 25897.63 | 2280 | 6911.81 | 4541.391 | 1826.41 | 30.55 | 1728.82 | 278.08 | 56241.1385 | 6480.04 | 4817.55 | 5824.37 | 62721.1785 | 61058.6885 | 62065.5085 |  | 39.2% | 35.51% | 37.74% | 53394.915 | 0.61829 | 0.1375 | 11880.5192 | 865.9283 | 0.45 | 18.5%
| 2024 | 8 | 19 | 44555 | 25897.63 | 2280 | 6911.81 | 9082.782 | 1826.41 | 30.55 | 1728.82 | 278.08 | 57928.6758 | 6480.04 | 4817.55 | 5824.37 | 64408.7158 | 62746.2258 | 63753.0458 |  | 44.56% | 40.83% | 43.09% | 52797.675 | 0.4478 | 0.20454 | 8604.4578 | 1288.136 | 0.9 | 18.5%
| 2024 | 8 | 20 | 42737 | 25897.63 | 2280 | 6911.81 | 9082.782 | 1826.41 | 30.55 | 1728.82 | 278.08 | 52638.2856 | 6480.04 | 4817.55 | 5824.37 | 59118.3256 | 57455.8356 | 58462.6556 |  | 38.33% | 34.44% | 36.8% | 50643.345 | 0.16381 | 0.23099 | 3147.5323 | 1454.6713 | 0.9 | 18.5%
| 2024 | 8 | 21 | 40474 | 25897.63 | 2280 | 6911.81 | 9082.782 | 1826.41 | 30.55 | 1728.82 | 278.08 | 49949.5484 | 6480.04 | 4817.55 | 5824.37 | 56429.5884 | 54767.0984 | 55773.9184 |  | 39.42% | 35.31% | 37.8% | 47961.69 | 0.010398 | 0.27211 | 199.7976 | 1713.6689 | 0.9 | 18.5%
| 2024 | 8 | 22 | 38409 | 25897.63 | 2280 | 6911.81 | 4541.391 | 1826.41 | 30.55 | 1728.82 | 278.08 | 45573.439 | 6480.04 | 4817.55 | 5824.37 | 52053.479 | 50390.989 | 51397.809 |  | 35.52% | 31.2% | 33.82% | 45514.665 | 0.000305 | 0.32915 | 5.8606 | 2072.8874 | 0.45 | 18.5%
| 2024 | 8 | 23 | 35259 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 41080.6483 | 6480.04 | 4817.55 | 5824.37 | 47560.6883 | 45898.1983 | 46905.0183 |  | 34.89% | 30.17% | 33.03% | 41781.915 | 0.00027 | 0.33698 | 5.1881 | 2122.1603 |  | 18.5%
| 2024 | 8 | 24 | 32011 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 40980.0117 | 6480.04 | 4817.55 | 5824.37 | 47460.0517 | 45797.5617 | 46804.3817 |  | 48.26% | 43.07% | 46.21% | 37933.035 | 0.00027 | 0.321 | 5.1881 | 2021.5237 |  | 18.5%
| 2024 | 8 | 1 | 29817 | 25897.63 | 2280 | 6911.81 | 0 | 1826.41 | 30.55 | 1728.82 | 278.08 | 40818.9953 | 6480.04 | 4817.55 | 5824.37 | 47299.0353 | 45636.5453 | 46643.3653 |  | 58.63% | 53.06% | 56.43% | 35333.145 | 0.000257 | 0.29547 | 4.9383 | 1860.757 |  | 18.5%
September 2024
| 2024 | 9 | 2 | 27807 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 39106.9011 | 8498.28 | 5177.72 | 6255.65 | 47605.1811 | 44284.6211 | 45362.5511 |  | 71.2% | 59.26% | 63.13% | 32951.295 | 0.00026 | 0.086922 | 4.9959 | 547.4052 |  | 18.5%
| 2024 | 9 | 3 | 26353 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 39081.6223 | 8498.28 | 5177.72 | 6255.65 | 47579.9023 | 44259.3423 | 45337.2723 |  | 80.55% | 67.95% | 72.04% | 31228.305 | 0.00026 | 0.082908 | 4.9959 | 522.1264 |  | 18.5%
| 2024 | 9 | 4 | 25460 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 38990.5203 | 8498.28 | 5177.72 | 6255.65 | 47488.8003 | 44168.2403 | 45246.1703 |  | 86.52% | 73.48% | 77.71% | 30170.1 | 0.00026 | 0.068442 | 4.9959 | 431.0244 |  | 18.5%
| 2024 | 9 | 5 | 25282 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 38944.781 | 8498.28 | 5177.72 | 6255.65 | 47443.061 | 44122.501 | 45200.431 |  | 87.66% | 74.52% | 78.79% | 29959.17 | 0.000301 | 0.061054 | 5.7837 | 384.4973 |  | 18.5%
| 2024 | 9 | 6 | 26048 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 38862.0614 | 8498.28 | 5177.72 | 6255.65 | 47360.3414 | 44039.7814 | 45117.7114 |  | 81.82% | 69.07% | 73.21% | 30866.88 | 0.000399 | 0.04762 | 7.6668 | 299.8946 |  | 18.5%
| 2024 | 9 | 7 | 27733 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 38804.5516 | 8498.28 | 5177.72 | 6255.65 | 47302.8316 | 43982.2716 | 45060.2016 |  | 70.57% | 58.59% | 62.48% | 32863.605 | 0.00042 | 0.038424 | 8.0703 | 241.9813 |  | 18.5%
| 2024 | 9 | 8 | 29081 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 38862.8343 | 8498.28 | 5177.72 | 6255.65 | 47361.1143 | 44040.5543 | 45118.4843 |  | 62.86% | 51.44% | 55.15% | 34460.985 | 0.005107 | 0.033378 | 98.131 | 210.2033 |  | 18.5%
| 2024 | 9 | 9 | 30097 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 41638.3355 | 8498.28 | 5177.72 | 6255.65 | 50136.6155 | 46816.0555 | 47893.9855 |  | 66.58% | 55.55% | 59.13% | 35664.945 | 0.1514 | 0.027738 | 2909.151 | 174.6845 |  | 18.5%
| 2024 | 9 | 10 | 30880 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 47973.8417 | 8498.28 | 5177.72 | 6255.65 | 56472.1217 | 53151.5617 | 54229.4917 |  | 82.88% | 72.12% | 75.61% | 36592.8 | 0.4828 | 0.022602 | 9277.002 | 142.3397 |  | 18.5%
| 2024 | 9 | 11 | 31849 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 51063.0455 | 8498.28 | 5177.72 | 6255.65 | 59561.3255 | 56240.7655 | 57318.6955 |  | 87.01% | 76.59% | 79.97% | 37741.065 | 0.6427 | 0.02527 | 12349.4036 | 159.1419 |  | 18.5%
| 2024 | 9 | 12 | 33240 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 52355.476 | 8498.28 | 5177.72 | 6255.65 | 60853.756 | 57533.196 | 58611.126 |  | 83.07% | 73.08% | 76.33% | 39389.4 | 0.71075 | 0.022846 | 13657.0997 | 143.8763 |  | 18.5%
| 2024 | 9 | 13 | 35347 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 53263.4511 | 8498.28 | 5177.72 | 6255.65 | 61761.7311 | 58441.1711 | 59519.1011 |  | 74.73% | 65.34% | 68.39% | 41886.195 | 0.75526 | 0.031238 | 14512.2248 | 196.7263 |  | 18.5%
| 2024 | 9 | 14 | 37995 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 53390.5862 | 8498.28 | 5177.72 | 6255.65 | 61888.8662 | 58568.3062 | 59646.2362 |  | 62.89% | 54.15% | 56.98% | 45024.075 | 0.76088 | 0.03426 | 14620.3284 | 215.7578 |  | 18.5%
| 2024 | 9 | 15 | 41447 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 53043.4731 | 8498.28 | 5177.72 | 6255.65 | 61541.7531 | 58221.1931 | 59299.1231 |  | 48.48% | 40.47% | 43.07% | 49114.695 | 0.73904 | 0.045782 | 14200.6536 | 288.3195 |  | 18.5%
| 2024 | 9 | 16 | 44465 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 52677.096 | 8498.28 | 5177.72 | 6255.65 | 61175.376 | 57854.816 | 58932.746 |  | 37.58% | 30.11% | 32.54% | 52691.025 | 0.71751 | 0.053284 | 13787.0315 | 335.5645 |  | 18.5%
| 2024 | 9 | 17 | 45565 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 51049.9896 | 8498.28 | 5177.72 | 6255.65 | 59548.2696 | 56227.7096 | 57305.6396 |  | 30.69% | 23.4% | 25.77% | 53994.525 | 0.63305 | 0.052622 | 12164.0942 | 331.3955 |  | 18.5%
| 2024 | 9 | 18 | 45972 | 25919.11 | 2280 | 6458.08 | 4541.391 | 1829.49 | 43.55 | 1734.42 | 289.85 | 53238.6503 | 8498.28 | 5177.72 | 6255.65 | 61736.9303 | 58416.3703 | 59494.3003 |  | 34.29% | 27.07% | 29.41% | 54476.82 | 0.51209 | 0.048096 | 9839.867 | 302.8923 | 0.45 | 18.5%
| 2024 | 9 | 19 | 45670 | 25919.11 | 2280 | 6458.08 | 9082.782 | 1829.49 | 43.55 | 1734.42 | 289.85 | 53784.1234 | 8498.28 | 5177.72 | 6255.65 | 62282.4034 | 58961.8434 | 60039.7734 |  | 36.37% | 29.1% | 31.46% | 54118.95 | 0.29728 | 0.069026 | 5712.1391 | 434.7023 | 0.9 | 18.5%
| 2024 | 9 | 20 | 43992 | 25919.11 | 2280 | 6458.08 | 9082.782 | 1829.49 | 43.55 | 1734.42 | 289.85 | 49312.4934 | 8498.28 | 5177.72 | 6255.65 | 57810.7734 | 54490.2134 | 55568.1434 |  | 31.41% | 23.86% | 26.31% | 52130.52 | 0.058658 | 0.087032 | 1127.1135 | 548.0979 | 0.9 | 18.5%
| 2024 | 9 | 21 | 40985 | 25919.11 | 2280 | 6458.08 | 9082.782 | 1829.49 | 43.55 | 1734.42 | 289.85 | 48381.2897 | 8498.28 | 5177.72 | 6255.65 | 56879.5697 | 53559.0097 | 54636.9397 |  | 38.78% | 30.68% | 33.31% | 48567.225 | 0.000691 | 0.11603 | 13.2776 | 730.7301 | 0.9 | 18.5%
| 2024 | 9 | 22 | 38824 | 25919.11 | 2280 | 6458.08 | 4541.391 | 1829.49 | 43.55 | 1734.42 | 289.85 | 43799.5704 | 8498.28 | 5177.72 | 6255.65 | 52297.8504 | 48977.2904 | 50055.2204 |  | 34.7% | 26.15% | 28.93% | 46006.44 | 0.000267 | 0.11092 | 5.1304 | 698.549 | 0.45 | 18.5%
| 2024 | 9 | 23 | 35815 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 39264.1391 | 8498.28 | 5177.72 | 6255.65 | 47762.4191 | 44441.8591 | 45519.7891 |  | 33.36% | 24.09% | 27.1% | 42440.775 | 0.000254 | 0.11191 | 4.8806 | 704.7585 |  | 18.5%
| 2024 | 9 | 24 | 32935 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 39329.0176 | 8498.28 | 5177.72 | 6255.65 | 47827.2976 | 44506.7376 | 45584.6676 |  | 45.22% | 35.14% | 38.41% | 39027.975 | 0.000254 | 0.12221 | 4.8806 | 769.637 |  | 18.5%
| 2024 | 9 | 1 | 30521 | 25919.11 | 2280 | 6458.08 | 0 | 1829.49 | 43.55 | 1734.42 | 289.85 | 39373.2829 | 8498.28 | 5177.72 | 6255.65 | 47871.5629 | 44551.0029 | 45628.9329 |  | 56.85% | 45.97% | 49.5% | 36167.385 | 0.000251 | 0.12925 | 4.823 | 813.96 |  | 18.5%
October 2024
| 2024 | 10 | 2 | 24028 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 37957.9664 | 5035.78 | 1772 | 3816.855 | 42993.7464 | 39729.9664 | 41774.8214 |  | 78.93% | 65.35% | 73.86% | 28473.18 | 0.000467 | 0.038564 | 8.9734 | 242.863 |  | 18.5%
| 2024 | 10 | 3 | 22968 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 37952.4127 | 5035.78 | 1772 | 3816.855 | 42988.1927 | 39724.4127 | 41769.2677 |  | 87.17% | 72.96% | 81.86% | 27217.08 | 0.00045 | 0.037734 | 8.6468 | 237.6359 |  | 18.5%
| 2024 | 10 | 4 | 22281 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 37925.9013 | 5035.78 | 1772 | 3816.855 | 42961.6813 | 39697.9013 | 41742.7563 |  | 92.82% | 78.17% | 87.35% | 26402.985 | 0.000397 | 0.033686 | 7.6284 | 212.143 |  | 18.5%
| 2024 | 10 | 5 | 22226 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 37913.9958 | 5035.78 | 1772 | 3816.855 | 42949.7758 | 39685.9958 | 41730.8508 |  | 93.24% | 78.56% | 87.76% | 26337.81 | 0.000427 | 0.031704 | 8.2048 | 199.661 |  | 18.5%
| 2024 | 10 | 6 | 22924 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 37901.9154 | 5035.78 | 1772 | 3816.855 | 42937.6954 | 39673.9154 | 41718.7704 |  | 87.3% | 73.07% | 81.99% | 27164.94 | 0.00052 | 0.029502 | 9.9918 | 185.7936 |  | 18.5%
| 2024 | 10 | 7 | 24697 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 37897.5612 | 5035.78 | 1772 | 3816.855 | 42933.3412 | 39669.5612 | 41714.4162 |  | 73.84% | 60.63% | 68.9% | 29265.945 | 0.00061 | 0.028536 | 11.7212 | 179.71 |  | 18.5%
| 2024 | 10 | 8 | 26040 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 37902.5791 | 5035.78 | 1772 | 3816.855 | 42938.3591 | 39674.5791 | 41719.4341 |  | 64.89% | 52.36% | 60.21% | 30857.4 | 0.001349 | 0.027078 | 25.921 | 170.528 |  | 18.5%
| 2024 | 10 | 9 | 26388 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 39659.4529 | 5035.78 | 1772 | 3816.855 | 44695.2329 | 41431.4529 | 43476.3079 |  | 69.38% | 57.01% | 64.76% | 31269.78 | 0.092786 | 0.027064 | 1782.883 | 170.4399 |  | 18.5%
| 2024 | 10 | 10 | 26237 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 45874.1718 | 5035.78 | 1772 | 3816.855 | 50909.9518 | 47646.1718 | 49691.0268 |  | 94.04% | 81.6% | 89.39% | 31090.845 | 0.41633 | 0.026718 | 7999.781 | 168.2609 |  | 18.5%
| 2024 | 10 | 11 | 26144 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 49592.2413 | 5035.78 | 1772 | 3816.855 | 54628.0213 | 51364.2413 | 53409.0963 |  | 109% | 96.47% | 104.3% | 30980.64 | 0.61129 | 0.022252 | 11745.9758 | 140.1355 |  | 18.5%
| 2024 | 10 | 12 | 26261 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 50995.544 | 5035.78 | 1772 | 3816.855 | 56031.324 | 52767.544 | 54812.399 |  | 113.4% | 100.9% | 108.7% | 31119.285 | 0.68565 | 0.018202 | 13174.784 | 114.63 |  | 18.5%
| 2024 | 10 | 13 | 27337 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 51486.3247 | 5035.78 | 1772 | 3816.855 | 56522.1047 | 53258.3247 | 55303.1797 |  | 106.8% | 94.82% | 102.3% | 32394.345 | 0.71044 | 0.020492 | 13651.143 | 129.0516 |  | 18.5%
| 2024 | 10 | 14 | 29099 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 51656.4504 | 5035.78 | 1772 | 3816.855 | 56692.2304 | 53428.4504 | 55473.3054 |  | 94.83% | 83.61% | 90.64% | 34482.315 | 0.71823 | 0.02375 | 13800.751 | 149.5694 |  | 18.5%
| 2024 | 10 | 15 | 31206 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 51590.1873 | 5035.78 | 1772 | 3816.855 | 56625.9673 | 53362.1873 | 55407.0423 |  | 81.46% | 71% | 77.55% | 36979.11 | 0.71358 | 0.027422 | 13711.3628 | 172.6944 |  | 18.5%
| 2024 | 10 | 16 | 33417 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 51240.3773 | 5035.78 | 1772 | 3816.855 | 56276.1573 | 53012.3773 | 55057.2323 |  | 68.41% | 58.64% | 64.76% | 39599.145 | 0.6949 | 0.028862 | 13352.4843 | 181.7631 |  | 18.5%
| 2024 | 10 | 17 | 35362 | 26067.51 | 2280 | 5663.18 | 4541.391 | 1804.24 | 36.38 | 1511.82 | 343 | 54478.4889 | 5035.78 | 1772 | 3816.855 | 59514.2689 | 56250.4889 | 58295.3439 |  | 68.3% | 59.07% | 64.85% | 41903.97 | 0.62689 | 0.029426 | 12045.6529 | 185.3149 | 0.45 | 18.5%
| 2024 | 10 | 18 | 36844 | 26067.51 | 2280 | 5663.18 | 9082.782 | 1804.24 | 36.38 | 1511.82 | 343 | 56095.6141 | 5035.78 | 1772 | 3816.855 | 61131.3941 | 57867.6141 | 59912.4691 |  | 65.92% | 57.06% | 62.61% | 43660.14 | 0.47447 | 0.030132 | 9116.9411 | 189.7611 | 0.9 | 18.5%
| 2024 | 10 | 19 | 36984 | 26067.51 | 2280 | 5663.18 | 9082.782 | 1804.24 | 36.38 | 1511.82 | 343 | 49369.8542 | 5035.78 | 1772 | 3816.855 | 54405.6342 | 51141.8542 | 53186.7092 |  | 47.11% | 38.28% | 43.81% | 43826.04 | 0.12617 | 0.024858 | 2424.395 | 156.5472 | 0.9 | 18.5%
| 2024 | 10 | 20 | 35098 | 26067.51 | 2280 | 5663.18 | 9082.782 | 1804.24 | 36.38 | 1511.82 | 343 | 47050.8516 | 5035.78 | 1772 | 3816.855 | 52086.6316 | 48822.8516 | 50867.7066 |  | 48.4% | 39.1% | 44.93% | 41591.13 | 0.002526 | 0.033886 | 48.5371 | 213.4025 | 0.9 | 18.5%
| 2024 | 10 | 21 | 33239 | 26067.51 | 2280 | 5663.18 | 4541.391 | 1804.24 | 36.38 | 1511.82 | 343 | 42533.0667 | 5035.78 | 1772 | 3816.855 | 47568.8467 | 44305.0667 | 46349.9217 |  | 43.11% | 33.29% | 39.44% | 39388.215 | 0.000578 | 0.043578 | 11.1063 | 274.4394 | 0.45 | 18.5%
| 2024 | 10 | 22 | 31712 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 38013.0704 | 5035.78 | 1772 | 3816.855 | 43048.8504 | 39785.0704 | 41829.9254 |  | 35.75% | 25.46% | 31.91% | 37578.72 | 0.000446 | 0.047378 | 8.5699 | 298.3705 |  | 18.5%
| 2024 | 10 | 23 | 29637 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 38000.4877 | 5035.78 | 1772 | 3816.855 | 43036.2677 | 39772.4877 | 41817.3427 |  | 45.21% | 34.2% | 41.1% | 35119.845 | 0.000446 | 0.04538 | 8.5699 | 285.7878 |  | 18.5%
| 2024 | 10 | 24 | 27787 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 38021.5801 | 5035.78 | 1772 | 3816.855 | 43057.3601 | 39793.5801 | 41838.4351 |  | 54.96% | 43.21% | 50.57% | 32927.595 | 0.000392 | 0.048894 | 7.5323 | 307.9178 |  | 18.5%
| 2024 | 10 | 1 | 26056 | 26067.51 | 2280 | 5663.18 | 0 | 1804.24 | 36.38 | 1511.82 | 343 | 38006.9267 | 5035.78 | 1772 | 3816.855 | 43042.7067 | 39778.9267 | 41823.7817 |  | 65.19% | 52.67% | 60.51% | 30876.36 | 0.000357 | 0.046674 | 6.8598 | 293.937 |  | 18.5%
November 2024
| 2024 | 11 | 1 | 22574 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37525.2684 | 5035.78 | 2275.76 | 3879.825 | 42561.0484 | 39801.0284 | 41405.0934 |  | 88.54% | 76.31% | 83.42% | 26750.19 | 0.000174 | 0.034909 | 3.3434 | 219.845 |  | 18.5%
| 2024 | 11 | 2 | 21677 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37518.1839 | 5035.78 | 2275.76 | 3879.825 | 42553.9639 | 39793.9439 | 41398.0089 |  | 96.31% | 83.58% | 90.98% | 25687.245 | 0.000224 | 0.033631 | 4.3042 | 211.7998 |  | 18.5%
| 2024 | 11 | 3 | 21002 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37516.4248 | 5035.78 | 2275.76 | 3879.825 | 42552.2048 | 39792.1848 | 41396.2498 |  | 102.6% | 89.47% | 97.11% | 24887.37 | 0.000237 | 0.033312 | 4.554 | 209.7908 |  | 18.5%
| 2024 | 11 | 4 | 20897 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37512.5444 | 5035.78 | 2275.76 | 3879.825 | 42548.3244 | 39788.3044 | 41392.3694 |  | 103.6% | 90.4% | 98.08% | 24762.945 | 0.000224 | 0.032736 | 4.3042 | 206.1602 |  | 18.5%
| 2024 | 11 | 5 | 21454 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37513.0066 | 5035.78 | 2275.76 | 3879.825 | 42548.7866 | 39788.7666 | 41392.8316 |  | 98.33% | 85.46% | 92.94% | 25422.99 | 0.00031 | 0.032547 | 5.9567 | 204.9699 |  | 18.5%
| 2024 | 11 | 6 | 22781 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37493.6917 | 5035.78 | 2275.76 | 3879.825 | 42529.4717 | 39769.4517 | 41373.5167 |  | 86.69% | 74.57% | 81.61% | 26995.485 | 0.00031 | 0.02948 | 5.9567 | 185.655 |  | 18.5%
| 2024 | 11 | 7 | 24596 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37697.9896 | 5035.78 | 2275.76 | 3879.825 | 42733.7696 | 39973.7496 | 41577.8146 |  | 73.74% | 62.52% | 69.04% | 29146.26 | 0.010935 | 0.029502 | 210.116 | 185.7936 |  | 18.5%
| 2024 | 11 | 8 | 24856 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 41602.0343 | 5035.78 | 2275.76 | 3879.825 | 46637.8143 | 43877.7943 | 45481.8593 |  | 87.63% | 76.53% | 82.98% | 29454.36 | 0.21388 | 0.0302 | 4109.7618 | 190.1925 |  | 18.5%
| 2024 | 11 | 9 | 24414 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 47136.3237 | 5035.78 | 2275.76 | 3879.825 | 52172.1037 | 49412.0837 | 51016.1487 |  | 113.7% | 102.4% | 109% | 28930.59 | 0.50057 | 0.034278 | 9618.3757 | 215.868 |  | 18.5%
| 2024 | 11 | 10 | 23452 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 49074.8104 | 5035.78 | 2275.76 | 3879.825 | 54110.5904 | 51350.5704 | 52954.6354 |  | 130.7% | 119% | 125.8% | 27790.62 | 0.6003 | 0.037792 | 11534.7261 | 238.0043 |  | 18.5%
| 2024 | 11 | 11 | 22761 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 49386.9108 | 5035.78 | 2275.76 | 3879.825 | 54422.6908 | 51662.6708 | 53266.7358 |  | 139.1% | 127% | 134% | 26971.785 | 0.61676 | 0.037129 | 11851.005 | 233.8258 |  | 18.5%
| 2024 | 11 | 12 | 22695 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 49548.872 | 5035.78 | 2275.76 | 3879.825 | 54584.652 | 51824.632 | 53428.697 |  | 140.5% | 128.4% | 135.4% | 26893.575 | 0.62464 | 0.038788 | 12002.5152 | 244.2768 |  | 18.5%
| 2024 | 11 | 13 | 23378 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 49523.9186 | 5035.78 | 2275.76 | 3879.825 | 54559.6986 | 51799.6786 | 53403.7436 |  | 133.4% | 121.6% | 128.4% | 27702.93 | 0.62373 | 0.037621 | 11984.9143 | 236.9243 |  | 18.5%
| 2024 | 11 | 14 | 24676 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 49159.9969 | 5035.78 | 2275.76 | 3879.825 | 54195.7769 | 51435.7569 | 53039.8219 |  | 119.6% | 108.4% | 114.9% | 29241.06 | 0.60466 | 0.038001 | 11618.5995 | 239.3174 |  | 18.5%
| 2024 | 11 | 15 | 26397 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 47607.4076 | 5035.78 | 2275.76 | 3879.825 | 52643.1876 | 49883.1676 | 51487.2326 |  | 99.43% | 88.97% | 95.05% | 31280.445 | 0.52545 | 0.03315 | 10096.5602 | 208.7674 |  | 18.5%
| 2024 | 11 | 16 | 28415 | 26053.22 | 2280 | 5536.22 | 4541.391 | 1815.23 | 35.1 | 1346.15 | 236.16 | 47559.0738 | 5035.78 | 2275.76 | 3879.825 | 52594.8538 | 49834.8338 | 51438.8988 |  | 85.1% | 75.38% | 81.03% | 33671.775 | 0.28576 | 0.035696 | 5490.8015 | 224.8013 | 0.45 | 18.5%
| 2024 | 11 | 17 | 29921 | 26053.22 | 2280 | 5536.22 | 9082.782 | 1815.23 | 35.1 | 1346.15 | 236.16 | 47082.3081 | 5035.78 | 2275.76 | 3879.825 | 52118.0881 | 49358.0681 | 50962.1331 |  | 74.19% | 64.96% | 70.32% | 35456.385 | 0.025783 | 0.032079 | 495.4203 | 202.0258 | 0.9 | 18.5%
| 2024 | 11 | 18 | 30937 | 26053.22 | 2280 | 5536.22 | 9082.782 | 1815.23 | 35.1 | 1346.15 | 236.16 | 46595.5614 | 5035.78 | 2275.76 | 3879.825 | 51631.3414 | 48871.3214 | 50475.3864 |  | 66.89% | 57.97% | 63.16% | 36660.345 | 0.000602 | 0.03162 | 11.5674 | 199.132 | 0.9 | 18.5%
| 2024 | 11 | 19 | 30077 | 26053.22 | 2280 | 5536.22 | 9082.782 | 1815.23 | 35.1 | 1346.15 | 236.16 | 46620.1012 | 5035.78 | 2275.76 | 3879.825 | 51655.8812 | 48895.8612 | 50499.9262 |  | 71.75% | 62.57% | 67.9% | 35641.245 | 0.000341 | 0.036313 | 6.5523 | 228.6869 | 0.9 | 18.5%
| 2024 | 11 | 20 | 29289 | 26053.22 | 2280 | 5536.22 | 4541.391 | 1815.23 | 35.1 | 1346.15 | 236.16 | 42107.8564 | 5035.78 | 2275.76 | 3879.825 | 47143.6364 | 44383.6164 | 45987.6814 |  | 60.96% | 51.54% | 57.01% | 34707.465 | 0.000284 | 0.041115 | 5.4571 | 258.9283 | 0.45 | 18.5%
| 2024 | 11 | 21 | 27963 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37578.0751 | 5035.78 | 2275.76 | 3879.825 | 42613.8551 | 39853.8351 | 41457.9001 |  | 52.39% | 42.52% | 48.26% | 33136.155 | 0.000284 | 0.042958 | 5.4571 | 270.538 |  | 18.5%
| 2024 | 11 | 22 | 26896 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37572.9089 | 5035.78 | 2275.76 | 3879.825 | 42608.6889 | 39848.6689 | 41452.7339 |  | 58.42% | 48.16% | 54.12% | 31871.76 | 0.000258 | 0.042217 | 4.9575 | 265.8715 |  | 18.5%
| 2024 | 11 | 23 | 25511 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37588.0705 | 5035.78 | 2275.76 | 3879.825 | 42623.8505 | 39863.8305 | 41467.8955 |  | 67.08% | 56.26% | 62.55% | 30230.535 | 0.000258 | 0.044625 | 4.9575 | 281.0331 |  | 18.5%
| 2024 | 11 | 24 | 24219 | 26053.22 | 2280 | 5536.22 | 0 | 1815.23 | 35.1 | 1346.15 | 236.16 | 37582.4539 | 5035.78 | 2275.76 | 3879.825 | 42618.2339 | 39858.2139 | 41462.2789 |  | 75.97% | 64.57% | 71.2% | 28699.515 | 0.000251 | 0.043754 | 4.823 | 275.551 |  | 18.5%
December 2024
| 2024 | 12 | 1 | 23823 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37859.8535 | 5035.78 | 1772 | 3816.855 | 42895.6335 | 39631.8535 | 41676.7085 |  | 80.06% | 66.36% | 74.94% | 28230.255 | 0.000178 | 0.064561 | 3.4203 | 406.5832 |  | 18.5%
| 2024 | 12 | 2 | 22877 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37866.1679 | 5035.78 | 1772 | 3816.855 | 42901.9479 | 39638.1679 | 41683.0229 |  | 87.53% | 73.27% | 82.2% | 27109.245 | 0.000181 | 0.065555 | 3.4779 | 412.84 |  | 18.5%
| 2024 | 12 | 3 | 22317 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37922.5356 | 5035.78 | 1772 | 3816.855 | 42958.3156 | 39694.5356 | 41739.3906 |  | 92.49% | 77.87% | 87.03% | 26445.645 | 0.000261 | 0.074261 | 5.0151 | 467.6705 |  | 18.5%
| 2024 | 12 | 4 | 22152 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37877.7939 | 5035.78 | 1772 | 3816.855 | 42913.5739 | 39649.7939 | 41694.6489 |  | 93.72% | 78.99% | 88.22% | 26250.12 | 0.000261 | 0.067156 | 5.0151 | 422.9288 |  | 18.5%
| 2024 | 12 | 5 | 22590 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37849.1616 | 5035.78 | 1772 | 3816.855 | 42884.9416 | 39621.1616 | 41666.0166 |  | 89.84% | 75.39% | 84.44% | 26769.15 | 0.000261 | 0.06261 | 5.0151 | 394.2965 |  | 18.5%
| 2024 | 12 | 6 | 24139 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37907.4559 | 5035.78 | 1772 | 3816.855 | 42943.2359 | 39679.4559 | 41724.3109 |  | 77.9% | 64.38% | 72.85% | 28604.715 | 0.000261 | 0.071866 | 5.0151 | 452.5908 |  | 18.5%
| 2024 | 12 | 7 | 26440 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37937.6273 | 5035.78 | 1772 | 3816.855 | 42973.4073 | 39709.6273 | 41754.4823 |  | 62.53% | 50.19% | 57.92% | 31331.4 | 0.001794 | 0.07198 | 34.4717 | 453.3056 |  | 18.5%
| 2024 | 12 | 8 | 27794 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 39864.639 | 5035.78 | 1772 | 3816.855 | 44900.419 | 41636.639 | 43681.494 |  | 61.55% | 49.8% | 57.16% | 32935.89 | 0.1014 | 0.074066 | 1948.3434 | 466.4456 |  | 18.5%
| 2024 | 12 | 9 | 27342 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 44062.4213 | 5035.78 | 1772 | 3816.855 | 49098.2013 | 45834.4213 | 47879.2763 |  | 79.57% | 67.63% | 75.11% | 32400.27 | 0.3241 | 0.06112 | 6227.6584 | 384.913 |  | 18.5%
| 2024 | 12 | 10 | 25858 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 46622.499 | 5035.78 | 1772 | 3816.855 | 51658.279 | 48394.499 | 50439.354 |  | 99.78% | 87.15% | 95.06% | 30641.73 | 0.45635 | 0.064141 | 8768.7076 | 403.9414 |  | 18.5%
| 2024 | 12 | 11 | 24327 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 47465.2005 | 5035.78 | 1772 | 3816.855 | 52500.9805 | 49237.2005 | 51282.0555 |  | 115.8% | 102.4% | 110.8% | 28827.495 | 0.49958 | 0.066031 | 9599.5066 | 415.8439 |  | 18.5%
| 2024 | 12 | 12 | 22842 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 47868.6608 | 5035.78 | 1772 | 3816.855 | 52904.4408 | 49640.6608 | 51685.5158 |  | 131.6% | 117.3% | 126.3% | 27067.77 | 0.52055 | 0.066123 | 10002.3875 | 416.4233 |  | 18.5%
| 2024 | 12 | 13 | 22436 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 47709.9015 | 5035.78 | 1772 | 3816.855 | 52745.6815 | 49481.9015 | 51526.7565 |  | 135.1% | 120.5% | 129.7% | 26586.66 | 0.51459 | 0.059099 | 9887.8661 | 372.1854 |  | 18.5%
| 2024 | 12 | 14 | 22783 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 46543.5928 | 5035.78 | 1772 | 3816.855 | 51579.3728 | 48315.5928 | 50360.4478 |  | 126.4% | 112.1% | 121% | 26997.855 | 0.45601 | 0.052652 | 8762.1553 | 331.5875 |  | 18.5%
| 2024 | 12 | 15 | 23884 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 44852.7485 | 5035.78 | 1772 | 3816.855 | 49888.5285 | 46624.7485 | 48669.6035 |  | 108.9% | 95.21% | 103.8% | 28302.54 | 0.3663 | 0.057854 | 7038.5506 | 364.348 |  | 18.5%
| 2024 | 12 | 16 | 25572 | 26060.77 | 2280 | 5899.79 | 4541.391 | 1827.15 | 30.65 | 1139.55 | 211.94 | 46069.2187 | 5035.78 | 1772 | 3816.855 | 51104.9987 | 47841.2187 | 49886.0737 |  | 99.85% | 87.08% | 95.08% | 30302.82 | 0.19489 | 0.052891 | 3744.8882 | 333.0895 | 0.45 | 18.5%
| 2024 | 12 | 17 | 27521 | 26060.77 | 2280 | 5899.79 | 9082.782 | 1827.15 | 30.65 | 1139.55 | 211.94 | 47175.246 | 5035.78 | 1772 | 3816.855 | 52211.026 | 48947.246 | 50992.101 |  | 89.71% | 77.85% | 85.28% | 32612.385 | 0.016831 | 0.050686 | 323.4077 | 319.2063 | 0.9 | 18.5%
| 2024 | 12 | 18 | 29574 | 26060.77 | 2280 | 5899.79 | 9082.782 | 1827.15 | 30.65 | 1139.55 | 211.94 | 46852.9531 | 5035.78 | 1772 | 3816.855 | 51888.7331 | 48624.9531 | 50669.8081 |  | 75.45% | 64.42% | 71.33% | 35045.19 | 0.000401 | 0.04964 | 7.7052 | 312.6158 | 0.9 | 18.5%
| 2024 | 12 | 19 | 29481 | 26060.77 | 2280 | 5899.79 | 9082.782 | 1827.15 | 30.65 | 1139.55 | 211.94 | 46872.5223 | 5035.78 | 1772 | 3816.855 | 51908.3023 | 48644.5223 | 50689.3773 |  | 76.07% | 65% | 71.94% | 34934.985 | 0.00034 | 0.052933 | 6.5331 | 333.3572 | 0.9 | 18.5%
| 2024 | 12 | 20 | 29270 | 26060.77 | 2280 | 5899.79 | 4541.391 | 1827.15 | 30.65 | 1139.55 | 211.94 | 42343.6875 | 5035.78 | 1772 | 3816.855 | 47379.4675 | 44115.6875 | 46160.5425 |  | 61.87% | 50.72% | 57.71% | 34684.95 | 0.000326 | 0.05497 | 6.2641 | 346.1824 | 0.45 | 18.5%
| 2024 | 12 | 21 | 28619 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37800.2319 | 5035.78 | 1772 | 3816.855 | 42836.0119 | 39572.2319 | 41617.0869 |  | 49.68% | 38.27% | 45.42% | 33913.515 | 0.000261 | 0.05484 | 5.0151 | 345.3668 |  | 18.5%
| 2024 | 12 | 22 | 27651 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37818.9202 | 5035.78 | 1772 | 3816.855 | 42854.7002 | 39590.9202 | 41635.7752 |  | 54.98% | 43.18% | 50.58% | 32766.435 | 0.000261 | 0.057808 | 5.0151 | 364.0551 |  | 18.5%
| 2024 | 12 | 23 | 26337 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37828.0802 | 5035.78 | 1772 | 3816.855 | 42863.8602 | 39600.0802 | 41644.9352 |  | 62.75% | 50.36% | 58.12% | 31209.345 | 0.000261 | 0.059262 | 5.0151 | 373.2151 |  | 18.5%
| 2024 | 12 | 24 | 25181 | 26060.77 | 2280 | 5899.79 | 0 | 1827.15 | 30.65 | 1139.55 | 211.94 | 37810.2218 | 5035.78 | 1772 | 3816.855 | 42846.0018 | 39582.2218 | 41627.0768 |  | 70.15% | 57.19% | 65.31% | 29839.485 | 0.000247 | 0.056469 | 4.7461 | 355.6257 |  | 18.5%

## Existing Resources (NQC MW)
Resource_ID | Resource_Name | RESOURCE_TYPE | COD | COD2 | ENERGY_SOURCE | UNIT_TYPE | Strategic Reserve Resource? | NET_DEPENDABLE_CAPACITY | NAMEPLATE_CAPACITY | PTO_AREA | On NQC LIST | Deliverability Status | 2024-01-01 | 2024-02-01 | 2024-03-01 | 2024-04-01 | 2024-05-01 | 2024-06-01 | 2024-07-01 | 2024-08-01 | 2024-09-01 | 2024-10-01 | 2024-11-01 | 2024-12-01 | *CAISO Public*
7STDRD_1_SOLAR1 | Shafter Solar | GEN | 2015-06-04 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
ACACIA_6_SOLAR | West Antelope Solar | GEN | 2014-11-13 | 2014 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
ADERA_1_SOLAR1 | Adera Solar | GEN | 2015-12-23 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ADLIN_1_UNITS | GEYSERS AIDLIN AGGREGATE | GEN | 2008-07-28 | 2008 | GEOTHERMAL | STEAM |  | 22 | 23 | PGAE | NQC | FC | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
ADMEST_6_SOLAR | Adams East | GEN | 2014-12-13 | 2014 | SUN | PHOTO VOLTAIC |  | 19 | 19 | PGAE | NQC | ID | 0.08 | 0.57 | 0.67 | 0.84 | 1.22 | 2.49 | 2.74 | 2.36 | 2.11 | 1.41 | 1.08 | 0.67
ADOBEE_1_SOLAR | Adobe Solar | GEN | 2014-05-21 | 2014 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
AGRICO_6_FEGBT1 | Fresno EGT | GEN | 0 |  | LESR | OTHER |  | 50.6 | 50.6 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AGRICO_6_PL3N5 | Fresno Peaker | GEN | 2006-08-30 | 2006 | NATURAL GAS | COMBUSTION TURBINE |  | 22.69 | 0 | PGAE | NQC | FC | 22.69 | 22.69 | 22.69 | 22.69 | 22.69 | 22.69 | 22.69 | 22.69 | 22.69 | 22.69 | 22.69 | 22.69
AGRICO_6_UNIT 3 | Fresno Peaker AG PL3N5 ICE5 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 21 | 21 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AGRICO_7_UNIT | Fresno Cogen | GEN | 2023-03-14 | 2023 | NATURAL GAS | OTHER |  | 50.6 | 0 | PGAE | NQC | FC | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
AGRICO_7_UNIT 4 | Fresno Cogen GT Unit 4 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 46.5 | 46.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AGUCAL_5_SOLAR1 | Agua Caliente Solar | GEN | 2014-06-10 | 2014 | SUN | PHOTO VOLTAIC |  | 290 | 290 | SDGE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AKINGS_6_AMESR1 | American Kings Solar | GEN | 2020-12-05 | 2020 | SUN | PHOTO VOLTAIC |  | 123 | 123 | PGAE | NQC | FC | 0.49 | 3.69 | 4.31 | 5.41 | 7.87 | 16.11 | 17.71 | 15.25 | 13.65 | 9.1 | 7.01 | 4.31
ALAMIT_2_PL1X3 | Alamitos Energy Center Unit 7 | GEN | 2020-02-06 | 2020 | NATURAL GAS | COMBINED CYCLE |  | 674.7 | 0 | SCE | NQC | FC | 674.7 | 674.7 | 674.7 | 674.7 | 674.7 | 674.7 | 674.7 | 674.7 | 674.7 | 674.7 | 674.7 | 674.7
ALAMIT_7_CTG1A | ALAMIT_7_CTG1A | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 234.5 | 234.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALAMIT_7_CTG1B | ALAMIT_7_CTG1B | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 234.5 | 234.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALAMIT_7_ES1 | Alamitos Energy Storage | GEN | 2020-12-04 | 2020 | LESR | OTHER |  | 100.45 | 100 | SCE | NQC | FC | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ALAMIT_7_STG1S | ALAMIT_7_STG1S | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 241.5 | 241.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALAMIT_7_UNIT 3 | ALAMITOS GEN STA. UNIT 3 | GEN | 1961-01-01 | 1961 | NATURAL GAS | STEAM | Yes | 326.76 | 322 | SCE | NQC | FC | 326.76 | 326.76 | 326.76 | 326.76 | 326.76 | 326.76 | 326.76 | 326.76 | 326.76 | 326.76 | 326.76 | 326.76
ALAMIT_7_UNIT 4 | ALAMITOS GEN STA. UNIT 4 | GEN | 1962-01-01 | 1962 | NATURAL GAS | STEAM | Yes | 334.43 | 320 | SCE | NQC | FC | 334.43 | 334.43 | 334.43 | 334.43 | 334.43 | 334.43 | 334.43 | 334.43 | 334.43 | 334.43 | 334.43 | 334.43
ALAMIT_7_UNIT 5 | ALAMITOS GEN STA. UNIT 5 | GEN | 1999-01-01 | 1999 | NATURAL GAS | STEAM | Yes | 480 | 482 | SCE | NQC | FC | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480 | 480
ALAMO_6_UNIT | ALAMO POWER PLANT | GEN | 1986-01-01 | 1986 | WATER | HYDRO |  | 17 | 18 | SCE | NQC | FC | 13.22 | 14 | 12.02 | 13.92 | 13.71 | 14 | 14 | 14 | 9.54 | 9.72 | 13.63 | 11.53
ALHMBR_1_ALHSLR | SG Alhambra | TG | 2015-08-29 | 2015 | SUN | PHOTO VOLTAIC |  | 50 | 50 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALLGNY_6_HYDRO1 | Salmon Creek Hydroelectric Project | GEN | 2014-12-03 | 2014 | WATER | HYDRO |  | 0.52 | 0.6 | PGAE | NQC | FC | 0.14 | 0.25 | 0.32 | 0.48 | 0.48 | 0.14 | 0.03 | 0 | 0 | 0.03 | 0.14 | 0.08
ALMASL_2_AL6BT6 | Almasol 6 BES | GEN | 2022-06-27 | 2022 | LESR | OTHER |  | 50 | 50 | SCE | NQC | FC | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
ALMASL_2_GS1SR1 | Almasol Generating Station 1 | GEN | 2020-12-11 | 2020 | SUN | PHOTO VOLTAIC |  | 125 | 125 | SCE | NQC | FC | 0.5 | 3.75 | 4.38 | 5.5 | 8 | 16.38 | 18 | 15.5 | 13.88 | 9.25 | 7.13 | 4.38
ALMASL_2_GS4SR4 | Almasol Generating Station 4 | GEN | 2020-12-11 | 2020 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE | NQC | FC | 0.4 | 3 | 3.5 | 4.4 | 6.4 | 13.1 | 14.4 | 12.4 | 11.1 | 7.4 | 5.7 | 3.5
ALMASL_2_GS6SR6 | Almasol Generating Station 6 | GEN | 2021-10-22 | 2021 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE | NQC | FC | 0.24 | 2.11 | 2.56 | 3.43 | 5.1 | 10.48 | 11.34 | 9.58 | 8.31 | 5.34 | 3.8 | 1.96
ALMASL_2_GS7SR7 | Almasol Generating Station 7 | GEN | 2021-12-22 | 2021 | SUN | PHOTO VOLTAIC |  | 132 | 132 | SCE | NQC | FC | 0.53 | 3.96 | 4.62 | 5.81 | 8.45 | 17.29 | 19.01 | 16.37 | 14.65 | 9.77 | 7.52 | 4.62
ALMEGT_1_UNIT 1 | ALAMEDA GT UNIT 1 | GEN | 1986-01-01 | 1986 | NATURAL GAS | FTUR |  | 25 | 25.4 | PGAE | NQC | FC | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4
ALMEGT_1_UNIT 2 | ALAMEDA GT UNIT 2 | GEN | 1986-01-01 | 1986 | NATURAL GAS | FTUR |  | 25 | 25.4 | PGAE | NQC | FC | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5
ALPAUG_1_TUDSR1 | Tulare DAC Solar | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 3 | 3 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALPSLR_1_NTHSLR | Alpaugh North, LLC | GEN | 2013-03-08 | 2013 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
ALPSLR_1_SPSSLR | Alpaugh 50 LLC | GEN | 2013-03-08 | 2013 | SUN | PHOTO VOLTAIC |  | 50 | 50 | PGAE | NQC | FC | 0.2 | 1.5 | 1.75 | 2.2 | 3.2 | 6.55 | 7.2 | 6.2 | 5.55 | 3.7 | 2.85 | 1.75
ALT6DN_2_WIND7 | Pinyon Pines 1 | GEN | 2013-01-01 | 2013 | WIND | WIND |  | 164.31 | 168 | SCE | NQC | FC | 29.03 | 30.88 | 27.13 | 25.99 | 27.64 | 25.34 | 23.54 | 17.89 | 18.48 | 17.14 | 23.1 | 27.98
ALT6DS_2_WIND9 | Pinyon Pines 2 | GEN | 2013-01-01 | 2013 | WIND | WIND |  | 132 | 132 | SCE | NQC | FC | 23.32 | 24.81 | 21.8 | 20.88 | 22.21 | 20.35 | 18.91 | 14.37 | 14.84 | 13.77 | 18.56 | 22.48
ALTA3A_2_CPCE4 | Alta Wind 4 | GEN | 2011-03-12 | 2011 | WIND | WIND |  | 102 | 102 | SCE | NQC | FC | 18.02 | 19.17 | 16.84 | 16.14 | 17.16 | 15.73 | 14.61 | 11.1 | 11.47 | 10.64 | 14.34 | 17.37
ALTA3A_2_CPCE5 | Alta Wind 5 | GEN | 2011-04-21 | 2011 | WIND | WIND |  | 168 | 168 | SCE | NQC | FC | 29.69 | 31.57 | 27.74 | 26.58 | 28.26 | 25.91 | 24.07 | 18.29 | 18.89 | 17.53 | 23.62 | 28.61
ALTA3A_2_CPCE8 | Alta Wind 8 | GEN | 2012-02-01 | 2012 | WIND | WIND |  | 150 | 150 | SCE | NQC | FC | 26.51 | 28.19 | 24.77 | 23.73 | 25.23 | 23.13 | 21.49 | 16.33 | 16.87 | 15.65 | 21.09 | 25.55
ALTA4A_2_CPCW1 | Alta Wind 1 | GEN | 2010-12-29 | 2010 | WIND | WIND |  | 150 | 150 | SCE | NQC | FC | 26.51 | 28.19 | 24.77 | 23.73 | 25.23 | 23.13 | 21.49 | 16.33 | 16.87 | 15.65 | 21.09 | 25.55
ALTA4B_2_CPCW2 | Alta Wind 2 | GEN | 2010-12-29 | 2010 | WIND | WIND |  | 150 | 150 | SCE | NQC | FC | 26.51 | 28.19 | 24.77 | 23.73 | 25.23 | 23.13 | 21.49 | 16.33 | 16.87 | 15.65 | 21.09 | 25.55
ALTA4B_2_CPCW3 | Alta Wind 3 | GEN | 2011-02-12 | 2011 | WIND | WIND |  | 150 | 150 | SCE | NQC | FC | 26.51 | 28.19 | 24.77 | 23.73 | 25.23 | 23.13 | 21.49 | 16.33 | 16.87 | 15.65 | 21.09 | 25.55
ALTA4B_2_CPCW6 | Mustang Hills | GEN | 2012-05-09 | 2012 | WIND | WIND |  | 150 | 150 | SCE | NQC | FC | 26.51 | 28.19 | 24.77 | 23.73 | 25.23 | 23.13 | 21.49 | 16.33 | 16.87 | 15.65 | 21.09 | 25.55
ALTA6B_2_WIND11 | Alta Wind 11 | GEN | 2014-03-13 | 2014 | WIND | WIND |  | 88.15 | 90 | SCE | NQC | FC | 15.58 | 16.57 | 14.56 | 13.95 | 14.83 | 13.59 | 12.63 | 9.6 | 9.91 | 9.2 | 12.39 | 15.01
ALTA6E_2_WIND10 | Alta Wind 10 | GEN | 2014-03-13 | 2014 | WIND | WIND |  | 134.84 | 138 | SCE | NQC | FC | 23.83 | 25.34 | 22.27 | 21.33 | 22.68 | 20.79 | 19.32 | 14.68 | 15.16 | 14.07 | 18.96 | 22.96
ALTWD_2_AT3WD3 | Altech 3 | GEN | 2021-06-24 | 2021 | WIND | WIND |  | 9.8 | 9.8 | SCE | NQC | FC | 1.73 | 1.84 | 1.62 | 1.55 | 1.65 | 1.51 | 1.4 | 1.07 | 1.1 | 1.02 | 1.38 | 1.67
ALTWD_2_COAWD1 | Coachella 1 | GEN | 2021-04-13 | 2021 | WIND | WIND |  | 50.4 | 50.4 | SCE | NQC | FC | 8.91 | 9.47 | 8.32 | 7.97 | 8.48 | 7.77 | 7.22 | 5.49 | 5.67 | 5.26 | 7.09 | 8.58
ANAHM_2_CANYN1 | CANYON POWER PLANT UNIT 1 | GEN | 2011-09-16 | 2011 | NATURAL GAS | COMBUSTION TURBINE |  | 49.21 | 71.2 | SCE | NQC | FC | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21
ANAHM_2_CANYN2 | CANYON POWER PLANT UNIT 2 | GEN | 2011-09-16 | 2011 | NATURAL GAS | COMBUSTION TURBINE |  | 48.04 | 71.2 | SCE | NQC | FC | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04
ANAHM_2_CANYN3 | CANYON POWER PLANT UNIT 3 | GEN | 2011-07-30 | 2011 | NATURAL GAS | COMBUSTION TURBINE |  | 46.49 | 71.2 | SCE | NQC | FC | 46.49 | 46.49 | 46.49 | 46.49 | 46.49 | 46.49 | 46.49 | 46.49 | 46.49 | 46.49 | 46.49 | 46.49
ANAHM_2_CANYN4 | CANYON POWER PLANT UNIT 4 | GEN | 2011-07-30 | 2011 | NATURAL GAS | COMBUSTION TURBINE |  | 49.8 | 71.2 | SCE | NQC | FC | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
ANZA_6_SOLAR1 | Seville Solar One | TG | 2015-12-30 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
APLHIL_1_SFKHY1 | South Fork Powerhouse | GEN | 2020-12-04 | 2020 | WATER | HYDRO |  | 2.68 | 2.7 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AQUAWS_2_AQWSR1 | Aquamarine Westside | GEN | 2021-12-08 | 2021 | SUN | PHOTO VOLTAIC |  | 250 | 0 | PGAE | NQC | ID | 1 | 7.5 | 8.75 | 11 | 16 | 32.75 | 36 | 31 | 27.75 | 18.5 | 14.25 | 8.75
AQUAWS_2_AQWSU1 | Aquamarine Westside | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 125 | 13.5 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AQUAWS_2_AQWSU2 | Aquamarine Westside | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 125 | 13.5 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ARBWD_6_QF | Wind Resource II | GEN | 2013-05-17 | 2013 | WIND | WIND |  | 19.95 | 21.8 | SCE | NQC | FC | 3.53 | 3.75 | 3.29 | 3.16 | 3.36 | 3.08 | 2.86 | 2.17 | 2.24 | 2.08 | 2.8 | 3.4
ARCOGN_2_UNITS | WATSON COGENERATION | GEN | 1987-12-04 | 1987 | NATURAL GAS | COMBINED CYCLE |  | 305 | 416.6 | SCE | NQC | FC | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305
ARKANS_1_ARKSLR | SG Arkansas | TG | 2015-08-29 | 2015 | SUN | PHOTO VOLTAIC |  | 50 | 50 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ARLINT_5_SCEDYN | Arlington Valley CC | TG | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 565 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ARLNTN_2_AR1SR1 | Arlington | GEN | 2022-03-21 | 2022 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE | NQC | ID | 0 | 0.62 | 0.91 | 1.79 | 2.85 | 6.01 | 6.2 | 4.82 | 3.57 | 1.81 | 0.5 | 0
ARLNTN_2_ASUSR1 | Arlington Solar Unit 1 | GEN | 2022-08-01 | 2022 | SUN | PHOTO VOLTAIC |  | 131 | 131 | SCE | NQC | ID | 0.17 | 1.94 | 2.43 | 3.51 | 5.39 | 11.13 | 12.02 | 9.85 | 8.11 | 4.68 | 2.99 | 0.83
ARLVAL_5_SOLAR | Arlington Valley Solar Energy II | TG | 2013-10-28 | 2013 | SUN | PHOTO VOLTAIC |  | 127 | 127 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ARVINN_6_ORION1 | Orion 1 Solar | GEN | 2014-06-26 | 2014 | SUN | PHOTO VOLTAIC |  | 12 | 12 | PGAE | NQC | FC | 0.05 | 0.36 | 0.42 | 0.53 | 0.77 | 1.57 | 1.73 | 1.49 | 1.33 | 0.89 | 0.68 | 0.42
ARVINN_6_ORION2 | Orion 2 Solar | GEN | 2014-06-26 | 2014 | SUN | PHOTO VOLTAIC |  | 8 | 8 | PGAE | NQC | FC | 0.03 | 0.24 | 0.28 | 0.35 | 0.51 | 1.05 | 1.15 | 0.99 | 0.89 | 0.59 | 0.46 | 0.28
ASTORA_2_SOLAR1 | Astoria 1 | GEN | 2016-10-18 | 2016 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE | NQC | FC | 0.4 | 3 | 3.5 | 4.4 | 6.4 | 13.1 | 14.4 | 12.4 | 11.1 | 7.4 | 5.7 | 3.5
ASTORA_2_SOLAR2 | Astoria 2 | GEN | 2016-10-31 | 2016 | SUN | PHOTO VOLTAIC |  | 75 | 75 | SCE | NQC | FC | 0.3 | 2.25 | 2.63 | 3.3 | 4.8 | 9.83 | 10.8 | 9.3 | 8.33 | 5.55 | 4.28 | 2.63
ATHOS_5_AP1SR1 | Athos Power Plant | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 125 | 125 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ATHOS_5_AP1SR2 | Athos Power Plant | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 125 | 125 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ATHOS_5_AP1X2 | Athos Power Plant | GEN | 2022-05-13 | 2022 | SUN | PHOTO VOLTAIC |  | 250 | 0 | SCE | NQC | FC | 1 | 7.5 | 8.75 | 11 | 16 | 32.75 | 36 | 31 | 27.75 | 18.5 | 14.25 | 8.75
ATHOS_5_AP2SR3 | Athos Power Plant 2 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 100 | 100 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ATHOS_5_AP2SR4 | Athos Power Plant 2 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 100 | 100 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ATHOS_5_AP2X2 | Athos Power Plant 2 | GEN | 2021-12-16 | 2021 | SUN | PHOTO VOLTAIC |  | 200 | 0 | SCE | NQC | FC | 0.8 | 6 | 7 | 8.8 | 12.8 | 26.2 | 28.8 | 24.8 | 22.2 | 14.8 | 11.4 | 7
ATWEL2_1_SOLAR1 | Atwell West | GEN | 2015-06-11 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
ATWELL_1_SOLAR | Atwell Island PV Solar Generating Faci. | GEN | 2013-03-08 | 2013 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
AVENAL_6_AVPARK | Avenal Park Solar Project | GEN | 2011-08-05 | 2011 | SUN | PHOTO VOLTAIC |  | 6 | 6 | PGAE | NQC | ID | 0.02 | 0.18 | 0.21 | 0.26 | 0.38 | 0.79 | 0.86 | 0.74 | 0.67 | 0.44 | 0.34 | 0.21
AVENAL_6_AVSLR1 | Avenal Solar 1 | GEN | 2017-01-28 | 2017 | SUN | PHOTO VOLTAIC |  | 7.9 | 7.9 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AVENAL_6_AVSLR2 | Avenal Solar 2 | GEN | 2017-01-28 | 2017 | SUN | PHOTO VOLTAIC |  | 7.9 | 7.9 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AVENAL_6_SANDDG | Sand Drag Solar Project | GEN | 2011-08-05 | 2011 | SUN | PHOTO VOLTAIC |  | 19 | 19 | PGAE | NQC | ID | 0.07 | 0.48 | 0.56 | 0.7 | 1.02 | 2.08 | 2.29 | 1.97 | 1.76 | 1.18 | 0.9 | 0.56
AVENAL_6_SUNCTY | Sun City Solar Project | GEN | 2011-08-05 | 2011 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | ID | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
AVSOLR_2_SOLAR | AV SOLAR RANCH 1 | GEN | 2014-06-19 | 2014 | SUN | PHOTO VOLTAIC |  | 241.5 | 250 | SCE | NQC | FC | 0.97 | 7.25 | 8.45 | 10.63 | 15.46 | 31.64 | 34.78 | 29.95 | 26.81 | 17.87 | 13.77 | 8.45
BAHIA_2_LKHSR1 | Lake Herman Solar | GEN | 2021-09-23 | 2021 | SUN | PHOTO VOLTAIC |  | 5 | 5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BALCHS_7_UNIT 1 | BALCH 1 PH UNIT 1 | GEN | 1927-01-01 | 1927 | WATER | HYDRO |  | 31 | 34 | PGAE | NQC | FC | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 24.8 | 31 | 31 | 31 | 28.2 | 24.8 | 24.8
BALCHS_7_UNIT 2 | BALCH 2 PH UNIT 2 | GEN | 1958-01-01 | 1958 | WATER | HYDRO |  | 52.5 | 52.5 | PGAE | NQC | FC | 42 | 42 | 0 | 42 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5
BALCHS_7_UNIT 3 | BALCH 2 PH UNIT 3 | GEN | 1958-01-01 | 1958 | WATER | HYDRO |  | 54.6 | 54.6 | PGAE | NQC | FC | 43.68 | 0 | 24.8 | 43.68 | 54.18 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 43.68
BANKPP_2_NSPIN | BANKPP_2_NSPIN | GEN | 0 |  | WATER | PUMP |  | 270 | 270 | PGAE | NQC | FC | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127
BARRE_2_ALASB1 | Los Alamitos 1 | GEN | 2023-11-10 | 2023 | HYBD | OTHER |  | 10 | 10 | SCE | NQC | FC | 5.02 | 5.21 | 5.25 | 5.34 | 5.5 | 6.04 | 6.13 | 5.96 | 5.83 | 5.52 | 5.37 | 5.18
BARRE_2_QF | BARRE QFS | GEN | 1994-01-01 | 1994 | OTHER | OTHER |  | 0.2 | 0.2 | SCE | NQC | FC | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BARRE_6_PEAKER | Barre Peaker | GEN | 2007-09-20 | 2007 | NATURAL GAS | COMBUSTION TURBINE |  | 49 | 59 | SCE | NQC | FC | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
BASICE_2_UNITS | King City Cogen | GEN | 1989-03-14 | 1989 | NATURAL GAS | COMBINED CYCLE |  | 120 | 120 | PGAE | NQC | FC | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BCTSYS_5_PWXDYN | BCTSYS_5_PWXDYN | TG | 0 |  | WATER | 0 |  | 428 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BDGRCK_1_UNITS | BADGER CREEK LIMITED | GEN | 1991-04-01 | 1991 | NATURAL GAS | COMBUSTION TURBINE |  | 48.08 | 55.3 | PGAE | NQC | FC | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08
BEARDS_7_UNIT 1 | Beardsley Hydro | GEN | 1957-01-01 | 1957 | WATER | HYDRO |  | 11.5 | 11.5 | PGAE | NQC | FC | 4.3 | 2.74 | 2 | 6.54 | 5.96 | 9.1 | 5.54 | 5.94 | 3.8 | 3.2 | 2.72 | 6.18
BEARMT_1_UNIT | Bear Mountain Limited | GEN | 1995-04-03 | 1995 | NATURAL GAS | COMBUSTION TURBINE |  | 49.21 | 48.1 | PGAE | NQC | FC | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21 | 49.21
BEJNLS_5_BV2SCEDYN | Broadview 2 | TG | 2017-01-27 | 2017 | WIND | WIND |  | 167 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BEKWJS_5_BV1SCEDYN | Broadview 1 | TG | 2017-01-27 | 2017 | WIND | WIND |  | 130 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BELDEN_7_UNIT 1 | BELDEN HYDRO | GEN | 1969-01-01 | 1969 | WATER | HYDRO |  | 119 | 119 | PGAE | NQC | FC | 1.6 | 1.6 | 0 | 0 | 0 | 35.2 | 38.7 | 38.7 | 38.7 | 38.7 | 0 | 1.6
BERCYN_2_BCEBT1 | Bear Canyon Energy Storage | GEN | 0 |  | LESR | OTHER |  | 13 | 13 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK1_7_PORTAL | PORTAL HYDRO | GEN | 0 |  | WATER | HYDRO |  | 10.8 | 10.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK1_7_UNIT 1 | BIG CREEK PH 1 UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 19.8 | 19.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK1_7_UNIT 2 | BIG CREEK PH 1 UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 15.8 | 15.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK1_7_UNIT 3 | BIG CREEK PH 1 UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 21.6 | 21.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK1_7_UNIT 4 | BIG CREEK PH 1 UNIT 4 | GEN | 0 |  | WATER | HYDRO |  | 31.2 | 31.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK2_7_UNIT 1 | BIG CREEK PH 2 UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 55 | 55 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK2_7_UNIT 2 | BIG CREEK PH 2 UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 55 | 55 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK2_7_UNIT 3 | BIG CREEK PH 2 UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 15.8 | 15.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK2_7_UNIT 4 | BIG CREEK PH 2 UNIT 4 | GEN | 0 |  | WATER | HYDRO |  | 15.8 | 15.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK2_7_UNIT 5 | BIG CREEK PH 2 UNIT 5 | GEN | 0 |  | WATER | HYDRO |  | 17.5 | 17.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK2_7_UNIT 6 | BIG CREEK PH 2 UNIT 6 | GEN | 0 |  | WATER | HYDRO |  | 17.5 | 17.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK3_7_UNIT 1 | BIG CREEK PH 3 UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 34 | 34 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK3_7_UNIT 2 | BIG CREEK PH 3 UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 34 | 34 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK3_7_UNIT 3 | BIG CREEK PH 3 UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 34 | 34 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK3_7_UNIT 4 | BIG CREEK PH 3 UNIT 4 | GEN | 0 |  | WATER | HYDRO |  | 36 | 36 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK3_7_UNIT 5 | BIG CREEK PH 3 UNIT 5 | GEN | 0 |  | WATER | HYDRO |  | 36.5 | 36.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK4_7_UNIT 1 | BIG CREEK PH 4 UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 50 | 50 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK4_7_UNIT 2 | BIG CREEK PH 4 UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 50 | 50 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK8_7_UNIT 1 | BIG CREEK PH 8 UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 30 | 30 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGCRK8_7_UNIT 2 | BIG CREEK PH 8 UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 45 | 45 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BGSKYN_2_AS2SR1 | Antelope Solar 2 | GEN | 2018-12-18 | 2018 | SUN | PHOTO VOLTAIC |  | 105 | 105 | SCE | NQC | ID | 0.34 | 2.71 | 3.2 | 4.14 | 6.06 | 12.39 | 13.56 | 11.58 | 10.19 | 6.66 | 4.93 | 2.79
BGSKYN_2_ASPSR2 | Antelope Solar 2 San Pablo | GEN | 2019-08-03 | 2019 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE | NQC | ID | 0.32 | 2.58 | 3.05 | 3.94 | 5.77 | 11.8 | 12.91 | 11.03 | 9.7 | 6.35 | 4.7 | 2.66
BGSKYN_2_ASSR1B | Antelope Solar 1B | GEN | 2022-11-23 | 2022 | SUN | PHOTO VOLTAIC |  | 17 | 17 | SCE | NQC | ID | 6.94 | 9.5 | 11.05 | 14.17 | 15.09 | 14.73 | 14.53 | 13.42 | 12.18 | 10.49 | 7.16 | 5.7
BGSKYN_2_ASSR3A | Antelope Solar 3A | GEN | 2021-06-22 | 2021 | SUN | PHOTO VOLTAIC |  | 15 | 15 | SCE | NQC | ID | 0.05 | 0.39 | 0.46 | 0.59 | 0.87 | 1.77 | 1.94 | 1.65 | 1.46 | 0.95 | 0.7 | 0.4
BGSKYN_2_ASSR3B | Antelope Solar 3B | GEN | 2021-06-22 | 2021 | SUN | PHOTO VOLTAIC |  | 5 | 5 | SCE | NQC | ID | 0.02 | 0.13 | 0.15 | 0.2 | 0.29 | 0.59 | 0.65 | 0.55 | 0.49 | 0.32 | 0.23 | 0.13
BGSKYN_2_BS3SR3 | Big Sky Solar 3 | GEN | 2019-09-14 | 2019 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.06 | 0.52 | 0.61 | 0.79 | 1.15 | 2.36 | 2.58 | 2.21 | 1.94 | 1.27 | 0.94 | 0.53
BIGCRK_2_EXESWD | BIG CREEK HYDRO PROJECT PSP | GEN | 1913-01-01 | 1913 | WATER | HYDRO |  | 820 | 0 | SCE | NQC | FC | 490.44 | 553.8 | 507 | 561.6 | 700 | 728.6 | 706.43 | 700 | 700 | 455.76 | 483 | 498.28
BIGCRK_7_DAM7 | DAM 7 AT BIG CREEK (FISHWATER GEN) | GEN | 1986-01-01 | 1986 | WATER | HYDRO |  | 0.3 | 0.3 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BIGCRK_7_MAMRES | MAMMOTH POOL RESERVOIR (FISHWATER | GEN | 0 |  | WATER | HYDRO |  | 1.25 | 1.3 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BIGSKY_2_AS2BT1 | Antelope Solar 2 LAB | GEN | 2022-09-02 | 2022 | LESR | OTHER |  | 127 | 127 | SCE | NQC | ID | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127
BIGSKY_2_ASLBT2 | Antelope Solar 2 Luna | GEN | 2022-07-30 | 2022 | LESR | OTHER |  | 100 | 100 | SCE | NQC | ID | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
BIGSKY_2_BSKSR6 | Big Sky Solar 6 | GEN | 2017-12-08 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.06 | 0.52 | 0.61 | 0.79 | 1.15 | 2.36 | 2.58 | 2.21 | 1.94 | 1.27 | 0.94 | 0.53
BIGSKY_2_BSKSR7 | Big Sky Solar 7 | GEN | 2017-12-08 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.06 | 0.52 | 0.61 | 0.79 | 1.15 | 2.36 | 2.58 | 2.21 | 1.94 | 1.27 | 0.94 | 0.53
BIGSKY_2_BSKSR8 | Big Sky Solar 8 | GEN | 2017-12-08 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.06 | 0.52 | 0.61 | 0.79 | 1.15 | 2.36 | 2.58 | 2.21 | 1.94 | 1.27 | 0.94 | 0.53
BIGSKY_2_SOLAR1 | Antelope Big Sky Ranch | GEN | 2016-08-19 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
BIGSKY_2_SOLAR2 | Big Sky Solar 4 | GEN | 2016-12-03 | 2016 | SUN | PHOTO VOLTAIC |  | 40 | 40 | SCE | NQC | FC | 16.29 | 22.17 | 26.04 | 32.99 | 34.97 | 34.31 | 34.61 | 31.53 | 28.76 | 24.78 | 16.97 | 12.6
BIGSKY_2_SOLAR3 | Big Sky Summer | GEN | 2016-07-25 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
BIGSKY_2_SOLAR4 | Western Antelope Blue Sky Ranch B | GEN | 2016-12-03 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 8.18 | 11.27 | 12.98 | 16.84 | 18.02 | 17.5 | 16.89 | 15.82 | 14.27 | 12.28 | 8.35 | 6.21
BIGSKY_2_SOLAR5 | Big Sky Solar 2 | GEN | 2016-11-30 | 2016 | SUN | PHOTO VOLTAIC |  | 5 | 5 | SCE | NQC | FC | 0.02 | 0.13 | 0.15 | 0.2 | 0.29 | 0.59 | 0.65 | 0.55 | 0.49 | 0.32 | 0.23 | 0.13
BIGSKY_2_SOLAR6 | Solverde 1 | GEN | 2016-12-17 | 2016 | SUN | PHOTO VOLTAIC |  | 85 | 85 | SCE | NQC | FC | 0.28 | 2.2 | 2.59 | 3.35 | 4.91 | 10.03 | 10.97 | 9.37 | 8.25 | 5.39 | 3.99 | 2.26
BIGSKY_2_SOLAR7 | Big Sky Solar 1 | GEN | 2016-12-15 | 2016 | SUN | PHOTO VOLTAIC |  | 50 | 50 | SCE | NQC | FC | 0.2 | 1.5 | 1.75 | 2.2 | 3.2 | 6.55 | 7.2 | 6.2 | 5.55 | 3.7 | 2.85 | 1.75
BIOMAS_1_UNIT 1 | WOODLAND BIOMASS | GEN | 1989-08-31 | 1989 | BIOMASS | STEAM |  | 25.5 | 28.8 | PGAE | NQC | FC | 15.98 | 15.69 | 7.86 | 8.07 | 8.06 | 7.5 | 7.93 | 8.07 | 15.24 | 8.03 | 12.07 | 16.22
BISHOP_1_ALAMO | BISHOP CREEK PLANT 2 AND 6 | GEN | 1908-01-01 | 1908 | WATER | HYDRO |  | 13.4 | 13.4 | SCE | NQC | FC | 3.13 | 2.38 | 2.6 | 3.84 | 7.55 | 7.84 | 6.7 | 6.15 | 4.45 | 3.01 | 2.57 | 2.08
BISHOP_1_UNITS | BISHOP CREEK PLANT 3 AND 4 | GEN | 1905-01-01 | 1905 | WATER | HYDRO |  | 15.8 | 15.8 | SCE | NQC | FC | 4.91 | 3.68 | 2.96 | 6.32 | 10.33 | 10.75 | 9.38 | 7.28 | 6.91 | 5.04 | 4.13 | 4.3
BKRFLD_2_SOLAR1 | Bakersfield 111 | GEN | 2015-07-28 | 2015 | SUN | PHOTO VOLTAIC |  | 1.38 | 1.4 | PGAE | NQC | FC | 0.01 | 0.04 | 0.05 | 0.06 | 0.09 | 0.18 | 0.2 | 0.17 | 0.15 | 0.1 | 0.08 | 0.05
BLACK_7_UNIT 1 | JAMES B. BLACK 1 | GEN | 1966-01-01 | 1966 | WATER | HYDRO |  | 85 | 84 | PGAE | NQC | FC | 84.2 | 82.4 | 82.4 | 82.4 | 84 | 84.6 | 84.4 | 84.4 | 82 | 68 | 68 | 84
BLACK_7_UNIT 2 | JAMES B. BLACK 2 | GEN | 1965-01-01 | 1965 | WATER | HYDRO |  | 84.1 | 84.1 | PGAE | NQC | FC | 83.48 | 83.28 | 83.28 | 82 | 83.28 | 83.88 | 84.08 | 84.08 | 84.08 | 67.28 | 83.48 | 83.28
BLAST_1_WIND | Mountain View IV Wind | GEN | 2012-02-23 | 2012 | WIND | WIND |  | 49 | 49 | SCE | NQC | FC | 8.66 | 9.21 | 8.09 | 7.75 | 8.24 | 7.56 | 7.02 | 5.33 | 5.51 | 5.11 | 6.89 | 8.35
BLCKBT_2_STONEY | BLACK BUTTE HYDRO | GEN | 1988-01-01 | 1988 | WATER | HYDRO |  | 6.2 | 6.2 | PGAE | NQC | FC | 2.04 | 1.6 | 1.3 | 3.5 | 2.7 | 2.57 | 2.02 | 1.83 | 1.5 | 1.5 | 2.1 | 2.51
BLCKWL_6_SOLAR1 | Blackwell Solar | GEN | 2015-04-16 | 2015 | SUN | PHOTO VOLTAIC |  | 12 | 12 | PGAE | NQC | FC | 0.05 | 0.36 | 0.42 | 0.53 | 0.77 | 1.57 | 1.73 | 1.49 | 1.33 | 0.89 | 0.68 | 0.42
BLKCRK_2_GMBT1A | Genesis McCoy Bess | GEN | 0 |  | LESR | OTHER |  | 115 | 115 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLKCRK_2_GMBT1B | Genesis McCoy Bess | GEN | 0 |  | LESR | OTHER |  | 115 | 115 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLKCRK_2_GMCBT1 | Genesis McCoy Bess | GEN | 2021-06-30 | 2021 | LESR | OTHER |  | 230 | 230 | SCE | NQC | FC | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
BLKCRK_2_SOLAR1 | McCoy Station | GEN | 2016-06-14 | 2016 | SUN | PHOTO VOLTAIC |  | 250 | 0 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLKCRK_2_SOLR1A | BLKCRK_2_SOLR1A | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 125 | 125 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLKCRK_2_SOLR1B | BLKCRK_2_SOLR1B | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 125 | 125 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLKDIA_2_BDEBT1 | Black Diamond Energy Storage | GEN | 2022-03-17 | 2022 | LESR | OTHER |  | 200 | 200 | PGAE | NQC | FC | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
BLM E_2_UNIT 7 | COSO ENERGY DEVELOPERS - BLM EAST UNIT 7 | GEN | 0 |  | 0 | 0 |  | 24 | 24 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLM E_2_UNIT 8 | COSO ENERGY DEVELOPERS - BLM EAST UNIT 8 | GEN | 0 |  | 0 | 0 |  | 24 | 24 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLM W_2_COSBT1 | Coso Battery Storage | GEN | 2022-02-28 | 2022 | LESR | OTHER |  | 60 | 60 | SCE | NQC | FC | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
BLM W_2_UNIT 9 | COSO ENERGY DEVELOPERS - BLM WEST UNIT 9 | GEN | 0 |  | 0 | 0 |  | 24 | 24 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLM_2_UNITS | BLM EAST Facility | GEN | 1988-12-05 | 1988 | GEOTHERMAL | STEAM |  | 72 | 0 | SCE | NQC | PD | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
BLVRDE_6_BLVBT1 | Boulevard Energy Storage | GEN | 0 |  | LESR | OTHER |  | 9.75 | 9.75 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLYTHE_1_SOLAR1 | Blythe Solar 1 Project | GEN | 2009-12-18 | 2009 | SUN | PHOTO VOLTAIC |  | 21 | 21 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLYTHE_1_SOLAR2 | Blythe Green 1 | GEN | 2017-04-05 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BNNIEN_7_ALTAPH | ALTA POWER HOUSE | GEN | 1902-01-01 | 1902 | WATER | HYDRO |  | 1 | 2 | PGAE | NQC | FC | 0.34 | 0.3 | 0.3 | 0.4 | 0.2 | 0.39 | 0.4 | 0.61 | 0.42 | 0.53 | 0.41 | 0.3
BOGUE_1_UNITA1 | Feather River Energy Center, Unit #1 | GEN | 2002-12-23 | 2002 | NATURAL GAS | COMBUSTION TURBINE |  | 48.69 | 49.9 | PGAE | NQC | FC | 47.38 | 47.38 | 47.38 | 47.38 | 47.38 | 47.38 | 47.38 | 47.38 | 47.38 | 47.38 | 47.38 | 47.38
BORDER_6_UNITA1 | CalPeak Power Border Unit 1 | GEN | 2001-10-26 | 2001 | NATURAL GAS | COMBUSTION TURBINE |  | 51.25 | 52 | SDGE | NQC | FC | 51.25 | 51.25 | 51.25 | 51.25 | 51.25 | 51.25 | 51.25 | 51.25 | 51.25 | 51.25 | 51.25 | 51.25
BOWMN_6_HYDRO | NID Hydro Bowman Powerhouse | GEN | 2016-12-20 | 2016 | WATER | HYDRO |  | 3.6 | 3.6 | PGAE | NQC | FC | 0.15 | 0.06 | 0.07 | 0.21 | 1.6 | 1.23 | 2.18 | 2 | 1.5 | 1.03 | 0.24 | 0.18
BRDGVL_7_BAKER | Baker Station Hydro | GEN | 1987-12-10 | 1987 | WATER | HYDRO |  | 1.49 | 2.5 | PGAE | NQC | FC | 0.47 | 0.45 | 0.37 | 0.28 | 0.13 | 0.01 | 0 | 0 | 0 | 0.01 | 0.06 | 0.46
BRDSLD_2_HIWIND | High Winds Energy Center | GEN | 2003-12-23 | 2003 | WIND | WIND |  | 162 | 162 | PGAE | NQC | FC | 53.2 | 57.07 | 50.9 | 53.78 | 55.64 | 41.04 | 36.5 | 34.28 | 35.2 | 29.49 | 37.26 | 47.63
BRDSLD_2_MTZUM2 | NextEra Energy Montezuma Wind II | GEN | 2012-02-01 | 2012 | WIND | WIND |  | 78.2 | 78.2 | PGAE | NQC | FC | 25.68 | 27.55 | 24.57 | 25.96 | 26.86 | 19.81 | 17.62 | 16.55 | 16.99 | 14.24 | 17.99 | 22.99
BRDSLD_2_MTZUMA | FPL Energy Montezuma Wind | GEN | 2011-01-25 | 2011 | WIND | WIND |  | 36.8 | 38 | PGAE | NQC | FC | 12.08 | 12.97 | 11.56 | 12.22 | 12.64 | 9.32 | 8.29 | 7.79 | 8 | 6.7 | 8.46 | 10.82
BRDSLD_2_SHILO1 | Shiloh I Wind Project | GEN | 2006-03-30 | 2006 | WIND | WIND |  | 150 | 150 | PGAE | NQC | FC | 49.26 | 52.85 | 47.13 | 49.79 | 51.51 | 38 | 33.8 | 31.74 | 32.59 | 27.31 | 34.5 | 44.1
BRDSLD_2_SHILO2 | SHILOH WIND PROJECT 2 | GEN | 2009-01-27 | 2009 | WIND | WIND |  | 150 | 150 | PGAE | NQC | FC | 49.26 | 52.85 | 47.13 | 49.79 | 51.51 | 38 | 33.8 | 31.74 | 32.59 | 27.31 | 34.5 | 44.1
BRDSLD_2_SHLO3A | Shiloh III Wind Project, LLC | GEN | 2011-12-22 | 2011 | WIND | WIND |  | 102.5 | 100 | PGAE | NQC | FC | 33.66 | 36.11 | 32.21 | 34.03 | 35.2 | 25.97 | 23.09 | 21.69 | 22.27 | 18.66 | 23.58 | 30.14
BRDSLD_2_SHLO3B | Shiloh IV Wind Project | GEN | 2012-12-07 | 2012 | WIND | WIND |  | 100 | 100 | PGAE | NQC | FC | 32.84 | 35.23 | 31.42 | 33.2 | 34.34 | 25.33 | 22.53 | 21.16 | 21.73 | 18.21 | 23 | 29.4
BREGGO_6_DEGRSL | Desert Green Solar Farm | GEN | 2013-02-13 | 2013 | SUN | PHOTO VOLTAIC |  | 6.3 | 6.5 | SDGE | NQC | FC | 0.03 | 0.19 | 0.22 | 0.28 | 0.4 | 0.83 | 0.91 | 0.78 | 0.7 | 0.47 | 0.36 | 0.22
BREGGO_6_SOLAR | NRG Borrego Solar One | GEN | 2013-02-12 | 2013 | SUN | PHOTO VOLTAIC |  | 26 | 26 | SDGE | NQC | FC | 0.1 | 0.78 | 0.91 | 1.14 | 1.66 | 3.41 | 3.74 | 3.22 | 2.89 | 1.92 | 1.48 | 0.91
BRODIE_2_WIND | Coram Brodie Wind Project | GEN | 2012-03-29 | 2012 | WIND | WIND |  | 102 | 0 | SCE | NQC | FC | 18.02 | 19.17 | 16.84 | 16.14 | 17.16 | 15.73 | 14.61 | 11.1 | 11.47 | 10.64 | 14.34 | 17.37
BRODIE_2_WIND1 | Coram Brodie Wind Project Cameron Ridge | GEN | 0 |  | WIND | WIND |  | 78 | 78 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BRODIE_2_WIND2 | Coram Brodie Wind Project Section 15 | GEN | 0 |  | WIND | WIND |  | 24 | 24 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BUCKBL_2_CTG11 | Blythe CTG 11 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 182 | 182 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BUCKBL_2_CTG12 | Blythe CTG 12 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 182 | 182 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BUCKBL_2_PL1X3 | Blythe Energy Center | GEN | 2010-07-31 | 2010 | NATURAL GAS | COMBINED CYCLE |  | 493.63 | 0 | SCE | NQC | FC | 493.63 | 493.63 | 493.63 | 493.63 | 493.63 | 493.63 | 493.63 | 493.63 | 493.63 | 493.63 | 493.63 | 493.63
BUCKBL_2_STG10 | Blythe STG | GEN | 0 |  | NATURAL GAS | STEAM |  | 227 | 227 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BUCKCK_2_HYDRO | Lassen Station Hydro | GEN | 2016-06-13 | 2016 | WATER | HYDRO |  | 0.99 | 1 | PGAE | NQC | FC | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.08 | 0.08 | 0 | 0.02 | 0.13 | 0.13
BUCKCK_7_OAKFLT | Oak Flat | GEN | 1985-01-01 | 1985 | WATER | HYDRO |  | 1.3 | 1.3 | PGAE | NQC | FC | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.2 | 0.21 | 0.2 | 0.22
BUCKCK_7_PL1X2 | BUCKS CREEK AGGREGATE | GEN | 1928-01-01 | 1928 | WATER | HYDRO |  | 57.25 | 0 | PGAE | NQC | FC | 24.86 | 24.86 | 24.86 | 24.86 | 24.86 | 24.86 | 24.86 | 24.86 | 24.86 | 24.86 | 24.86 | 24.86
BUCKCK_7_UNIT 1 | Bucks Creek Unit #1 | GEN | 0 |  | WATER | HYDRO |  | 33 | 33 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BUCKCK_7_UNIT 2 | Bucks Creek Unit #2 | GEN | 0 |  | WATER | HYDRO |  | 32.5 | 32.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BUCKWD_1_NPALM1 | North Palm Springs 1A | GEN | 2012-04-02 | 2012 | SUN | PHOTO VOLTAIC |  | 2.4 | 2.4 | SCE | NQC | FC | 0.01 | 0.07 | 0.08 | 0.11 | 0.15 | 0.31 | 0.35 | 0.3 | 0.27 | 0.18 | 0.14 | 0.08
BUCKWD_1_QF | Buckwind Re-powering project | GEN | 1984-12-13 | 1984 | WIND | WIND |  | 16.5 | 16.5 | SCE | NQC | FC | 2.92 | 3.1 | 2.72 | 2.61 | 2.78 | 2.54 | 2.36 | 1.8 | 1.86 | 1.72 | 2.32 | 2.81
BUCKWD_7_WINTCV | Wintec Energy, Ltd. | GEN | 2003-12-30 | 2003 | WIND | WIND |  | 1.32 | 1.3 | SCE | NQC | FC | 0.23 | 0.25 | 0.22 | 0.21 | 0.22 | 0.2 | 0.19 | 0.14 | 0.15 | 0.14 | 0.19 | 0.22
BUENVS_2_NSPIN | BUENVS_2_NSPIN | GEN | 0 |  | WATER | PUMP |  | 104.4 | 104.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BURNYF_2_UNIT 1 | Burney Forest Power | GEN | 2018-08-17 | 2018 | BIOMASS | STEAM |  | 29 | 35.7 | PGAE | NQC | FC | 28.71 | 29 | 28.68 | 29 | 29 | 28.85 | 29 | 29 | 29 | 28.56 | 28.88 | 29
BUTTVL_7_UNIT 1 | BUTT VALLEY HYDRO | GEN | 1958-01-01 | 1958 | WATER | HYDRO |  | 39.5 | 41 | PGAE | NQC | FC | 38.8 | 31.6 | 31.6 | 31.2 | 32.4 | 32.4 | 39.2 | 39.2 | 39.5 | 32.4 | 32.4 | 38.8
CABALO_2_M2BSR1 | Mustang 2 Barbaro Solar | GEN | 2020-11-18 | 2020 | SUN | PHOTO VOLTAIC |  | 50 | 50 | PGAE | NQC | ID | 0.2 | 1.5 | 1.75 | 2.2 | 3.2 | 6.55 | 7.2 | 6.2 | 5.55 | 3.7 | 2.85 | 1.75
CABALO_2_M2WSR2 | Mustang 2 Whirlaway Solar | GEN | 2020-11-11 | 2020 | SUN | PHOTO VOLTAIC |  | 100 | 100 | PGAE | NQC | ID | 0.4 | 3 | 3.5 | 4.4 | 6.4 | 13.1 | 14.4 | 12.4 | 11.1 | 7.4 | 5.7 | 3.5
CABZON_1_WINDA1 | Cabazon Wind Project | GEN | 2002-08-31 | 2002 | WIND | WIND |  | 41 | 41 | SCE | NQC | FC | 7.24 | 7.71 | 6.77 | 6.49 | 6.9 | 6.32 | 5.87 | 4.46 | 4.61 | 4.28 | 5.76 | 6.98
CALFTN_2_CFSBT1 | California Flats Solar Battery | GEN | 2021-08-31 | 2021 | LESR | OTHER |  | 60 | 60 | PGAE | NQC | FC | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
CALFTN_2_SOLAR | California Flats North | GEN | 2017-11-29 | 2017 | SUN | PHOTO VOLTAIC |  | 130 | 130 | PGAE | NQC | ID | 0.25 | 2.22 | 2.54 | 3.5 | 5.37 | 11.17 | 12.29 | 10.3 | 8.76 | 5.3 | 3.6 | 1.63
CALFTS_2_CFSSR1 | California Flats Solar South | GEN | 2019-03-05 | 2019 | SUN | PHOTO VOLTAIC |  | 150 | 150 | PGAE | NQC | FC | 0.6 | 4.5 | 5.25 | 6.6 | 9.6 | 19.65 | 21.6 | 18.6 | 16.65 | 11.1 | 8.55 | 5.25
CALGEN_1_UNIT 1 | CALGEN_1_UNIT 1 | GEN | 0 |  | 0 | 0 |  | 32.2 | 32.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CALGEN_1_UNIT 2 | CALGEN_1_UNIT 2 | GEN | 0 |  | 0 | 0 |  | 32.2 | 32.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CALGEN_1_UNIT 3 | CALGEN_1_UNIT 3 | GEN | 0 |  | 0 | 0 |  | 32.2 | 32.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CALGEN_1_UNITS | Coso Navy 1 | GEN | 1987-07-13 | 1987 | GEOTHERMAL | STEAM |  | 80 | 0 | SCE | NQC | FC | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
CALPIN_1_AGNEW | Agnews Power Plant | GEN | 1990-10-19 | 1990 | NATURAL GAS | COMBUSTION TURBINE |  | 28.56 | 41.5 | PGAE | NQC | FC | 28.56 | 28.56 | 28.56 | 28.56 | 28.56 | 28.56 | 28.56 | 28.56 | 28.56 | 28.56 | 28.56 | 28.56
CALPSS_6_SOLAR1 | Calipatria Solar Farm | TG | 2016-02-12 | 2016 | SUN | PHOTO VOLTAIC |  | 19.9 | 20 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAMCHE_1_PL1X3 | CAMANCHE UNITS 1, 2 & 3 AGGREGATE | GEN | 1983-01-01 | 1983 | WATER | HYDRO |  | 9.99 | 0 | PGAE | NQC | FC | 1.62 | 1.67 | 1.74 | 1.99 | 2.31 | 0.99 | 0.83 | 0.88 | 0.48 | 0.52 | 0.95 | 1.4
CAMCHE_1_UNIT 1 | Camanche 1 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAMCHE_1_UNIT 2 | Camanche 2 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAMCHE_1_UNIT 3 | Camanche 3 | GEN | 0 |  | WATER | HYDRO |  | 3.7 | 3.7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAMDEN_6_RDDBM1 | RuAnn Dairy Digester BioMAT | GEN | 0 |  | BIOMASS | RECIPROCATING ENGINE |  | 0.55 | 0.55 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAMERN_6_BSPSR1 | Buckman Springs PV | GEN | 2024-01-29 | 2024 | SUN | PHOTO VOLTAIC |  | 0.84 | 0.85 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAMLOT_2_SOLAR1 | Camelot | GEN | 2014-12-11 | 2014 | SUN | PHOTO VOLTAIC |  | 45 | 45 | SCE | NQC | FC | 0.18 | 1.35 | 1.58 | 1.98 | 2.88 | 5.9 | 6.48 | 5.58 | 5 | 3.33 | 2.57 | 1.58
CAMLOT_2_SOLAR2 | Columbia Two | GEN | 2014-12-10 | 2014 | SUN | PHOTO VOLTAIC |  | 15 | 15 | SCE | NQC | FC | 0.06 | 0.45 | 0.53 | 0.66 | 0.96 | 1.97 | 2.16 | 1.86 | 1.67 | 1.11 | 0.86 | 0.53
CAMPFW_7_FARWST | CAMP FAR WEST HYDRO | GEN | 1985-01-01 | 1985 | WATER | HYDRO |  | 6.8 | 7.9 | PGAE | NQC | FC | 0 | 2.08 | 5.6 | 5.44 | 2.64 | 2.48 | 3.36 | 2.94 | 0 | 0 | 0 | 0
CANTUA_1_SOLAR | Cantua Solar Station | GEN | 2012-07-25 | 2012 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
CAPWD_1_QF | Edom Hills Wind Farm | GEN | 2015-10-19 | 2015 | WIND | WIND |  | 19.55 | 20 | SCE | NQC | FC | 3.45 | 3.67 | 3.23 | 3.09 | 3.29 | 3.01 | 2.8 | 2.13 | 2.2 | 2.04 | 2.75 | 3.33
CARBOU_7_PL2X3 | CARIBOU PH 1 UNIT 2 & 3 AGGREGATE | GEN | 1921-01-01 | 1921 | WATER | HYDRO |  | 49 | 0 | PGAE | NQC | FC | 19.2 | 1.6 | 0 | 0 | 0 | 0 | 28.8 | 35.36 | 20.8 | 12 | 0 | 7.2
CARBOU_7_PL4X5 | CARIBOU PH 2 UNIT 4 & 5 AGGREGATE | GEN | 1958-01-01 | 1958 | WATER | HYDRO |  | 120 | 0 | PGAE | NQC | FC | 42.34 | 36.4 | 32 | 16.8 | 18.98 | 67.6 | 101.18 | 103.18 | 103.2 | 72 | 25.22 | 24.84
CARBOU_7_UNIT 1 | CARIBOU PH 1 UNIT 1 | GEN | 1921-01-01 | 1921 | WATER | HYDRO |  | 24 | 24 | PGAE | NQC | FC | 4 | 1.6 | 0 | 0 | 0 | 0 | 9.12 | 19.2 | 18.4 | 0 | 0 | 0
CARBOU_7_UNIT 2 | CARIBOU PH 1 UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 25 | 25 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CARBOU_7_UNIT 3 | CARIBOU PH 1 UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 25 | 25 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CARBOU_7_UNIT 4 | Caribou PH 2 Unit 4 | GEN | 0 |  | WATER | HYDRO |  | 61 | 61 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CARBOU_7_UNIT 5 | Caribou PH 2 Unit 5 | GEN | 0 |  | WATER | HYDRO |  | 61 | 61 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CARLS1_2_CARCT1 | Carlsbad 1 | GEN | 2018-11-19 | 2018 | NATURAL GAS | COMBUSTION TURBINE |  | 422 | 0 | SDGE | NQC | FC | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422
CARLS1_2_CTG6 | CARLS1_2_CTG6 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 105.5 | 105.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CARLS1_2_CTG7 | CARLS1_2_CTG7 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 105.5 | 105.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CARLS1_2_CTG8 | CARLS1_2_CTG8 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 105.5 | 105.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CARLS1_2_CTG9 | CARLS1_2_CTG9 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 105.5 | 105.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CARLS2_1_CARCT1 | Carlsbad 2 | GEN | 2018-11-20 | 2018 | NATURAL GAS | COMBUSTION TURBINE |  | 105.5 | 105.5 | SDGE | NQC | FC | 105.5 | 105.5 | 105.5 | 105.5 | 105.5 | 105.5 | 105.5 | 105.5 | 105.5 | 105.5 | 105.5 | 105.5
CASADB_1_CD4GT1 | Casa Diablo 4 | GEN | 2022-12-28 | 2022 | GEOTHERMAL | STEAM |  | 40.7 | 40.7 | SCE | NQC | FC | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
CASCES_6_CESBT1 | Cascade Energy Storage | GEN | 2023-12-14 | 2023 | LESR | OTHER |  | 25 | 25 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CATLNA_2_SOLAR | Catalina Solar - Phases 1 and 2 | GEN | 2013-02-15 | 2013 | SUN | PHOTO VOLTAIC |  | 110 | 110 | SCE | NQC | FC | 0.44 | 3.3 | 3.85 | 4.84 | 7.04 | 14.41 | 15.84 | 13.64 | 12.21 | 8.14 | 6.27 | 3.85
CATLNA_2_SOLAR2 | Catalina Solar 2 | GEN | 2015-07-22 | 2015 | SUN | PHOTO VOLTAIC |  | 18 | 18 | SCE | NQC | FC | 0.07 | 0.54 | 0.63 | 0.79 | 1.15 | 2.36 | 2.59 | 2.23 | 2 | 1.33 | 1.03 | 0.63
CAVLSR_2_BSOLAR | California Valley Solar Ranch-Phase B | GEN | 2013-01-01 | 2013 | SUN | PHOTO VOLTAIC |  | 40 | 40 | PGAE | NQC | FC | 0.16 | 1.2 | 1.4 | 1.76 | 2.56 | 5.24 | 5.76 | 4.96 | 4.44 | 2.96 | 2.28 | 1.4
CAVLSR_2_RSOLAR | California Valley Solar Ranch-Phase A | GEN | 2013-11-01 | 2013 | SUN | PHOTO VOLTAIC |  | 210 | 210 | PGAE | NQC | FC | 0.84 | 6.3 | 7.35 | 9.24 | 13.44 | 27.51 | 30.24 | 26.04 | 23.31 | 15.54 | 11.97 | 7.35
CAYTNO_2_VASCO | Vasco Road | GEN | 2014-02-05 | 2014 | BIOGAS | RECIPROCATING ENGINE |  | 4.3 | 4.3 | PGAE | NQC | FC | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
CDWR07_2_GEN | CDWR07_2_GEN | GEN | 0 |  | WATER | PUMP |  | 415.3 | 0 | PGAE | NQC | FC | 115.6 | 115.6 | 115.6 | 115.6 | 115.6 | 115.6 | 115.6 | 115.6 | 115.6 | 115.6 | 115.6 | 115.6
CEDRCK_6_UNIT | Water Wheel Ranch | GEN | 1984-03-22 | 1984 | WATER | HYDRO |  | 0.98 | 1 | PGAE | NQC | FC | 0.29 | 0.33 | 0.32 | 0.52 | 0.45 | 0.19 | 0.07 | 0.06 | 0.05 | 0.08 | 0.12 | 0.17
CEDUCR_2_SOLAR1 | Ducor Solar 1 | GEN | 2016-12-23 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CEDUCR_2_SOLAR2 | Ducor Solar 2 | GEN | 2016-12-23 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CEDUCR_2_SOLAR3 | Ducor Solar 3 | GEN | 2016-12-23 | 2016 | SUN | PHOTO VOLTAIC |  | 15 | 15 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CEDUCR_2_SOLAR4 | Ducor Solar 4 | GEN | 2016-12-23 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENT40_1_C40SR1 | CENTRAL 40 | GEN | 2021-02-23 | 2021 | SUN | PHOTO VOLTAIC |  | 40 | 40 | PGAE | NQC | FC | 0.16 | 1.2 | 1.4 | 1.76 | 2.56 | 5.24 | 5.76 | 4.96 | 4.44 | 2.96 | 2.28 | 1.4
CENTER_2_RHONDO | MWD Rio Hondo Hydroelectric Recovery Pla | GEN | 1984-01-01 | 1984 | WATER | HYDRO |  | 1.91 | 1.9 | SCE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTER_2_SOLAR1 | Pico Rivera | GEN | 2015-11-20 | 2015 | SUN | PHOTO VOLTAIC |  | 0.9 | 1 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTER_2_TECNG1 | TECHNICAST | GEN | 2018-05-01 | 2018 | NATURAL GAS | RECIPROCATING ENGINE |  | 0.99 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTER_6_PEAKER | Center Peaker | GEN | 2007-09-20 | 2007 | NATURAL GAS | COMBUSTION TURBINE |  | 47.3 | 59 | SCE | NQC | FC | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3
CENTPD_2_BMSBT1 | Blythe Mesa Solar 2 BESS | GEN | 0 |  | LESR | OTHER |  | 56 | 56 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTPD_2_BMSBT2 | Blythe Mesa Solar 2 BESS | GEN | 0 |  | LESR | OTHER |  | 56 | 56 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTPD_2_BMSSR1 | Blythe Mesa Solar | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 111.8 | 111.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTPD_2_BMSSR2 | Blythe Mesa Solar | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 111.8 | 111.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTPD_2_BMSSX2 | Blythe Mesa Solar | GEN | 2022-12-21 | 2022 | SUN | PHOTO VOLTAIC |  | 223.6 | 223.6 | SCE | NQC | FC | 0.53 | 4.69 | 5.63 | 7.54 | 11.26 | 23.15 | 25.23 | 21.36 | 18.5 | 11.71 | 8.2 | 3.97
CENTPD_2_BMSX2 | Blythe Mesa Solar 2 BESS | GEN | 2022-12-21 | 2022 | LESR | OTHER |  | 112 | 112 | SCE | NQC | FC | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
CENTRY_6_GEN 1 | CENTURY GEN 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 10.8 | 10.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTRY_6_GEN 2 | CENTURY GEN 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 10.8 | 10.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTRY_6_GEN 3 | CENTURY GEN 3 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 10.8 | 10.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTRY_6_GEN 4 | CENTURY GEN 4 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 10.8 | 10.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CENTRY_6_PL1X4 | CENTURY GENERATING PLANT (AGGREGATE) | GEN | 2001-09-17 | 2001 | NATURAL GAS | FTUR |  | 41.4 | 0 | SCE | NQC | FC | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
CHALK_1_UNIT | CHALK CLIFF LIMITED | GEN | 1990-03-20 | 1990 | NATURAL GAS | COMBUSTION TURBINE |  | 48.67 | 55.1 | PGAE | NQC | FC | 48.67 | 48.67 | 48.67 | 48.67 | 48.67 | 48.67 | 48.67 | 48.67 | 48.67 | 48.67 | 48.67 | 48.67
CHARMN_2_PGONG1 | PROCTER AND GAMBLE OXNARD I | GEN | 2020-08-01 | 2020 | NATURAL GAS | FTUR |  | 19.87 | 19.9 | SCE | NQC | FC | 19.17 | 18.8 | 17.87 | 18.55 | 18.27 | 18.02 | 18.39 | 19.61 | 18.64 | 18.9 | 15.88 | 18.73
CHESTN_2_CHWBT1 | Chestnut Westside BESS | GEN | 0 |  | LESR | OTHER |  | 67.5 | 67.5 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHESTN_2_CHWBT2 | Chestnut Westside BESS | GEN | 0 |  | LESR | OTHER |  | 67.5 | 67.5 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHESTN_2_CHWBX2 | Chestnut Westside BESS | GEN | 2023-12-14 | 2023 | LESR | OTHER |  | 135 | 0 | PGAE | NQC | ID | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
CHESTN_2_CHWSR1 | Chestnut Westside PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 75 | 75 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHESTN_2_CHWSR2 | Chestnut Westside PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 75 | 75 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHESTN_2_CHWSX2 | Chestnut Westside PV | GEN | 2023-12-14 | 2023 | SUN | PHOTO VOLTAIC |  | 150 | 0 | PGAE | NQC | ID | 0.16 | 2.06 | 2.6 | 3.84 | 5.92 | 12.24 | 13.2 | 10.92 | 9.02 | 5.28 | 3.08 | 0.6
CHEVCD_6_UNIT | CHEVRON USA (TAFT/CADET) | GEN | 1982-07-26 | 1982 | NATURAL GAS | COMBUSTION TURBINE |  | 11.5 | 11.5 | PGAE | NQC | FC | 1.05 | 1.72 | 1.6 | 1.42 | 1.32 | 1.73 | 1.51 | 1.59 | 1.63 | 1.53 | 1.77 | 1.46
CHEVCO_6_UNIT 1 | CHEVRON USA (COALINGA) | GEN | 1986-01-17 | 1986 | NATURAL GAS | COMBUSTION TURBINE |  | 16.5 | 19 | PGAE | NQC | FC | 1.11 | 0.99 | 1.31 | 1.13 | 1.63 | 1.87 | 1.73 | 2.24 | 2.54 | 1.9 | 1.25 | 1.08
CHEVCO_6_UNIT 2 | AERA ENERGY LLC. (COALINGA) | GEN | 1988-06-03 | 1988 | NATURAL GAS | FTUR |  | 8.5 | 12.5 | PGAE | NQC | FC | 0.92 | 0.92 | 1.03 | 0.96 | 0.93 | 0.84 | 0.76 | 0.73 | 0.79 | 0.95 | 1.01 | 1.05
CHEVCY_1_UNIT | CHEVRON USA (CYMRIC) | GEN | 1982-10-15 | 1982 | NATURAL GAS | COMBUSTION TURBINE |  | 24.3 | 24.3 | PGAE | NQC | FC | 3.74 | 3.14 | 2.49 | 2.77 | 2.69 | 2.92 | 2.78 | 1.98 | 1.79 | 2 | 1.75 | 2.15
CHEVMN_2_UNITS | CHEVRON U.S.A. UNITS 1 & 2 AGGREGATE | GEN | 1987-12-29 | 1987 | OTHER | 0 |  | 124.87 | 170.7 | SCE | NQC | FC | 3.84 | 4.11 | 8.28 | 26.35 | 6.88 | 5.52 | 13.32 | 7.93 | 13.95 | 7.64 | 6.21 | 1.26
CHICPK_7_UNIT 1 | Chicago Park Powerhouse | GEN | 1965-01-01 | 1965 | WATER | HYDRO |  | 42 | 42 | PGAE | NQC | FC | 25.04 | 24.54 | 20.24 | 20 | 20.8 | 24 | 28.06 | 28.04 | 8.8 | 8 | 19.2 | 26.03
CHILLS_1_SYCENG | Sycamore Energy 1 | GEN | 2011-05-19 | 2011 | BIOGAS | COMBUSTION TURBINE |  | 1.5 | 1.9 | SDGE | NQC | FC | 0.78 | 0.77 | 0.87 | 0.92 | 0.88 | 0.83 | 0.98 | 1 | 0.99 | 0.95 | 0.93 | 0.95
CHILLS_7_UNITA1 | Sycamore Energy 2 | GEN | 2004-07-14 | 2004 | BIOGAS | 0 |  | 2.25 | 2.5 | SDGE | NQC | FC | 1.82 | 2 | 2 | 2 | 1.4 | 1.68 | 1.56 | 1.52 | 1.74 | 1.75 | 1.8 | 1.61
CHINO_2_APEBT1 | Pomona Energy Storage | GEN | 2016-12-31 | 2016 | LESR | OTHER |  | 20 | 20 | SCE | NQC | FC | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
CHINO_2_JURUPA | Jurupa | GEN | 2013-12-20 | 2013 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHINO_2_PESBT1 | Pomona Energy Storage 2 | GEN | 2023-07-08 | 2023 | LESR | OTHER |  | 20 | 20 | SCE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
CHINO_2_QF | CHINO QFS | GEN | 1987-01-01 | 1987 | OTHER | OTHER |  | 0.19 | 21.8 | SCE | NQC | FC | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHINO_2_SASOLR | SS San Antonio West LLC | GEN | 2013-12-20 | 2013 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHINO_2_SOLAR2 | Kona Solar - Terra Francesca | GEN | 2015-04-13 | 2015 | SUN | PHOTO VOLTAIC |  | 1.49 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHINO_6_CIMGEN | Chino Co-Generation | GEN | 2018-06-27 | 2018 | NATURAL GAS | COMBINED CYCLE |  | 26 | 31.6 | SCE | NQC | FC | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
CHWCHL_1_UNIT | CHOW 2 PEAKER PLANT | GEN | 2001-06-13 | 2001 | NATURAL GAS | RECIPROCATING ENGINE |  | 48.6 | 48.6 | PGAE | NQC | FC | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
CLINESCO_3_PVDYN | CLINES CORNERS | TG | 2021-12-01 | 2021 | WIND | WIND |  | 129.94 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLINESCO_3_WBDYN | CLINES CORNERS B | TG | 2021-12-01 | 2021 | WIND | WIND |  | 194.28 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLOVDL_1_SOLAR | Cloverdale Solar I | GEN | 2014-06-26 | 2014 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | FC | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
CLOVER_2_UNIT | Clover Creek | GEN | 2016-05-06 | 2016 | WATER | HYDRO |  | 0.99 | 1 | PGAE | NQC | FC | 0.47 | 0.47 | 0.38 | 0.55 | 0.45 | 0.26 | 0.1 | 0.04 | 0.01 | 0 | 0.14 | 0.33
CLRMNT_6_CLEBT1 | Clairemont Energy Storage | GEN | 0 |  | LESR | OTHER |  | 9 | 9 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLRMTK_1_QF | SMALL QF AGGREGATION - OAKLAND | GEN | 1983-12-05 | 1983 | NATURAL GAS | FTUR |  | 1.25 | 1.3 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CMBLND_2_DS2BT1 | Daggett 2 a BESS | GEN | 2023-11-22 | 2023 | LESR | OTHER |  | 52 | 52 | SCE | NQC | ID | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
CMBLND_2_DS2BT2 | Daggett 2 b BESS | GEN | 2023-11-22 | 2023 | LESR | OTHER |  | 33 | 33 | SCE | NQC | ID | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
CMBLND_2_DS2BT3 | Daggett 2 c BESS | GEN | 2023-12-01 | 2023 | LESR | OTHER |  | 46 | 46 | SCE | NQC | ID | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
CMBLND_2_DS2SR1 | Daggett 2 a PV | GEN | 2023-11-22 | 2023 | SUN | PHOTO VOLTAIC |  | 65 | 65 | SCE | NQC | ID | 0.09 | 1.01 | 1.25 | 1.79 | 2.74 | 5.66 | 6.12 | 5.1 | 4.28 | 2.57 | 1.59 | 0.48
CMBLND_2_DS2SR2 | Daggett 2 b PV | GEN | 2023-11-17 | 2023 | SUN | PHOTO VOLTAIC |  | 65 | 65 | SCE | NQC | ID | 0.15 | 1.35 | 1.63 | 2.18 | 3.26 | 6.7 | 7.31 | 6.18 | 5.35 | 3.39 | 2.37 | 1.14
CMBLND_2_DS2SR3 | Daggett 2 c PV | GEN | 2023-12-01 | 2023 | SUN | PHOTO VOLTAIC |  | 52 | 52 | SCE | NQC | ID |  | 0.73 | 0.92 | 1.34 | 2.08 | 4.29 | 4.63 | 3.83 | 3.18 | 1.86 | 1.1 | 0.23
CNTNLA_2_SOLAR1 | Centinela Solar Energy I | GEN | 2013-10-16 | 2013 | SUN | PHOTO VOLTAIC |  | 125 | 127 | SDGE | NQC | FC | 0.5 | 3.75 | 4.38 | 5.5 | 8 | 16.38 | 18 | 15.5 | 13.88 | 9.25 | 7.13 | 4.38
CNTNLA_2_SOLAR2 | Centinels Solar Energy 2 | GEN | 2014-08-15 | 2014 | SUN | PHOTO VOLTAIC |  | 45.6 | 47 | SDGE | NQC | FC | 0.18 | 1.37 | 1.6 | 2.01 | 2.92 | 5.97 | 6.57 | 5.65 | 5.06 | 3.37 | 2.6 | 1.6
COCOPP_2_CTG1 | Marsh Landing 1 | GEN | 2013-05-01 | 2013 | NATURAL GAS | FTUR |  | 204.2 | 222 | PGAE | NQC | FC | 203.08 | 202.82 | 202.21 | 199.04 | 197.87 | 194.63 | 193.62 | 193.09 | 194.72 | 198.97 | 200.43 | 203.72
COCOPP_2_CTG2 | Marsh Landing 2 | GEN | 2013-05-01 | 2013 | NATURAL GAS | FTUR |  | 202.7 | 222 | PGAE | NQC | FC | 202.25 | 201.68 | 201.36 | 198.21 | 197.04 | 193.81 | 192.86 | 192.32 | 193.95 | 198.13 | 199.65 | 202.7
COCOPP_2_CTG3 | Marsh Landing 3 | GEN | 2013-05-01 | 2013 | NATURAL GAS | FTUR |  | 208.96 | 222 | PGAE | NQC | FC | 201.79 | 201.31 | 200.92 | 197.81 | 196.72 | 193.1 | 192.03 | 191.57 | 193.18 | 197.81 | 199.11 | 202.45
COCOPP_2_CTG4 | Marsh Landing 4 | GEN | 2013-05-01 | 2013 | NATURAL GAS | FTUR |  | 204.29 | 222 | PGAE | NQC | FC | 203.72 | 203.2 | 202.81 | 199.67 | 198.47 | 194.44 | 193.36 | 192.89 | 194.53 | 199.67 | 200.98 | 204.2
COCOSB_6_SOLAR | Oakley Solar Project | GEN | 2013-06-12 | 2013 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COGNAT_1_UNIT | Stockton Biomas | GEN | 2014-02-12 | 2014 | BIOMASS | STEAM |  | 45 | 45 | PGAE | NQC | FC | 44.87 | 45 | 44.81 | 45 | 44.73 | 45 | 45 | 45 | 45 | 44.87 | 45 | 44.94
COLEMN_2_UNIT | Coleman | GEN | 1979-01-01 | 1979 | WATER | HYDRO |  | 13 | 13 | PGAE | NQC | FC | 4.18 | 5.05 | 5.07 | 4.79 | 4.92 | 2.89 | 2.14 | 0.28 | 1.11 | 1.3 | 1.7 | 3.27
COLGAT_7_UNIT 1 | Colgate Powerhouse Unit 1 | GEN | 1969-01-01 | 1969 | WATER | HYDRO |  | 176.72 | 176.7 | PGAE | NQC | FC | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
COLGAT_7_UNIT 2 | Colgate Powerhouse Unit 2 | GEN | 1969-01-01 | 1969 | WATER | HYDRO |  | 175.67 | 175.7 | PGAE | NQC | FC | 139.74 | 139.74 | 139.74 | 139.74 | 139.74 | 139.74 | 139.74 | 139.74 | 139.74 | 139.74 | 139.74 | 139.74
COLGNS_2_CNSSR1 | ColGreen North Shore | TG | 2018-12-31 | 2018 | SUN | PHOTO VOLTAIC |  | 74.8 | 74.8 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COLPIN_6_COLLNS | Collins Pine | GEN | 2021-11-19 | 2021 | BIOMASS | STEAM |  | 3.3 | 3.3 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COLTON_6_AGUAM1 | AGUA MANSA UNIT 1 (CITY OF COLTON) | GEN | 2003-06-27 | 2003 | NATURAL GAS | COMBUSTION TURBINE |  | 43 | 45.5 | SCE | NQC | FC | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
COLUSA_2_CTG1 | Colusa Generating Station | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 213.5 | 213.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COLUSA_2_CTG2 | Colusa Generating Station | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 213.5 | 213.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COLUSA_2_PL1X3 | Colusa Generating Station | GEN | 2010-12-22 | 2010 | NATURAL GAS | COMBINED CYCLE |  | 641 | 0 | PGAE | NQC | FC | 630 | 630 | 630 | 630 | 618 | 612 | 606 | 604 | 607 | 614 | 623 | 628
COLUSA_2_STG | Colusa Generating Station | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 411 | 411 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COLVIL_7_PL1X2 | COLLIERVILLE HYDRO UNIT 1 & 2 AGGREGATE | GEN | 0 |  | WATER | HYDRO |  | 246.86 | 0 | PGAE | NQC | FC | 246.86 | 246.86 | 246.86 | 246.86 | 246.86 | 246.86 | 246.86 | 246.86 | 246.86 | 246.86 | 246.86 | 246.86
COLVIL_7_UNIT 1 | COLLIERVILLE HYDRO UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 126.5 | 126.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COLVIL_7_UNIT 2 | COLLIERVILLE HYDRO UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 126 | 126 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CONDOR_2_CDRBT1 | Condor BESS | GEN | 0 |  | LESR | OTHER |  | 200 | 200 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CONTRL_1_CASAD1 | Mammoth G1 | GEN | 1984-11-26 | 1984 | GEOTHERMAL | OTHER |  | 7.2 | 10 | SCE | NQC | FC | 6.97 | 7.2 | 6.97 | 6.85 | 6.73 | 5.74 | 5.1 | 5.35 | 5.53 | 5.64 | 6.99 | 6.64
CONTRL_1_CASAD2 | Mammoth G2 | GEN | 2020-12-08 | 2020 | GEOTHERMAL | OTHER |  | 10.5 | 12 | SCE | NQC | FC | 10.11 | 9.97 | 9.45 | 8.35 | 8.63 | 8.23 | 9.41 | 9.28 | 9.17 | 9.16 | 9.99 | 10.2
CONTRL_1_CASAD3 | Mammoth G3 | GEN | 2013-04-01 | 2013 | GEOTHERMAL | OTHER |  | 14 | 14 | SCE | NQC | FC | 12.35 | 12.89 | 13.08 | 12.43 | 11.48 | 9.69 | 8.75 | 9.02 | 9.88 | 10.72 | 12.99 | 13.07
CONTRL_1_LUNDY | LUNDY | GEN | 1911-01-01 | 1911 | WATER | HYDRO |  | 3 | 3 | SCE | NQC | FC | 0.33 | 0.32 | 0.35 | 0.37 | 1.06 | 1.54 | 1.1 | 0.39 | 0.28 | 0.16 | 0.41 | 0.32
CONTRL_1_OXBOW | Dixie Valley Geo | GEN | 2018-07-05 | 2018 | GEOTHERMAL | STEAM |  | 60 | 64.7 | SCE | NQC | FC | 59.46 | 57.37 | 57.75 | 43.02 | 46.29 | 55.03 | 54.04 | 53.91 | 54.61 | 46.22 | 59.38 | 58.79
CONTRL_1_POOLE | POOLE HYDRO PLANT 1 | GEN | 1924-01-01 | 1924 | WATER | HYDRO |  | 11.07 | 11.3 | SCE | NQC | FC | 0.96 | 0.8 | 0.48 | 0.76 | 1.6 | 8.27 | 5.42 | 1.46 | 10.9 | 0.31 | 0.48 | 0.8
CONTRL_1_QF | CONTROL QFS | GEN | 1982-01-01 | 1982 | OTHER | OTHER |  | 2.55 | 41.9 | SCE | NQC | FC | 0.56 | 0.6 | 0.59 | 0.84 | 0.57 | 0.67 | 0.64 | 0.59 | 0.66 | 0.53 | 0.56 | 0.53
CONTRL_1_RUSHCK | RUSH CREEK | GEN | 1916-01-01 | 1916 | WATER | HYDRO |  | 11.94 | 13 | SCE | NQC | FC | 0.8 | 0.82 | 4.82 | 0.82 | 0.8 | 9.45 | 9.46 | 1.82 | 11.94 | 1.01 | 0.97 | 0.8
COPMT2_2_SOLAR2 | CMS2 | GEN | 2012-06-27 | 2012 | SUN | PHOTO VOLTAIC |  | 155 | 155 | SCE | NQC | FC | 0.62 | 4.65 | 5.43 | 6.82 | 9.92 | 20.31 | 22.32 | 19.22 | 17.21 | 11.47 | 8.84 | 5.43
COPMT4_2_SOLAR4 | Copper Mountain Solar 4 | GEN | 2016-12-02 | 2016 | SUN | PHOTO VOLTAIC |  | 92 | 92 | SCE | NQC | FC | 0.37 | 2.76 | 3.22 | 4.05 | 5.89 | 12.05 | 13.25 | 11.41 | 10.21 | 6.81 | 5.24 | 3.22
COPMTN_2_CM10 | Copper Mountain 10 | GEN | 2011-10-03 | 2011 | SUN | PHOTO VOLTAIC |  | 10 | 10 | SCE | NQC | PD | 0.04 | 0.3 | 0.35 | 0.44 | 0.64 | 1.31 | 1.44 | 1.24 | 1.11 | 0.74 | 0.57 | 0.35
COPMTN_2_SOLAR1 | Copper Mountain 48 | GEN | 2010-06-15 | 2010 | SUN | PHOTO VOLTAIC |  | 48 | 48 | SCE | NQC | PD | 0.19 | 1.44 | 1.68 | 2.11 | 3.07 | 6.29 | 6.91 | 5.95 | 5.33 | 3.55 | 2.74 | 1.68
CORCAN_1_SOLAR1 | CID Solar | GEN | 2015-01-09 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
CORCAN_1_SOLAR2 | Corcoran City | GEN | 2015-05-23 | 2015 | SUN | PHOTO VOLTAIC |  | 11 | 12 | PGAE | NQC | FC | 0.04 | 0.33 | 0.39 | 0.48 | 0.7 | 1.44 | 1.58 | 1.36 | 1.22 | 0.81 | 0.63 | 0.39
CORONS_2_SOLAR | Master Development Corona | GEN | 2013-04-24 | 2013 | SUN | PHOTO VOLTAIC |  | 0.99 | 1 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CORONS_6_CLRCTG | CORONS_6_CLRCTG | GEN | 0 |  | 0 | 0 |  | 23.8 | 23.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CORONS_6_CLRSTG | CORONS_6_CLRSTG | GEN | 0 |  | 0 | 0 |  | 8.5 | 8.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CORONS_6_CLRWTR | Clearwater Power Plant | GEN | 2005-02-28 | 2005 | NATURAL GAS | COMBINED CYCLE |  | 28 | 0 | SCE | NQC | FC | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
CORRAL_6_SJOAQN | Ameresco San Joaquin | GEN | 2014-04-24 | 2014 | BIOGAS | RECIPROCATING ENGINE |  | 4.3 | 4.3 | PGAE | NQC | FC | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
COTTLE_2_FRNKNH | Frankenheimer Power Plant | GEN | 2013-04-01 | 2013 | WATER | HYDRO |  | 5.3 | 5 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0.61 | 0 | 0 | 0
COVERD_2_HCKHY1 | HATCHET CREEK | GEN | 2017-06-01 | 2017 | WATER | HYDRO |  | 6.89 | 7 | PGAE | NQC | FC | 1.77 | 1.66 | 1.39 | 2.53 | 1.57 | 0.24 | 0 | 0 | 0 | 0.14 | 0.09 | 0.41
COVERD_2_MCKHY1 | Montgomery Creek Hydro | GEN | 2017-08-01 | 2017 | WATER | HYDRO |  | 2.8 | 2.8 | PGAE | NQC | FC | 1.15 | 0.81 | 0.85 | 0.98 | 0.54 | 0.09 | 0 | 0 | 0 | 0.08 | 0 | 0.62
COVERD_2_QFUNTS | Cove Hydroelectric Project | GEN | 1987-01-05 | 1987 | WATER | HYDRO |  | 5.5 | 20.3 | PGAE | NQC | FC | 0.78 | 1.58 | 1.66 | 3.3 | 3.3 | 0.8 | 0.22 | 0 | 0 | 0 | 0 | 0.24
COVERD_2_RCKHY1 | ROARING CREEK | GEN | 2017-06-01 | 2017 | WATER | HYDRO |  | 2 | 2 | PGAE | NQC | FC | 1.01 | 1.07 | 0.22 | 0.49 | 0.18 | 0.15 | 0.01 | 0 | 0 | 0.04 | 0.09 | 0.27
COWCRK_2_UNIT | Cow Creek Hydro | GEN | 1907-01-01 | 1907 | WATER | HYDRO |  | 2 | 2 | PGAE | NQC | FC | 0.69 | 0.93 | 0.75 | 0.87 | 0.58 | 0.41 | 0.19 | 0.1 | 0.09 | 0.17 | 0.55 | 0.82
CPVERD_2_SOLAR | Campo Verde Solar | GEN | 2013-10-22 | 2013 | SUN | PHOTO VOLTAIC |  | 139 | 147 | SDGE | NQC | FC | 0.56 | 4.17 | 4.87 | 6.12 | 8.9 | 18.21 | 20.02 | 17.24 | 15.43 | 10.29 | 7.92 | 4.87
CRELMN_6_AABBT1 | Air Attack Base | GEN | 2023-08-15 | 2023 | LESR | OTHER |  | 0.47 | 0.5 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CRELMN_6_RAMON1 | Ramona 1 | GEN | 2013-12-31 | 2013 | SUN | PHOTO VOLTAIC |  | 2 | 2 | SDGE | NQC | FC | 0.01 | 0.06 | 0.07 | 0.09 | 0.13 | 0.26 | 0.29 | 0.25 | 0.22 | 0.15 | 0.11 | 0.07
CRELMN_6_RAMON2 | Ramona 2 | GEN | 2013-12-31 | 2013 | SUN | PHOTO VOLTAIC |  | 5 | 5 | SDGE | NQC | FC | 0.02 | 0.15 | 0.18 | 0.22 | 0.32 | 0.66 | 0.72 | 0.62 | 0.56 | 0.37 | 0.29 | 0.18
CRELMN_6_RAMSR3 | Ramona Solar Energy | GEN | 2018-02-03 | 2018 | SUN | PHOTO VOLTAIC |  | 4.32 | 4.4 | SDGE | NQC | PD | 0.02 | 0.1 | 0.12 | 0.15 | 0.22 | 0.46 | 0.5 | 0.43 | 0.38 | 0.26 | 0.2 | 0.12
CRESSY_1_PARKER | PARKER POWERHOUSE | GEN | 1981-09-23 | 1981 | WATER | HYDRO |  | 2.83 | 3.8 | PGAE | NQC | FC | 0 | 0 | 0.01 | 0.33 | 0.8 | 0.9 | 0.92 | 1.03 | 0.51 | 0.28 | 0 | 0
CRESTA_7_PL1X2 | CRESTA PH UNIT 1 & 2 AGGREGATE | GEN | 1949-01-01 | 1949 | WATER | HYDRO |  | 70.4 | 0 | PGAE | NQC | FC | 22.06 | 22.06 | 22.06 | 22.06 | 22.06 | 22.06 | 22.06 | 22.06 | 22.06 | 22.06 | 15.7 | 22.06
CRESTA_7_UNIT 1 | CRESTA UNIT #1 | GEN | 0 |  | WATER | HYDRO |  | 35.2 | 35.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CRESTA_7_UNIT 2 | CRESTA UNIT #2 | GEN | 0 |  | WATER | HYDRO |  | 35.2 | 35.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CRIMSN_2_CRMBT1 | Crimson | GEN | 2022-09-16 | 2022 | LESR | OTHER |  | 200 | 200 | SCE | NQC | ID | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
CRIMSN_2_CRMBT2 | Crimson 2 | GEN | 2022-10-28 | 2022 | LESR | OTHER |  | 150 | 150 | SCE | NQC | ID | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
CRNEVL_6_CRNVA | Crane Valley | GEN | 1919-01-01 | 1919 | WATER | HYDRO |  | 0.9 | 0.9 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.37 | 0.16 | 0.12
CRNEVL_6_SJQN 2 | SAN JOAQUIN 2 | GEN | 1917-01-01 | 1917 | WATER | HYDRO |  | 3.2 | 3.2 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.28 | 0.35
CROKET_7_UNIT | CROCKETT COGEN | GEN | 1995-12-20 | 1995 | NATURAL GAS | COMBINED CYCLE |  | 240 | 240 | PGAE | NQC | FC | 217.11 | 217.33 | 145.95 | 226.42 | 223.9 | 225.62 | 221.95 | 223 | 215.29 | 218.19 | 211.4 | 206.77
CRSTWD_6_KUMYAY | Kumeyaay Wind Farm | GEN | 2005-12-21 | 2005 | WIND | WIND |  | 50 | 50 | SDGE | NQC | FC | 8.84 | 9.4 | 8.26 | 7.91 | 8.41 | 7.71 | 7.16 | 5.44 | 5.62 | 5.22 | 7.03 | 8.52
CRWCKS_1_SOLAR1 | Crow Creek Solar 1 | GEN | 2016-06-30 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CSCCOG_1_UNIT 1 | SANTA CLARA CO-GEN | GEN | 1981-01-01 | 1981 | NATURAL GAS | FTUR |  | 7 | 7 | PGAE | NQC | FC | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
CSCGNR_1_UNIT 1 | GIANERA PEAKER UNIT 1 | GEN | 1987-01-01 | 1987 | NATURAL GAS | FTUR |  | 24.75 | 24.8 | PGAE | NQC | FC | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
CSCGNR_1_UNIT 2 | GIANERA PEAKER UNIT 2 | GEN | 1986-01-01 | 1986 | NATURAL GAS | FTUR |  | 24.75 | 24.8 | PGAE | NQC | FC | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
CSLR4S_2_SOLAR | Csolar IV South | GEN | 2013-10-11 | 2013 | SUN | PHOTO VOLTAIC |  | 130 | 130 | SDGE | NQC | FC | 0.52 | 3.9 | 4.55 | 5.72 | 8.32 | 17.03 | 18.72 | 16.12 | 14.43 | 9.62 | 7.41 | 4.55
CSTOGA_6_LNDFIL | Clover Flat Land Fill Gas | GEN | 2014-06-25 | 2014 | BIOGAS | RECIPROCATING ENGINE |  | 0.85 | 0.9 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CSTRVL_7_PL1X2 | Marina Land Fill Gas | GEN | 2007-09-01 | 2007 | OTHER | RECIPROCATING ENGINE |  | 4.53 | 5 | PGAE | NQC | FC | 4.13 | 3.51 | 3.69 | 4.01 | 3.63 | 3.95 | 4.16 | 4.14 | 4.17 | 3.86 | 3.98 | 3.73
CSTRVL_7_QFUNTS | Castroville QF Aggregate | GEN | 2006-06-01 | 2006 | OTHER | OTHER |  | 2 | 11 | PGAE | NQC | FC | 0.04 | 0.06 | 0.15 | 0.07 | 0.04 | 0.08 | 0.07 | 0.09 | 0.09 | 0.07 | 0.05 | 0.03
CTNWDP_1_QF | SMALL QF AGGREGATION - BURNEY | GEN | 1982-01-01 | 1982 | WATER | HYDRO |  | 0.5 | 1 | PGAE | NQC | FC | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.02 | 0.02 | 0.01 | 0.02 | 0.03 | 0.04
CUMBIA_1_SOLAR | Columbia Solar Energy II | GEN | 2015-10-21 | 2015 | SUN | PHOTO VOLTAIC |  | 19 | 19 | PGAE | NQC | FC | 0.08 | 0.57 | 0.67 | 0.84 | 1.22 | 2.49 | 2.74 | 2.36 | 2.11 | 1.41 | 1.08 | 0.67
CUMMNG_6_SUNCT1 | SunSelect 1 | GEN | 2018-05-31 | 2018 | NATURAL GAS | RECIPROCATING ENGINE |  | 4 | 4 | SCE | NQC | FC | 3.33 | 3.39 | 3.04 | 3.01 | 3.34 | 3.54 | 3.53 | 3.56 | 3.4 | 3.16 | 3.38 | 3.45
CURTIS_1_CANLCK | Canal Creek Powerhouse | GEN | 1983-01-01 | 1983 | WATER | HYDRO |  | 0.9 | 0.9 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CURTIS_1_FARFLD | Fairfield Powerhouse | GEN | 1983-08-02 | 1983 | WATER | HYDRO |  | 0.9 | 0.9 | PGAE | NQC | FC | 0 | 0 | 0 | 0.01 | 0.24 | 0.31 | 0.26 | 0.28 | 0.08 | 0 | 0 | 0
CUYAMA_6_SB3SB1 | SEPV Barbara 3 | GEN | 2024-01-02 | 2024 | HYBD | OTHER |  | 3 | 3 | PGAE | NQC | ID |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
CUYAMS_6_CUYSR1 | Cuyama Solar | GEN | 2017-11-30 | 2017 | SUN | PHOTO VOLTAIC |  | 40 | 40 | PGAE | NQC | FC | 0.16 | 1.2 | 1.4 | 1.76 | 2.56 | 5.24 | 5.76 | 4.96 | 4.44 | 2.96 | 2.28 | 1.4
DAIRLD_1_CR1BM1 | Clapper Rail Plant 1 | GEN | 2021-10-01 | 2021 | BIOMASS | RECIPROCATING ENGINE |  | 2 | 2 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DAIRLD_1_MD1SL1 | Madera 1 | GEN | 2017-12-29 | 2017 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DAIRLD_1_MD2BM1 | Madera Digester Genset 2 | GEN | 2019-01-11 | 2019 | BIOGAS | RECIPROCATING ENGINE |  | 0.8 | 0.8 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DAVIS_1_SOLAR1 | Grasslands 3 | GEN | 2013-07-01 | 2013 | SUN | PHOTO VOLTAIC |  | 1 | 1 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DAVIS_1_SOLAR2 | Grasslands 4 | GEN | 2013-08-05 | 2013 | SUN | PHOTO VOLTAIC |  | 1 | 1 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DAVIS_7_MNMETH | MM Yolo Power LLC | GEN | 1997-01-01 | 1997 | BIOGAS | RECIPROCATING ENGINE |  | 4 | 2.7 | PGAE | NQC | FC | 2.14 | 2.4 | 2.42 | 2.4 | 1.94 | 2.01 | 2 | 2.26 | 2.32 | 2.39 | 2.37 | 2.24
DEADCK_1_UNIT | DEADCK_1_UNIT | GEN | 1990-01-29 | 1990 | WATER | HYDRO |  | 1.96 | 2 | PGAE | NQC | FC | 0.07 | 0.05 | 0.08 | 0.15 | 0 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0
DEERCR_6_UNIT 1 | DEER CREEK | GEN | 1908-01-01 | 1908 | WATER | HYDRO |  | 7 | 7 | PGAE | NQC | FC | 1.2 | 1.26 | 0.73 | 0.76 | 2.63 | 3.17 | 3.25 | 3.41 | 3.3 | 2.66 | 1.5 | 1.29
DELAMO_2_ALASB2 | Los Alamitos 2 | GEN | 2023-11-10 | 2023 | HYBD | OTHER |  | 10 | 10 | SCE | NQC | FC | 5.02 | 5.21 | 5.25 | 5.34 | 5.5 | 6.04 | 6.13 | 5.96 | 5.83 | 5.52 | 5.37 | 5.18
DELAMO_2_SOLAR1 | Golden Springs Building H | GEN | 2015-04-22 | 2015 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE | NQC | FC | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
DELAMO_2_SOLAR2 | Golden Springs Building M | GEN | 2015-04-01 | 2015 | SUN | PHOTO VOLTAIC |  | 1.75 | 1.8 | SCE | NQC | FC | 0.01 | 0.05 | 0.06 | 0.08 | 0.11 | 0.23 | 0.25 | 0.22 | 0.19 | 0.13 | 0.1 | 0.06
DELAMO_2_SOLAR3 | Golden Springs Building G | GEN | 2017-02-24 | 2017 | SUN | PHOTO VOLTAIC |  | 1.25 | 1.3 | SCE | NQC | FC | 0.01 | 0.04 | 0.04 | 0.06 | 0.08 | 0.16 | 0.18 | 0.16 | 0.14 | 0.09 | 0.07 | 0.04
DELAMO_2_SOLAR4 | Golden Springs Building F | GEN | 2017-02-24 | 2017 | SUN | PHOTO VOLTAIC |  | 1.3 | 1.4 | SCE | NQC | FC | 0.01 | 0.04 | 0.05 | 0.06 | 0.08 | 0.17 | 0.19 | 0.16 | 0.14 | 0.1 | 0.07 | 0.05
DELAMO_2_SOLAR5 | Golden Springs Building L | GEN | 2017-02-24 | 2017 | SUN | PHOTO VOLTAIC |  | 1 | 1 | SCE | NQC | FC | 0 | 0.03 | 0.04 | 0.04 | 0.06 | 0.13 | 0.14 | 0.12 | 0.11 | 0.07 | 0.06 | 0.04
DELAMO_2_SOLAR6 | Freeway Springs | GEN | 2017-01-25 | 2017 | SUN | PHOTO VOLTAIC |  | 2 | 2 | SCE | NQC | FC | 0.01 | 0.06 | 0.07 | 0.09 | 0.13 | 0.26 | 0.29 | 0.25 | 0.22 | 0.15 | 0.11 | 0.07
DELAMO_2_SOLRC1 | Golden Springs Building C1 | GEN | 2012-02-10 | 2012 | SUN | PHOTO VOLTAIC |  | 1.16 | 1.3 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELAMO_2_SOLRD | Golden Solar Building D | GEN | 2012-04-02 | 2012 | SUN | PHOTO VOLTAIC |  | 1.25 | 1.4 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELSUR_6_BSOLAR | Central Antelope Dry Ranch B | GEN | 2017-09-29 | 2017 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE | NQC | FC | 0.01 | 0.09 | 0.11 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.11
DELSUR_6_CREST | Delsur Aggregate Solar Resources | GEN | 2016-04-05 | 2016 | SUN | PHOTO VOLTAIC |  | 8.5 | 0 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELSUR_6_CREST1 | DELSUR_6_CREST1 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 8.5 | 8.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELSUR_6_DRYFRB | Dry Farm Ranch B | GEN | 2014-11-21 | 2014 | SUN | PHOTO VOLTAIC |  | 5 | 5 | SCE | NQC | FC | 0.02 | 0.15 | 0.18 | 0.22 | 0.32 | 0.66 | 0.72 | 0.62 | 0.56 | 0.37 | 0.29 | 0.18
DELSUR_6_HORSR1 | Horn | GEN | 2023-08-22 | 2023 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELSUR_6_SOLAR1 | Summer Solar North | GEN | 2015-06-03 | 2015 | SUN | PHOTO VOLTAIC |  | 6.5 | 6.5 | SCE | NQC | FC | 0.03 | 0.2 | 0.23 | 0.29 | 0.42 | 0.85 | 0.94 | 0.81 | 0.72 | 0.48 | 0.37 | 0.23
DELSUR_6_SOLAR4 | Radiance Solar 4 | GEN | 2018-12-31 | 2018 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.9 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELSUR_6_SOLAR5 | Radiance Solar 5 | GEN | 2018-12-31 | 2018 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.9 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELTA_2_CTG1 | DELTA ENERGY CENTER CTG UNIT 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 212.5 | 212.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELTA_2_CTG2 | DELTA ENERGY CENTER CTG UNIT 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 212.5 | 212.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELTA_2_CTG3 | DELTA ENERGY CENTER CTG UNIT 3 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 212.5 | 212.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DELTA_2_PL1X4 | DELTA ENERGY CENTER AGGREGATE | GEN | 2002-06-17 | 2002 | NATURAL GAS | COMBINED CYCLE |  | 880 | 0 | PGAE | NQC | FC | 880 | 880 | 880 | 875 | 880 | 880 | 873 | 873 | 873 | 880 | 880 | 880
DELTA_2_STG | DELTA ENERGY CENTER STG UNIT | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 306 | 306 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEVERS_1_SEPV05 | SEPV 5 | GEN | 2012-05-10 | 2012 | SUN | PHOTO VOLTAIC |  | 2 | 2 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEVERS_1_SOLAR | Cascade Solar | GEN | 2013-11-30 | 2013 | SUN | PHOTO VOLTAIC |  | 18.5 | 18.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEVERS_1_SOLAR1 | SEPV8 | GEN | 2013-06-01 | 2013 | SUN | PHOTO VOLTAIC |  | 12 | 12 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEVERS_1_SOLAR2 | SEPV9 | GEN | 2013-06-01 | 2013 | SUN | PHOTO VOLTAIC |  | 9 | 9 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEVERS_2_CS2SR4 | Caliente Solar 2 | GEN | 2018-05-18 | 2018 | SUN | PHOTO VOLTAIC |  | 0.91 | 1 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEVERS_2_DHSPG2 | Desert Hot Springs 2 | GEN | 2013-12-31 | 2013 | SUN | PHOTO VOLTAIC |  | 1.4 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEXZEL_1_UNIT | Western Power and Steam Cogeneration | GEN | 1989-11-30 | 1989 | NATURAL GAS | COMBUSTION TURBINE |  | 20 | 36.8 | PGAE | NQC | FC | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
DIABLO_7_UNIT 1 | Diablo Canyon Unit 1 | GEN | 1985-01-01 | 1985 | URANIUM | STEAM |  | 1150 | 1176 | PGAE | NQC | FC | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140
DIABLO_7_UNIT 2 | Diablo Canyon Unit 2 | GEN | 1986-01-01 | 1986 | URANIUM | STEAM |  | 1150 | 1176 | PGAE | NQC | FC | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140
DISCOV_1_CHEVRN | CHEVRON USA (EASTRIDGE) | GEN | 1988-06-13 | 1988 | NATURAL GAS | FTUR |  | 48.8 | 56.2 | PGAE | NQC | FC | 4.7 | 7.04 | 5.36 | 4.58 | 4.9 | 5.21 | 5.07 | 6.33 | 6.34 | 3.62 | 4.2 | 4.22
DIXNLD_1_LNDFL | Zero Waste Energy | GEN | 2015-11-13 | 2015 | BIOMASS | RECIPROCATING ENGINE |  | 1.6 | 1.6 | PGAE | NQC | FC | 0.72 | 0.67 | 0.75 | 0.84 | 0.81 | 0.84 | 0.87 | 0.87 | 0.88 | 0.89 | 0.87 | 0.86
DMDVLY_1_GEN 1 | Diamond Valley Unit 1 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 10 | Diamond Valley Unit 10 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 11 | Diamond Valley Unit 11 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 12 | Diamond Valley Unit 12 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 2 | Diamond Valley Unit 2 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 3 | Diamond Valley Unit 3 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 4 | Diamond Valley Unit 4 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 5 | Diamond Valley Unit 5 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 6 | Diamond Valley Unit 6 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 7 | Diamond Valley Unit 7 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 8 | Diamond Valley Unit 8 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_GEN 9 | Diamond Valley Unit 9 | GEN | 0 |  | WATER | HYDRO |  | 3.3 | 3.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DMDVLY_1_UNITS | Diamond Valley Lake Pump Gen | GEN | 2001-01-01 | 2001 | WATER | PUMPED STORAGE |  | 15.6 | 0 | SCE | NQC | FC | 1.6 | 5.28 | 0.84 | 0.88 | 2.5 | 0.95 | 0.24 | 0.6 | 0 | 0 | 0 | 0
DONNLS_7_UNIT | Donnells Hydro | GEN | 1957-01-01 | 1957 | WATER | HYDRO |  | 72 | 72 | PGAE | NQC | FC | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
DOSMGO_2_NSPIN | DOSMGO_2_NSPIN | GEN | 0 |  | WATER | PUMP |  | 159 | 159 | PGAE | NQC | FC | 16.26 | 16.26 | 16.26 | 16.26 | 15.21 | 16.26 | 16.26 | 16.26 | 16.26 | 13.64 | 16.26 | 16.26
DOUBLC_1_UNITS | DOUBLE "C" LIMITED | GEN | 1989-03-14 | 1989 | NATURAL GAS | COMBUSTION TURBINE |  | 52.23 | 55.3 | PGAE | NQC | FC | 52.23 | 52.23 | 52.23 | 52.23 | 52.23 | 52.23 | 52.23 | 52.23 | 52.23 | 52.23 | 52.23 | 52.23
DRACKR_2_D4SR4B | Dracker Solar Unit 4B | GEN | 2020-11-10 | 2020 | SUN | PHOTO VOLTAIC |  | 62.5 | 62.5 | SCE | NQC | FC | 0.25 | 1.88 | 2.19 | 2.75 | 4 | 8.19 | 9 | 7.75 | 6.94 | 4.63 | 3.56 | 2.19
DRACKR_2_DS3SR3 | Dracker Solar Unit 3 | GEN | 2020-05-19 | 2020 | SUN | PHOTO VOLTAIC |  | 125 | 125 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRACKR_2_DS4SR4 | Dracker Solar Unit 4A | GEN | 2020-08-24 | 2020 | SUN | PHOTO VOLTAIC |  | 62.5 | 62.5 | SCE | NQC | FC | 0.11 | 1.01 | 1.17 | 1.87 | 2.81 | 5.66 | 6.07 | 5.15 | 4.43 | 2.71 | 1.7 | 0.52
DRACKR_2_DSUBT1 | Dracker Solar Unit 1 BESS | GEN | 2021-08-12 | 2021 | LESR | OTHER |  | 63 | 63 | SCE | NQC | FC | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
DRACKR_2_DSUBT2 | Dracker Solar Unit 2 BESS | GEN | 2021-04-08 | 2021 | LESR | OTHER |  | 115 | 115 | SCE | NQC | FC | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
DRACKR_2_DSUBT3 | Dracker Solar Unit 3 BESS | GEN | 2021-07-23 | 2021 | LESR | OTHER |  | 115 | 115 | SCE | NQC | FC | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 101.05
DRACKR_2_DSUBT4 | Dracker Solar Unit 4 BESS | GEN | 2022-09-28 | 2022 | LESR | OTHER |  | 47 | 47 | SCE | NQC | FC | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
DRACKR_2_SOLAR1 | Dracker Solar Unit 1 | GEN | 2016-03-07 | 2016 | SUN | PHOTO VOLTAIC |  | 110 | 110 | SCE | NQC | FC | 0.23 | 2.02 | 2.58 | 3.63 | 5.47 | 11.01 | 11.67 | 9.87 | 8.49 | 5.38 | 3.6 | 1.65
DRACKR_2_SOLAR2 | Dracker Solar Unit 2 | GEN | 2016-09-30 | 2016 | SUN | PHOTO VOLTAIC |  | 125 | 125 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DREWS_6_GEN 1 | DREWS UNIT 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 10.8 | 10.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DREWS_6_GEN 2 | DREWS UNIT 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 10.8 | 10.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DREWS_6_GEN 3 | DREWS UNIT 3 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 10.8 | 10.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DREWS_6_GEN 4 | DREWS UNIT 4 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 10.8 | 10.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DREWS_6_PL1X4 | Drews Generating Plant | GEN | 2001-08-14 | 2001 | NATURAL GAS | FTUR |  | 41.4 | 0 | SCE | NQC | FC | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
DREWSR_2_BHSSR1 | Blue Hornet Solar | GEN | 2022-11-04 | 2022 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRUM_7_PL1X2 | Drum PH 1 Units 1 & 2 Aggregate | GEN | 1913-01-01 | 1913 | WATER | HYDRO |  | 26 | 0 | PGAE | NQC | FC | 9.6 | 0 | 0 | 0 | 0 | 0 | 10.4 | 10.4 | 0 | 0 | 9.6 | 10.4
DRUM_7_PL3X4 | Drum PH 1 Units 3 & 4 Aggregate | GEN | 1922-01-01 | 1922 | WATER | HYDRO |  | 28.9 | 0 | PGAE | NQC | FC | 12.8 | 0 | 0 | 0 | 12.8 | 12.8 | 12.8 | 12.8 | 0 | 0 | 12.8 | 12.8
DRUM_7_UNIT 1 | DRUM PH 1 UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 13 | 13 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRUM_7_UNIT 2 | DRUM PH 1 UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 13 | 13 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRUM_7_UNIT 3 | Drum PH 1 Unit 3 | GEN | 0 |  | WATER | HYDRO |  | 12.9 | 12.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRUM_7_UNIT 4 | Drum PH 1 Unit 4 | GEN | 0 |  | WATER | HYDRO |  | 16 | 16 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRUM_7_UNIT 5 | DRUM PH 2 UNIT 5 | GEN | 1965-01-01 | 1965 | WATER | HYDRO |  | 50 | 50 | PGAE | NQC | FC | 39.2 | 44.24 | 43.6 | 38.8 | 41.74 | 39.2 | 48.1 | 47.74 | 27.28 | 0 | 36 | 44.06
DSABLA_7_UNIT | De Sabla Hydro | GEN | 1963-01-01 | 1963 | WATER | HYDRO |  | 18.5 | 18.5 | PGAE | NQC | FC | 5.85 | 6.81 | 6.42 | 4.13 | 5.7 | 6.4 | 7.32 | 5.87 | 3.26 | 2.05 | 3.09 | 3.85
DSFLWR_2_W9CSB1 | Willy 9 Chap 1 | GEN | 2023-03-08 | 2023 | HYBD | OTHER |  | 102 | 102 | SCE | NQC | ID | 0.41 | 3.06 | 3.57 | 4.49 | 6.53 | 13.36 | 14.69 | 12.65 | 11.32 | 7.55 | 5.81 | 3.57
DSFLWR_2_W9CSB2 | Willy 9 Chap 2 | GEN | 2023-03-08 | 2023 | HYBD | OTHER |  | 72 | 72 | SCE | NQC | ID | 0.29 | 2.16 | 2.52 | 3.17 | 4.61 | 9.43 | 10.37 | 8.93 | 7.99 | 5.33 | 4.1 | 2.52
DSFLWR_2_WS2SR1 | Willow Springs 2 | GEN | 2019-01-29 | 2019 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE | NQC | FC | 0.4 | 3 | 3.5 | 4.4 | 6.4 | 13.1 | 14.4 | 12.4 | 11.1 | 7.4 | 5.7 | 3.5
DSRTHV_2_DH1SR1 | Desert Harvest | GEN | 2020-12-11 | 2020 | SUN | PHOTO VOLTAIC |  | 80 | 80 | SCE | NQC | FC | 0.32 | 2.4 | 2.8 | 3.52 | 5.12 | 10.48 | 11.52 | 9.92 | 8.88 | 5.92 | 4.56 | 2.8
DSRTHV_2_DH2BT1 | Desert Harvest BESS | GEN | 2021-06-10 | 2021 | LESR | OTHER |  | 35 | 35 | SCE | NQC | PD | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
DSRTHV_2_DH2SR2 | Desert Harvest 2 | GEN | 2020-12-11 | 2020 | SUN | PHOTO VOLTAIC |  | 70 | 70 | SCE | NQC | FC | 0.17 | 1.49 | 1.77 | 2.41 | 3.54 | 7.15 | 7.7 | 6.45 | 5.71 | 3.71 | 2.62 | 1.28
DSRTSL_2_SOLAR1 | Desert Stateline | GEN | 2016-08-30 | 2016 | SUN | PHOTO VOLTAIC |  | 296.19 | 0 | SCE | NQC | FC | 1.18 | 8.89 | 10.37 | 13.03 | 18.96 | 38.8 | 42.65 | 36.73 | 32.88 | 21.92 | 16.88 | 10.37
DSRTSL_2_SOLR1A | DSRTSL_2_SOLR1A | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 148.1 | 148.1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRTSL_2_SOLR1B | DSRTSL_2_SOLR1B | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 148.1 | 148.1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRTSN_2_DS2BT1 | Desert Sunlight PV II Storage | GEN | 0 |  | LESR | OTHER |  | 87.4 | 87.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRTSN_2_DS2BT2 | Desert Sunlight PV II Storage | GEN | 0 |  | LESR | OTHER |  | 142.6 | 142.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRTSN_2_DS2BT3 | Desert Sunlight PV II Storage 2 | GEN | 0 |  | LESR | OTHER |  | 115 | 115 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRTSN_2_DS2BT4 | Desert Sunlight PV II Storage 2 | GEN | 0 |  | LESR | OTHER |  | 115 | 115 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRTSN_2_DS2BX2 | Desert Sunlight PV II Storage 2 | GEN | 0 |  | LESR | OTHER |  | 230 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRTSN_2_DS2X2 | Desert Sunlight PV II Storage | GEN | 2022-08-28 | 2022 | LESR | OTHER |  | 230 | 230 | SCE | NQC | FC | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
DSRTSN_2_SOLAR1 | Desert Sunlight 300 | GEN | 2013-10-22 | 2013 | SUN | PHOTO VOLTAIC |  | 300 | 300 | SCE | NQC | FC | 1.2 | 9 | 10.5 | 13.2 | 19.2 | 39.3 | 43.2 | 37.2 | 33.3 | 22.2 | 17.1 | 10.5
DSRTSN_2_SOLAR2 | Desert Sunlight 250 | GEN | 2013-10-12 | 2013 | SUN | PHOTO VOLTAIC |  | 250 | 0 | SCE | NQC | FC | 0.24 | 1.6 | 3.98 | 5.55 | 7.33 | 15.85 | 17.3 | 14.83 | 12.25 | 7.52 | 4.72 | 1.32
DSRTSN_2_SOLR1A | Desert Sunlight 300 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 156.9 | 156.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRTSN_2_SOLR1B | Desert Sunlight 300 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 156.9 | 156.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRTSN_2_SOLR2A | Desert Sunlight 250 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 129.8 | 129.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSRTSN_2_SOLR2B | Desert Sunlight 250 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 129.8 | 129.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DTCHWD_2_BT3WND | Brookfield Tehachapi 3 | GEN | 2016-04-22 | 2016 | WIND | WIND |  | 4.5 | 4.5 | SCE | NQC | FC | 0.8 | 0.85 | 0.74 | 0.71 | 0.76 | 0.69 | 0.64 | 0.49 | 0.51 | 0.47 | 0.63 | 0.77
DTCHWD_2_BT4WND | Brookfield Tehachapi 4 | GEN | 2016-04-22 | 2016 | WIND | WIND |  | 6.52 | 7.1 | SCE | NQC | FC | 1.15 | 1.23 | 1.08 | 1.03 | 1.1 | 1.01 | 0.93 | 0.71 | 0.73 | 0.68 | 0.92 | 1.11
DUANE_1_PL1X3 | DONALD VON RAESFELD POWER PROJECT | GEN | 2005-03-24 | 2005 | NATURAL GAS | COMBINED CYCLE |  | 147.8 | 0 | PGAE | NQC | FC | 147.8 | 147.8 | 147.8 | 147.8 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 147.8 | 147.8 | 147.8
DUANE_7_CTG1 | Donald Von Raesfeld CTG Unit 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 50.4 | 50.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DUANE_7_CTG2 | Donald Von Raesfeld CTG Unit 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 50.4 | 50.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DUANE_7_STG3 | Donald Von Raesfeld STG Unit 3 | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 53.6 | 53.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DURNMESA_3_WBDYN | DURAN MESA | TG | 2021-12-02 | 2021 | WIND | WIND |  | 105.08 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DUTCH1_7_UNIT 1 | DUTCH FLAT 1 PH | GEN | 1943-01-01 | 1943 | WATER | HYDRO |  | 22 | 22 | PGAE | NQC | FC | 17.6 | 17.6 | 6.8 | 16.8 | 15.2 | 17.2 | 19.28 | 20.78 | 12.8 | 9.6 | 17.6 | 20.2
DUTCH2_7_UNIT 1 | DUTCH FLAT 2 PH | GEN | 1965-01-01 | 1965 | WATER | HYDRO |  | 26 | 26 | PGAE | NQC | FC | 5.2 | 16 | 17.2 | 5.6 | 5.6 | 5.6 | 16 | 16.76 | 0 | 0 | 2.8 | 5.6
DVLCYN_1_UNIT 1 | DEVIL CANYON HYDRO UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 60 | 60 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DVLCYN_1_UNIT 2 | DEVIL CANYON HYDRO UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 60 | 60 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DVLCYN_1_UNIT 3 | DEVIL CANYON HYDRO UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 80 | 80 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DVLCYN_1_UNIT 4 | DEVIL CANYON HYDRO UNIT 4 | GEN | 0 |  | WATER | HYDRO |  | 80 | 80 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DVLCYN_1_UNITS | DEVIL CANYON HYDRO UNITS 1-4 AGGREGATE | GEN | 1972-01-01 | 1972 | WATER | HYDRO |  | 235 | 0 | SCE | NQC | FC | 146.91 | 82.76 | 106.43 | 145.35 | 134.52 | 146.86 | 134.22 | 140.09 | 138.61 | 137.34 | 146.49 | 132.7
DYERSM_6_DSWWD1 | Dyer Summit Wind Repower | GEN | 2022-04-05 | 2022 | WIND | WIND |  | 44.8 | 44.8 | PGAE | NQC | FC | 14.71 | 15.78 | 14.08 | 14.87 | 15.39 | 11.35 | 10.09 | 9.48 | 9.73 | 8.16 | 10.3 | 13.17
DYLAN_2_BMTBT1 | Beaumont BESS | GEN | 0 |  | LESR | OTHER |  | 100 | 100 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EASTWD_7_UNIT | EASTWOOD PUMP-GEN | GEN | 1987-01-01 | 1987 | WATER | PUMPED STORAGE |  | 200 | 207 | SCE | NQC | FC | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199
ECASCO_2_SJGBT1 | San Jacinto Grid | GEN | 0 |  | LESR | OTHER |  | 65 | 65 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EDMONS_2_NSPIN | EDMONS_2_NSPIN | GEN | 0 |  | WATER | PUMP |  | 775.8 | 840 | SCE | NQC | FC | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236
EDWARD_2_E21SB1 | EdSan 2 Edwards 1A | GEN | 2022-08-27 | 2022 | HYBD | OTHER |  | 166 | 166 | SCE | NQC | ID | 71.29 | 73.62 | 74.16 | 75.26 | 77.39 | 84.13 | 85.3 | 83.08 | 81.42 | 77.56 | 75.53 | 73.1
EDWARD_2_E23SB1 | EdSan 2 Edwards 3 | GEN | 2021-12-30 | 2021 | HYBD | OTHER |  | 24 | 24 | SCE | NQC | ID | 6.08 | 6.61 | 6.72 | 6.93 | 7.37 | 8.81 | 9.08 | 8.63 | 8.33 | 7.52 | 7.12 | 6.63
EDWARD_2_ES2BT3 | EdSan 2 | GEN | 2022-04-02 | 2022 | HYBD | OTHER |  | 151 | 151 | SCE | NQC | ID | 66.26 | 68.35 | 68.83 | 69.84 | 71.76 | 77.84 | 78.89 | 76.88 | 75.37 | 71.88 | 70.05 | 67.86
EDWARD_2_ESSSB1 | Sanborn Solar 2 Edwards 5 | GEN | 2023-11-17 | 2023 | HYBD | OTHER |  | 116 | 116 | SCE | NQC | ID | 0.46 | 3.48 | 4.06 | 5.1 | 7.42 | 15.2 | 16.7 | 14.38 | 12.88 | 8.58 | 6.61 | 4.06
EDWARD_2_ESSSB2 | Sanborn Solar 2 | GEN | 2023-11-14 | 2023 | HYBD | OTHER |  | 132 | 132 | SCE | NQC | ID | 0.53 | 3.96 | 4.62 | 5.81 | 8.45 | 17.29 | 19.01 | 16.37 | 14.65 | 9.77 | 7.52 | 4.62
EEKTMN_6_SOLAR1 | EE K Solar 1 | GEN | 2015-08-12 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELCABO_5_ECWSCEDYN | El Cabo Wind | TG | 2017-06-02 | 2017 | WIND | WIND |  | 298 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELCAJN_6_EB1BT1 | Eastern BESS 1 | GEN | 2017-02-18 | 2017 | LESR | OTHER |  | 7.5 | 7.5 | SDGE | NQC | FC | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
ELCAJN_6_LM6K | El Cajon Energy Center | GEN | 2010-06-16 | 2010 | NATURAL GAS | COMBUSTION TURBINE |  | 48.1 | 49.7 | SDGE | NQC | FC | 48.1 | 48.1 | 48.1 | 48.1 | 48.1 | 48.1 | 48.1 | 48.1 | 48.1 | 48.1 | 48.1 | 48.1
ELCAJN_6_UNITA1 | Cuyamaca Peak Energy Plant | GEN | 2002-05-29 | 2002 | NATURAL GAS | COMBUSTION TURBINE |  | 45.42 | 48 | SDGE | NQC | FC | 45.42 | 45.42 | 45.42 | 45.42 | 45.42 | 45.42 | 45.42 | 45.42 | 45.42 | 45.42 | 45.42 | 45.42
ELCAP_1_SOLAR | 2097 Helton | GEN | 2015-05-01 | 2015 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELDORO_7_UNIT 1 | El Dorado Unit 1 | GEN | 2005-05-21 | 2005 | WATER | HYDRO |  | 11 | 10.5 | PGAE | NQC | FC | 2.28 | 3.32 | 2.76 | 5.08 | 7.4 | 4.29 | 4.39 | 4.1 | 5.44 | 0.14 | 0 | 0
ELDORO_7_UNIT 2 | El Dorado Unit 2 | GEN | 2005-05-21 | 2005 | WATER | HYDRO |  | 11 | 10.5 | PGAE | NQC | FC | 4.82 | 3.61 | 1.16 | 4.93 | 7.78 | 4.33 | 2.04 | 5.19 | 3.49 | 0.14 | 0 | 0
ELECTR_7_PL1X3 | ELECTRA PH UNIT 1 & 2 AGGREGATE | GEN | 1948-01-01 | 1948 | WATER | HYDRO |  | 93 | 0 | PGAE | NQC | FC | 49.6 | 48 | 50.76 | 25.4 | 48.6 | 55.9 | 50.88 | 61.83 | 63.68 | 50.9 | 52.8 | 55.6
ELECTR_7_UNIT 1 | ELECTRA UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 31.7 | 31.7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELECTR_7_UNIT 2 | ELECTRA UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 31.7 | 31.7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELECTR_7_UNIT 3 | ELECTRA UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 38.1 | 38.1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELKCRK_6_STONYG | STONEY GORGE HYDRO AGGREGATE | GEN | 1986-01-01 | 1986 | WATER | HYDRO |  | 4.9 | 4.9 | PGAE | NQC | FC | 1.8 | 2.4 | 2.7 | 2.2 | 1.6 | 1.7 | 2.2 | 2 | 1.4 | 0.4 | 0.1 | 0.9
ELKHIL_2_PL1X3 | ELK HILLS COMBINED CYCLE (AGGREGATE) | GEN | 2003-07-24 | 2003 | NATURAL GAS | COMBINED CYCLE |  | 551.7 | 0 | PGAE | NQC | FC | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
ELKHIL_7_CTG1 | ELK HILLS COMBUSTION TURBINE UNIT 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 169 | 169 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELKHIL_7_CTG2 | ELK HILLS COMBUSTION TURBINE UNIT 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 169 | 169 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELKHIL_7_STG | ELK HILLS STEAM TURBINE UNIT | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 223 | 223 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELKHRN_1_EESBT1 | Elkhorn Energy Storage | GEN | 0 |  | LESR | OTHER |  | 60.83 | 60.83 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELKHRN_1_EESBT2 | Elkhorn Energy Storage | GEN | 0 |  | LESR | OTHER |  | 60.83 | 60.83 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELKHRN_1_EESBT3 | Elkhorn Energy Storage | GEN | 0 |  | LESR | OTHER |  | 60.83 | 60.83 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELKHRN_1_EESX3 | Elkhorn Energy Storage | GEN | 2022-04-07 | 2022 | LESR | OTHER |  | 182.5 | 0 | PGAE | NQC | FC | 182.5 | 182.5 | 182.5 | 182.5 | 182.5 | 182.5 | 182.5 | 182.5 | 182.5 | 182.5 | 182.5 | 182.5
ELLIOT_6_ELIBT1 | Elliott Energy Storage | GEN | 0 |  | LESR | OTHER |  | 9.75 | 9.75 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELLIS_2_QF | ELLIS QFS | GEN | 1993-01-01 | 1993 | OTHER | OTHER |  | 12 | 28.2 | SCE | NQC | FC | 2.08 | 2.23 | 1.7 | 1.97 | 1.92 | 2.2 | 1.6 | 0.76 | 1 | 1 | 1.01 | 0.98
ELSEGN_2_UN1011 | El Segundo Energy Center 5/6 | GEN | 2013-06-29 | 2013 | NATURAL GAS | COMBINED CYCLE |  | 274.31 | 0 | SCE | NQC | FC | 274.31 | 274.31 | 274.31 | 274.31 | 274.31 | 274.31 | 274.31 | 274.31 | 274.31 | 274.31 | 274.31 | 274.31
ELSEGN_2_UN2021 | El Segundo Energy Center 7/8 | GEN | 2013-06-29 | 2013 | NATURAL GAS | COMBINED CYCLE |  | 271.74 | 0 | SCE | NQC | FC | 271.74 | 271.74 | 271.74 | 271.74 | 271.74 | 271.74 | 271.74 | 271.74 | 271.74 | 271.74 | 271.74 | 271.74
ELSEGN_2_UNIT10 | El Segundo Energy Center Unit 6 | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 90.5 | 90.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELSEGN_2_UNIT11 | El Segundo Energy Center Unit 5 | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 228 | 228 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELSEGN_2_UNIT20 | El Segundo Energy Center Unit 8 | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 90.5 | 90.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELSEGN_2_UNIT21 | El Segundo Energy Center Unit 7 | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 228 | 228 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ENERSJ_2_WIND | ESJ Wind Energy | GEN | 2022-01-13 | 2022 | WIND | WIND |  | 151 | 151 | SDGE | NQC | FC | 26.68 | 28.38 | 24.93 | 23.89 | 25.4 | 23.28 | 21.63 | 16.44 | 16.98 | 15.75 | 21.23 | 25.72
ENERSJ_5_ESJWD2 | Energia Sierra Juarez Wind 2 | GEN | 2022-01-13 | 2022 | WIND | WIND |  | 105 | 105 | SDGE | NQC | FC | 18.55 | 19.73 | 17.34 | 16.61 | 17.66 | 16.19 | 15.04 | 11.43 | 11.81 | 10.95 | 14.76 | 17.88
ENWIND_2_WIND1 | Cameron Ridge | GEN | 2014-12-10 | 2014 | WIND | WIND |  | 47.1 | 47.1 | SCE | NQC | FC | 8.32 | 8.85 | 7.78 | 7.45 | 7.92 | 7.26 | 6.75 | 5.13 | 5.3 | 4.91 | 6.62 | 8.02
ENWIND_2_WIND2 | Ridgetop I | GEN | 2015-03-23 | 2015 | WIND | WIND |  | 38.24 | 65 | SCE | NQC | FC | 6.76 | 7.19 | 6.31 | 6.05 | 6.43 | 5.9 | 5.48 | 4.16 | 4.3 | 3.99 | 5.38 | 6.51
ESCNDO_6_EB1BT1 | Escondido BESS 1 | GEN | 2017-03-06 | 2017 | LESR | OTHER |  | 10 | 10 | SDGE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
ESCNDO_6_EB2BT2 | Escondido BESS 2 | GEN | 2017-03-06 | 2017 | LESR | OTHER |  | 10 | 10 | SDGE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
ESCNDO_6_EB3BT3 | Escondido BESS 3 | GEN | 2017-03-06 | 2017 | LESR | OTHER |  | 10 | 10 | SDGE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
ESCNDO_6_PL1X2 | MMC Escondido Aggregate | GEN | 2014-01-25 | 2014 | NATURAL GAS | COMBUSTION TURBINE |  | 48.71 | 49.5 | SDGE | NQC | FC | 48.71 | 48.71 | 48.71 | 48.71 | 48.71 | 48.71 | 48.71 | 48.71 | 48.71 | 48.71 | 48.71 | 48.71
ESCNDO_6_UNITB1 | CalPeak Power Enterprise Unit 1 | GEN | 2001-10-23 | 2001 | NATURAL GAS | COMBUSTION TURBINE |  | 48.04 | 52 | SDGE | NQC | FC | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04 | 48.04
ESCO_6_GLMQF | Goal Line Cogen | GEN | 1994-01-01 | 1994 | NATURAL GAS | COMBUSTION TURBINE |  | 49.9 | 49.9 | SDGE | NQC | FC | 49.9 | 49.9 | 49.9 | 49.9 | 49.9 | 49.9 | 49.9 | 49.9 | 49.9 | 49.9 | 49.9 | 49.9
ESNHWR_2_CS1BT3 | Carris Storage 1 | GEN | 0 |  | LESR | OTHER |  | 10 | 10 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ESNHWR_2_HDSBT2 | Hecate Energy Desert Storage 1 | GEN | 0 |  | LESR | OTHER |  | 10 | 10 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ESNHWR_2_WC1BT1 | Wildcat I BESS | GEN | 2021-10-13 | 2021 | LESR | OTHER |  | 3 | 3 | SCE | NQC | ID | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
ESQUON_6_LNDFIL | Neal Road Landfill Generating Facility | GEN | 2012-09-27 | 2012 | BIOGAS | RECIPROCATING ENGINE |  | 2.1 | 2.1 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ESTWND_2_OPPWD1 | Oasis Power Plant Eastwind | GEN | 2021-10-12 | 2021 | WIND | WIND |  | 57.14 | 57.2 | SCE | NQC | FC | 10.1 | 10.74 | 9.44 | 9.04 | 9.61 | 8.81 | 8.19 | 6.22 | 6.43 | 5.96 | 8.03 | 9.73
ETIWND_2_CHMPNE | Champagne | GEN | 2013-12-20 | 2013 | SUN | PHOTO VOLTAIC |  | 1 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ETIWND_2_FONTNA | FONTANALYTLE CREEK POWERHOUSE P | GEN | 1904-01-01 | 1904 | WATER | HYDRO |  | 2.56 | 2.6 | SCE | NQC | FC | 0.94 | 1.02 | 0.53 | 0.78 | 0.78 | 0.57 | 0.5 | 0.38 | 0.42 | 0.46 | 0.59 | 0.57
ETIWND_2_SEPBT1 | Separator | GEN | 0 |  | LESR | OTHER |  | 100 | 100 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ETIWND_2_SOLAR1 | Dedeaux Ontario | GEN | 2016-03-23 | 2016 | SUN | PHOTO VOLTAIC |  | 1 | 1 | SCE | NQC | FC | 0 | 0.03 | 0.04 | 0.04 | 0.06 | 0.13 | 0.14 | 0.12 | 0.11 | 0.07 | 0.06 | 0.04
ETIWND_2_SOLAR2 | Rochester | GEN | 2016-09-06 | 2016 | SUN | PHOTO VOLTAIC |  | 1 | 1 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ETIWND_2_SOLAR5 | Dulles | GEN | 2016-11-17 | 2016 | SUN | PHOTO VOLTAIC |  | 2 | 2 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ETIWND_2_UNIT1 | ETIWND_2_UNIT1 | GEN | 2016-01-01 | 2016 | NATURAL GAS | FTUR |  | 33.6 | 33.6 | SCE | NQC | FC | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6
ETIWND_6_GRPLND | Grapeland Peaker | GEN | 2007-09-20 | 2007 | NATURAL GAS | COMBUSTION TURBINE |  | 45.64 | 59 | SCE | NQC | FC | 45.64 | 45.64 | 45.64 | 45.64 | 45.64 | 45.64 | 45.64 | 45.64 | 45.64 | 45.64 | 45.64 | 45.64
ETIWND_6_MWDETI | ETIWANDA RECOVERY HYDRO | GEN | 1994-01-01 | 1994 | WATER | HYDRO |  | 24 | 23.9 | SCE | NQC | FC | 1.21 | 2.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EXCHEC_7_UNIT 1 | EXCHEQUER HYDRO | GEN | 1967-01-01 | 1967 | WATER | HYDRO |  | 94.5 | 94.5 | PGAE | NQC | FC | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5
EXCLSG_1_SOLAR | Excelsior Solar | GEN | 2016-10-06 | 2016 | SUN | PHOTO VOLTAIC |  | 60 | 60 | PGAE | NQC | FC | 0.24 | 1.8 | 2.1 | 2.64 | 3.84 | 7.86 | 8.64 | 7.44 | 6.66 | 4.44 | 3.42 | 2.1
FALBRK_6_FESBT1 | Fallbrook Energy Storage | GEN | 2023-05-03 | 2023 | LESR | OTHER |  | 40 | 40 | SDGE | NQC | FC | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
FELLOW_7_QFUNTS | Fellow QF Aggregate | GEN | 2006-06-01 | 2006 | NATURAL GAS | FTUR |  | 6.2 | 17.5 | PGAE | NQC | FC | 2.44 | 2.39 | 2.43 | 2.42 | 2.73 | 2.7 | 2.58 | 2.6 | 2.76 | 2.82 | 2.78 | 2.82
FIFTHS_2_FSSBT | Fifth Standard Battery | GEN | 2023-09-15 | 2023 | LESR | OTHER |  | 137 | 137 | PGAE | NQC | FC | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137
FIFTHS_2_FSSR1 | Fifth Standard Solar | GEN | 2023-09-29 | 2023 | SUN | PHOTO VOLTAIC |  | 150 | 150 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FLOWD_2_RT2WD2 | Ridgetop 2 | GEN | 2018-10-12 | 2018 | WIND | WIND |  | 27.39 | 27.4 | SCE | NQC | FC | 4.84 | 5.15 | 4.52 | 4.33 | 4.61 | 4.22 | 3.92 | 2.98 | 3.08 | 2.86 | 3.85 | 4.66
FLOWD_2_WIND1 | Cameron Ridge 2 | GEN | 2016-01-15 | 2016 | WIND | WIND |  | 11.9 | 11.9 | SCE | NQC | FC | 2.1 | 2.24 | 1.97 | 1.88 | 2 | 1.83 | 1.7 | 1.3 | 1.34 | 1.24 | 1.67 | 2.03
FLOWD2_2_FPLWND | DIABLO WINDS | GEN | 2005-05-01 | 2005 | WIND | WIND |  | 18 | 18 | PGAE | NQC | FC | 5.91 | 6.34 | 5.66 | 5.98 | 6.18 | 4.56 | 4.06 | 3.81 | 3.91 | 3.28 | 4.14 | 5.29
FMEADO_6_HELLHL | FMEADO_6_HELLHL | GEN | 1983-04-30 | 1983 | WATER | HYDRO |  | 0.6 | 0.5 | PGAE | NQC | FC | 0.21 | 0.21 | 0.28 | 0.39 | 0.12 | 0.47 | 0.44 | 0.4 | 0.24 | 0.23 | 0.21 | 0.19
FMEADO_7_UNIT | FRENCH MEADOWS HYDRO | GEN | 1966-01-01 | 1966 | WATER | HYDRO |  | 16 | 18 | PGAE | NQC | FC | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
FORBST_7_UNIT 1 | FORBESTOWN HYDRO | GEN | 1963-01-01 | 1963 | WATER | HYDRO |  | 37.5 | 39 | PGAE | NQC | FC | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
FORKBU_6_UNIT | Forks of Butte Hydro | GEN | 2023-02-06 | 2023 | WATER | HYDRO |  | 14.3 | 14.4 | PGAE | NQC | FC | 6.93 | 7.31 | 7.08 | 9.2 | 7.35 | 9.85 | 9.84 | 9.07 | 8.26 | 6.19 | 6.63 | 6.37
FRESHW_1_SOLAR1 | Corcoran 3 | GEN | 2016-03-04 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FRIANT_6_UNITS | FRIANT DAM | GEN | 2016-03-01 | 2016 | WATER | HYDRO |  | 25 | 34.7 | PGAE | NQC | FC | 3.74 | 2.68 | 1.36 | 1.72 | 3.8 | 7.65 | 7.09 | 4.13 | 2.57 | 2.31 | 0.59 | 1.67
FRNTBW_6_SOLAR1 | Frontier Solar | GEN | 2019-02-05 | 2019 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
FROGTN_1_UTICAA | Angels Powerhouse | GEN | 2017-08-22 | 2017 | WATER | HYDRO |  | 1.4 | 1.4 | PGAE | NQC | FC | 0.8 | 0.72 | 0.72 | 0.64 | 0.46 | 0.31 | 0.3 | 0.23 | 0.34 | 0.43 | 0 | 0.72
FROGTN_1_UTICAM | Murphys Powerhouse | GEN | 2017-08-22 | 2017 | WATER | HYDRO |  | 3.6 | 3.6 | PGAE | NQC | FC | 1.66 | 1.56 | 1.58 | 1.45 | 1.36 | 1.27 | 1.24 | 1.26 | 1.25 | 1.26 | 0 | 1.45
FTSWRD_6_TRFORK | Three Forks Water Power Project | GEN | 2011-11-01 | 2011 | WATER | HYDRO |  | 1.63 | 1.5 | PGAE | NQC | PD | 0.57 | 0.5 | 0.29 | 0.53 | 0.54 | 0.3 | 0.22 | 0.11 | 0.16 | 0.09 | 0.14 | 0.17
FTSWRD_7_QFUNTS | FTSWRD_7_QFUNTS | GEN | 0 |  | WATER | HYDRO |  | 1.6 | 1.3 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FULTON_1_QF | SMALL QF AGGREGATION - ZENIA | GEN | 1983-01-01 | 1983 | WATER | HYDRO |  | 1 | 1 | PGAE | NQC | FC | 0.12 | 0.11 | 0.1 | 0.11 | 0.1 | 0.07 | 0.04 | 0.02 | 0.03 | 0.04 | 0.06 | 0.07
GALE_1_SR3SR3 | Sunray 3 | GEN | 2017-06-29 | 2017 | SUN | PHOTO VOLTAIC |  | 13.8 | 13.8 | SCE | NQC | FC | 0.06 | 0.41 | 0.48 | 0.61 | 0.88 | 1.81 | 1.99 | 1.71 | 1.53 | 1.02 | 0.79 | 0.48
GANSO_1_WSTBM1 | Weststar Dairy Biogas | GEN | 2018-02-02 | 2018 | BIOGAS | RECIPROCATING ENGINE |  | 1 | 1 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GARLND_2_GARBT1 | Garland B BESS | GEN | 2022-01-31 | 2022 | LESR | OTHER |  | 88 | 88 | SCE | NQC | FC | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
GARLND_2_GASLR | Garland B | GEN | 2016-10-27 | 2016 | SUN | PHOTO VOLTAIC |  | 180 | 180 | SCE | NQC | FC | 0.44 | 3.74 | 4.45 | 5.65 | 8.57 | 18.55 | 20.6 | 17.44 | 14.87 | 9.23 | 6.4 | 3.28
GARLND_2_GASLRA | Garland A | GEN | 2016-09-23 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
GARNET_1_SOLAR | North Palm Springs 4A | GEN | 2012-11-02 | 2012 | SUN | PHOTO VOLTAIC |  | 4 | 4.1 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GARNET_1_SOLAR2 | Garnet Solar Power Generation Station 1 | GEN | 2014-12-23 | 2014 | SUN | PHOTO VOLTAIC |  | 4 | 4 | SCE | NQC | FC | 0.02 | 0.12 | 0.14 | 0.18 | 0.26 | 0.52 | 0.58 | 0.5 | 0.44 | 0.3 | 0.23 | 0.14
GARNET_1_WIND | GARNET WIND ENERGY CENTER | GEN | 2009-06-02 | 2009 | WIND | WIND |  | 6.5 | 6.5 | SCE | NQC | FC | 1.15 | 1.22 | 1.07 | 1.03 | 1.09 | 1 | 0.93 | 0.71 | 0.73 | 0.68 | 0.91 | 1.11
GARNET_1_WINDS | Garnet Winds Aggregation | GEN | 2011-02-21 | 2011 | WIND | WIND |  | 22.5 | 23.3 | SCE | NQC | FC | 3.98 | 4.23 | 3.72 | 3.56 | 3.79 | 3.47 | 3.22 | 2.45 | 2.53 | 2.35 | 3.16 | 3.83
GARNET_1_WT3WND | Wagner Wind | GEN | 2012-12-24 | 2012 | WIND | WIND |  | 6 | 6 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GARNET_2_COAWD2 | Coachella 2 | GEN | 2021-04-26 | 2021 | WIND | WIND |  | 10.8 | 10.8 | SCE | NQC | FC | 1.91 | 2.03 | 1.78 | 1.71 | 1.82 | 1.67 | 1.55 | 1.18 | 1.21 | 1.13 | 1.52 | 1.84
GARNET_2_HYDRO | Whitewater Hydro | GEN | 2016-07-08 | 2016 | WATER | HYDRO |  | 1 | 1 | SCE | NQC | FC | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.27 | 0.24 | 0.54
GARNET_2_WIND1 | Phoenix | GEN | 2015-01-26 | 2015 | WIND | WIND |  | 11.2 | 11.2 | SCE | NQC | FC | 1.98 | 2.1 | 1.85 | 1.77 | 1.88 | 1.73 | 1.6 | 1.22 | 1.26 | 1.17 | 1.57 | 1.91
GARNET_2_WIND2 | Karen Avenue Wind Farm | GEN | 2015-08-05 | 2015 | WIND | WIND |  | 11.7 | 12 | SCE | NQC | FC | 2.07 | 2.2 | 1.93 | 1.85 | 1.97 | 1.8 | 1.68 | 1.27 | 1.32 | 1.22 | 1.64 | 1.99
GARNET_2_WIND3 | San Gorgonio East | GEN | 2016-02-05 | 2016 | WIND | WIND |  | 12.6 | 12.6 | SCE | NQC | FC | 2.23 | 2.37 | 2.08 | 1.99 | 2.12 | 1.94 | 1.81 | 1.37 | 1.42 | 1.31 | 1.77 | 2.15
GARNET_2_WIND4 | Windustries | GEN | 2015-12-10 | 2015 | WIND | WIND |  | 9.8 | 9.8 | SCE | NQC | FC | 1.73 | 1.84 | 1.62 | 1.55 | 1.65 | 1.51 | 1.4 | 1.07 | 1.1 | 1.02 | 1.38 | 1.67
GARNET_2_WIND5 | Eastwind | GEN | 2016-03-01 | 2016 | WIND | WIND |  | 3 | 3 | SCE | NQC | FC | 0.53 | 0.56 | 0.5 | 0.47 | 0.5 | 0.46 | 0.43 | 0.33 | 0.34 | 0.31 | 0.42 | 0.51
GASKW1_2_GW1SR1 | Gaskell West 1 | GEN | 2018-03-06 | 2018 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
GASKW1_2_GW2BT1 | Gaskell West 2 BESS | GEN | 2023-05-05 | 2023 | LESR | OTHER |  | 20 | 20 | SCE | NQC | ID | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
GASKW1_2_GW2SR1 | Gaskell West 2a | GEN | 2023-05-05 | 2023 | SUN | PHOTO VOLTAIC |  | 16 | 16 | SCE | NQC | ID | 0.04 | 0.35 | 0.42 | 0.56 | 0.83 | 1.71 | 1.86 | 1.58 | 1.37 | 0.88 | 0.62 | 0.31
GASKW1_2_GW2SR2 | Gaskell West 2b | GEN | 2023-05-05 | 2023 | SUN | PHOTO VOLTAIC |  | 29 | 29 | SCE | NQC | ID | 0.07 | 0.64 | 0.76 | 1.01 | 1.51 | 3.09 | 3.37 | 2.86 | 2.49 | 1.59 | 1.13 | 0.57
GASKW1_2_GW3SR1 | Gaskell West 3 | GEN | 2023-05-05 | 2023 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | ID | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
GASKW1_2_GW4SR1 | Gaskell West 4 | GEN | 2023-05-05 | 2023 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | ID | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
GASKW1_2_GW5SR1 | Gaskell West 5 | GEN | 2023-05-05 | 2023 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | ID | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
GATES_2_SOLAR | Gates Solar Station | GEN | 2013-06-24 | 2013 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
GATES_2_WSOLAR | West Gates Solar Station | GEN | 2013-06-24 | 2013 | SUN | PHOTO VOLTAIC |  | 10 | 10 | PGAE | NQC | FC | 0.04 | 0.3 | 0.35 | 0.44 | 0.64 | 1.31 | 1.44 | 1.24 | 1.11 | 0.74 | 0.57 | 0.35
GATEWY_2_GESBT1 | Gateway Energy Storage | GEN | 2020-09-16 | 2020 | LESR | OTHER |  | 250 | 250 | SDGE | NQC | FC | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
GATWAY_2_CTGA | Gateway CTG A | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 203.1 | 203.1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GATWAY_2_CTGB | Gateway CTG B | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 203.1 | 203.1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GATWAY_2_PL1X3 | GATEWAY GENERATING STATION | GEN | 2009-01-06 | 2009 | NATURAL GAS | COMBINED CYCLE |  | 585 | 0 | PGAE | NQC | FC | 546 | 548 | 545 | 531 | 519 | 504 | 494 | 500 | 504 | 519 | 538 | 546
GATWAY_2_STGC | Gateway STG C | GEN | 0 |  | NATURAL GAS | STEAM |  | 213.4 | 213.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GENESI_2_STG | Genesis Station | GEN | 2013-11-27 | 2013 | SUN | STEAM |  | 250 | 0 | SCE | NQC | FC | 0.3 | 4.48 | 6.12 | 8.53 | 12.8 | 26.02 | 28.21 | 23.89 | 20.48 | 12.88 | 8.4 | 2.46
GENESI_2_STG1 | Genesis McCoy Solar Project | GEN | 0 |  | SUN | STEAM |  | 140 | 140 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GENESI_2_STG2 | Genesis McCoy Solar Project | GEN | 0 |  | SUN | STEAM |  | 140 | 140 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GEYS11_7_UNIT11 | GEYSERS UNIT 11 (HEALDSBURG) | GEN | 1975-01-01 | 1975 | GEOTHERMAL | STEAM |  | 86.8 | 85 | PGAE | NQC | FC | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
GEYS12_7_UNIT12 | GEYSERS UNIT 12 (HEALDSBURG) | GEN | 1979-01-01 | 1979 | GEOTHERMAL | STEAM |  | 57 | 77 | PGAE | NQC | FC | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
GEYS13_7_UNIT13 | GEYSERS UNIT 13 (HEALDSBURG) | GEN | 1980-01-01 | 1980 | GEOTHERMAL | STEAM |  | 73 | 102 | PGAE | NQC | FC | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
GEYS14_7_UNIT14 | GEYSERS UNIT 14 (HEALDSBURG) | GEN | 1980-01-01 | 1980 | GEOTHERMAL | STEAM |  | 70 | 74.4 | PGAE | NQC | FC | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
GEYS16_7_UNIT16 | GEYSERS UNIT 16 (HEALDSBURG) | GEN | 1985-01-01 | 1985 | GEOTHERMAL | STEAM |  | 63 | 119.9 | PGAE | NQC | FC | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
GEYS17_7_UNIT17 | GEYSERS UNIT 17 (HEALDSBURG) | GEN | 1982-01-01 | 1982 | GEOTHERMAL | STEAM |  | 75.5 | 84 | PGAE | NQC | FC | 75.5 | 75.5 | 75.5 | 75.5 | 75.5 | 75.5 | 75.5 | 75.5 | 75.5 | 75.5 | 75.5 | 75.5
GEYS18_7_UNIT18 | GEYSERS UNIT 18 (HEALDSBURG) | GEN | 1983-01-01 | 1983 | GEOTHERMAL | STEAM |  | 72 | 119.9 | PGAE | NQC | FC | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
GEYS20_7_UNIT20 | GEYSERS UNIT 20 (HEALDSBURG) | GEN | 1985-01-01 | 1985 | GEOTHERMAL | STEAM |  | 50 | 84 | PGAE | NQC | FC | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
GIFENS_6_BUGSL1 | Burford Giffen | GEN | 2017-06-16 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
GIFFEN_6_SOLAR | Giffen Solar Station | GEN | 2012-07-25 | 2012 | SUN | PHOTO VOLTAIC |  | 10 | 20 | PGAE | NQC | FC | 0.04 | 0.3 | 0.35 | 0.44 | 0.64 | 1.31 | 1.44 | 1.24 | 1.11 | 0.74 | 0.57 | 0.35
GIFFEN_6_SOLAR1 | Aspiration Solar G | GEN | 2017-09-15 | 2017 | SUN | PHOTO VOLTAIC |  | 9 | 9 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GILROY_1_CT1 | GILROY COGEN - UNIT 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 95 | 95 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GILROY_1_ST2 | GILROY COGEN - UNIT 2 | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 45 | 45 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GILROY_1_UNIT | GILROY COGEN AGGREGATE | GEN | 1987-01-01 | 1987 | NATURAL GAS | COMBINED CYCLE |  | 120 | 0 | PGAE | NQC | FC | 120 | 120 | 120 | 120 | 115 | 115 | 115 | 115 | 115 | 120 | 120 | 120
GILRPP_1_PL1X2 | GILROY ENERGY CENTER UNITS 1&2 AGGREGATE | GEN | 2002-01-29 | 2002 | NATURAL GAS | COMBUSTION TURBINE |  | 95.2 | 0 | PGAE | NQC | FC | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2
GILRPP_1_PL3X4 | GILROY ENERGY CENTER, UNIT #3 | GEN | 2002-02-28 | 2002 | NATURAL GAS | COMBUSTION TURBINE |  | 46.2 | 49.9 | PGAE | NQC | FC | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2
GILRPP_1_UNIT 1 | Gilroy Energy Center Unit 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49.9 | 49.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GILRPP_1_UNIT 2 | Gilroy Energy Center Unit 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49.9 | 49.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GLDFGR_6_SOLAR1 | Portal Ridge B | GEN | 2017-02-15 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
GLDFGR_6_SOLAR2 | Portal Ridge C | GEN | 2017-02-14 | 2017 | SUN | PHOTO VOLTAIC |  | 11.4 | 11.4 | SCE | NQC | FC | 0.05 | 0.34 | 0.4 | 0.5 | 0.73 | 1.49 | 1.64 | 1.41 | 1.27 | 0.84 | 0.65 | 0.4
GLDTWN_6_COLUM3 | Columbia 3 | GEN | 2013-12-10 | 2013 | SUN | PHOTO VOLTAIC |  | 10 | 10 | SCE | NQC | FC | 0.04 | 0.3 | 0.35 | 0.44 | 0.64 | 1.31 | 1.44 | 1.24 | 1.11 | 0.74 | 0.57 | 0.35
GLDTWN_6_SOLAR | Rio Grande | GEN | 2013-11-18 | 2013 | SUN | PHOTO VOLTAIC |  | 5 | 5 | SCE | NQC | FC | 0.02 | 0.15 | 0.18 | 0.22 | 0.32 | 0.66 | 0.72 | 0.62 | 0.56 | 0.37 | 0.29 | 0.18
GLNARM_2_UNIT 5 | Glenarm Turbine 5 | GEN | 2016-12-20 | 2016 | NATURAL GAS | COMBINED CYCLE |  | 65.81 | 71 | SCE | NQC | PD | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
GLNARM_7_UNIT 1 | GLEN ARM UNIT 1 | GEN | 1976-01-01 | 1976 | NATURAL GAS | COMBUSTION TURBINE |  | 22.13 | 30.6 | SCE | NQC | FC | 22.13 | 22.13 | 22.13 | 22.13 | 22.13 | 22.13 | 22.13 | 22.13 | 22.13 | 22.13 | 22.13 | 22.13
GLNARM_7_UNIT 2 | GLEN ARM UNIT 2 | GEN | 1976-01-01 | 1976 | NATURAL GAS | COMBUSTION TURBINE |  | 22.38 | 30.6 | SCE | NQC | FC | 22.38 | 22.38 | 22.38 | 22.38 | 22.38 | 22.38 | 22.38 | 22.38 | 22.38 | 22.38 | 22.38 | 22.38
GLNARM_7_UNIT 3 | GLEN ARM UNIT 3 | GEN | 2004-01-08 | 2004 | NATURAL GAS | COMBUSTION TURBINE |  | 44.83 | 47.3 | SCE | NQC | FC | 44.83 | 44.83 | 44.83 | 44.83 | 44.83 | 44.83 | 44.83 | 44.83 | 44.83 | 44.83 | 44.83 | 44.83
GLNARM_7_UNIT 4 | GLEN ARM UNIT 4 | GEN | 2004-01-08 | 2004 | NATURAL GAS | COMBUSTION TURBINE |  | 42.42 | 47.3 | SCE | NQC | FC | 42.42 | 42.42 | 42.42 | 42.42 | 42.42 | 42.42 | 42.42 | 42.42 | 42.42 | 42.42 | 42.42 | 42.42
GLOW_6_SOLAR | Antelope Power Plant | GEN | 2013-03-25 | 2013 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GOLETA_2_GE2BT3 | Goleta Energy Storage | GEN | 2024-01-06 | 2024 | LESR | OTHER |  | 60 | 60 | SCE | NQC | FC |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
GOLETA_2_QF | GOLETA QFS | GEN | 1986-01-01 | 1986 | OTHER | OTHER |  | 0.25 | 0.5 | SCE | NQC | FC | 0.02 | 0.05 | 0.05 | 0.08 | 0.11 | 0.11 | 0.12 | 0.11 | 0.11 | 0.09 | 0.05 | 0.03
GOLETA_2_VALBT1 | Vallecito Energy Storage | GEN | 2021-02-04 | 2021 | LESR | OTHER |  | 10 | 10 | SCE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
GOLETA_6_ELLWOD | ELLWOOD ENERGY SUPPORT FACILITY | GEN | 1998-04-29 | 1998 | NATURAL GAS | COMBUSTION TURBINE |  | 54 | 56 | SCE | NQC | FC | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
GOLETA_6_EXGEN | EXXON COMPANY USA | GEN | 1993-08-19 | 1993 | OTHER | 0 |  | 48.2 | 48.2 | SCE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GOLETA_6_TR2BM2 | Tajiguas Biogas Engines | GEN | 2022-06-24 | 2022 | BIOGAS | RECIPROCATING ENGINE |  | 1.99 | 1.99 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GONZLS_6_UNIT | Johnson Canyon Landfill | GEN | 2013-07-08 | 2013 | BIOGAS | RECIPROCATING ENGINE |  | 1.42 | 1.4 | PGAE | NQC | FC | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42
GOOSLK_1_SOLAR1 | Goose Lake | GEN | 2015-05-23 | 2015 | SUN | PHOTO VOLTAIC |  | 12 | 12 | PGAE | NQC | FC | 0.05 | 0.36 | 0.42 | 0.53 | 0.77 | 1.57 | 1.73 | 1.49 | 1.33 | 0.89 | 0.68 | 0.42
GRADYW_5_GDYWD1 | Grady Wind | TG | 2019-08-01 | 2019 | WIND | WIND |  | 200 | 220.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRIDLY_6_SOLAR | GRIDLEY MAIN TWO | GEN | 2013-04-01 | 2013 | SUN | PHOTO VOLTAIC |  | 2.5 | 2.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRIFFI_2_LSPDYN | Griffith Energy | TG | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 570 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRIZLY_1_UNIT 1 | GRIZZLY HYDRO | GEN | 1993-01-01 | 1993 | WATER | HYDRO |  | 20 | 20 | PGAE | NQC | FC | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82 | 5.82
GRNITE_6_ESCBT1 | EnerSmart El Cajon | GEN | 0 |  | LESR | OTHER |  | 3 | 3 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRNLF1_1_PL1X2 | Greenleaf 1 | GEN | 2022-06-24 | 2022 | NATURAL GAS | COMBUSTION TURBINE | Yes | 60 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRNLF1_1_UNITA | Greenleaf 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 37 | 37 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRNLF1_1_UNITB | Greenleaf 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 37 | 37 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GRNLF2_1_UNIT | GREENLEAF II COGEN | GEN | 2020-06-01 | 2020 | NATURAL GAS | COMBUSTION TURBINE |  | 49.2 | 63.8 | PGAE | NQC | FC | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2 | 49.2
GRNVLY_7_SCLAND | SANTA CRUZ LANDFILL GENERATING PLANT | GEN | 2006-02-02 | 2006 | BIOGAS | RECIPROCATING ENGINE |  | 3.04 | 3.6 | PGAE | NQC | FC | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04
GRSCRK_6_BGCKWW | BIG CREEK WATER WORKS - CEDAR FLAT | GEN | 1987-01-01 | 1987 | WATER | HYDRO |  | 5 | 5 | PGAE | NQC | FC | 0.45 | 1.19 | 0.97 | 1.42 | 1.1 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0.02
GRZZLY_1_BERKLY | Berkeley Cogeneration | GEN | 2018-02-20 | 2018 | NATURAL GAS | COMBINED CYCLE |  | 26.35 | 32.5 | PGAE | NQC | FC | 0.43 | 7.57 | 0.22 | 2.81 | 0.67 | 0.4 | 0.33 | 0.31 | 0 | 0 | 0 | 0
GUERNS_6_HD3BM3 | Hanford Digester Genset 3 | GEN | 2019-07-01 | 2019 | BIOGAS | RECIPROCATING ENGINE |  | 1 | 1.1 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GUERNS_6_SOLAR | Guernsey Solar Station | GEN | 2013-09-18 | 2013 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
GUERNS_6_VH2BM1 | Hanford Digester Genset 2 | GEN | 2019-07-01 | 2019 | BIOGAS | RECIPROCATING ENGINE |  | 1 | 1.02 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GWFPWR_1_CT 1 | HEP PEAKER PLANT UNIT 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 50 | 50 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GWFPWR_1_CT 2 | HEP PEAKER PLANT UNIT 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 50 | 50 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GWFPWR_1_UNITS | Hanford Peaker Plant | GEN | 2001-08-27 | 2001 | NATURAL GAS | COMBUSTION TURBINE |  | 98.46 | 0 | PGAE | NQC | FC | 98.46 | 98.46 | 98.46 | 98.46 | 98.46 | 98.46 | 98.46 | 98.46 | 98.46 | 98.46 | 98.46 | 98.46
GYS5X6_7_UNIT 5 | Geysers Unit 5 | GEN | 0 |  | GEOTHERMAL | STEAM |  | 55 | 55 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GYS5X6_7_UNIT 6 | Geysers Unit 6 | GEN | 0 |  | GEOTHERMAL | STEAM |  | 55 | 55 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GYS5X6_7_UNITS | GEYSERS UNITS 5 & 6 AGGREGATE | GEN | 1971-01-01 | 1971 | GEOTHERMAL | STEAM |  | 98.43 | 0 | PGAE | NQC | FC | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
GYS7X8_7_UNIT 7 | Geysers Unit 7 | GEN | 0 |  | GEOTHERMAL | STEAM |  | 55 | 55 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GYS7X8_7_UNIT 8 | Geysers Unit 8 | GEN | 0 |  | GEOTHERMAL | STEAM |  | 55 | 55 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GYS7X8_7_UNITS | GEYSERS UNITS 7 & 8 AGGREGATE | GEN | 1972-01-01 | 1972 | GEOTHERMAL | STEAM |  | 95.8 | 0 | PGAE | NQC | FC | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8
GYSRVL_7_WSPRNG | Warm Springs Hydro | GEN | 1988-12-22 | 1988 | WATER | HYDRO |  | 3.75 | 3.8 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HAASPH_7_PL1X2 | HAAS PH UNIT 1 & 2 AGGREGATE | GEN | 1958-01-01 | 1958 | WATER | HYDRO |  | 144 | 0 | PGAE | NQC | FC | 115.2 | 115.2 | 115.2 | 115.2 | 118.2 | 139.2 | 144 | 144 | 129.6 | 129.6 | 57.6 | 115.2
HAASPH_7_UNIT 1 | HAAS PH UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 72 | 72 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HAASPH_7_UNIT 2 | HAAS PH UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 72 | 72 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HALSEY_6_UNIT | HALSEY HYDRO | GEN | 1916-01-01 | 1916 | WATER | HYDRO |  | 13.5 | 13.5 | PGAE | NQC | FC | 1.96 | 2.8 | 3.28 | 4.2 | 4.8 | 4.33 | 5.92 | 5.52 | 4.16 | 0 | 0 | 1.78
HAMLIN_1_BLDSB1 | Baldy Mesa Hybrid | GEN | 0 |  | HYBD | PHOTO VOLTAIC |  | 150 | 150 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HAMLIN_1_BMSBT2 | Baldy Mesa SP | GEN | 0 |  | HYBD | PHOTO VOLTAIC |  | 50 | 50 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HARBGN_7_UNIT 1 | Harbor Cogen Unit 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 82.3 | 82.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HARBGN_7_UNIT 2 | Harbor Cogen Unit 2 | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 13.6 | 13.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HARBGN_7_UNIT 3 | Harbor Cogen Unit 3 | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 11.5 | 11.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HARBGN_7_UNITS | HARBOR COGEN COMBINED CYCLE | GEN | 2001-06-14 | 2001 | NATURAL GAS | COMBINED CYCLE |  | 109.01 | 0 | SCE | NQC | FC | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
HATCR1_7_UNIT | Hat Creek #1 | GEN | 1921-01-01 | 1921 | WATER | HYDRO |  | 8.5 | 8.5 | PGAE | NQC | FC | 4.13 | 3.65 | 3.51 | 2.72 | 2.47 | 2.63 | 2.58 | 2.42 | 2.31 | 2.75 | 2.84 | 3.33
HATCR2_7_UNIT | Hat Creek #2 | GEN | 1921-01-01 | 1921 | WATER | HYDRO |  | 8.5 | 8.5 | PGAE | NQC | FC | 3.98 | 4.81 | 4.19 | 2.97 | 2.87 | 3.04 | 2.81 | 2.61 | 2.26 | 2.76 | 1.49 | 1.07
HATLOS_6_BWDHY1 | Bidwell Ditch | GEN | 2017-06-29 | 2017 | WATER | HYDRO |  | 2 | 2 | PGAE | NQC | FC | 1.38 | 1.38 | 1.38 | 1.37 | 1.35 | 1.23 | 1.31 | 1.28 | 1.28 | 1.31 | 1.32 | 1.28
HATLOS_6_LSCRK | Lost Creek 1 & 2 Hydro Conversion | GEN | 1989-06-15 | 1989 | WATER | HYDRO |  | 1.7 | 1.7 | PGAE | NQC | FC | 0.98 | 0.97 | 0.97 | 0.96 | 0.94 | 0.85 | 0.9 | 0.87 | 0.87 | 0.88 | 0.9 | 0.87
HATRDG_2_WIND | Hatchet Ridge Wind Farm | GEN | 2010-11-19 | 2010 | WIND | WIND |  | 102 | 102 | PGAE | NQC | FC | 33.49 | 35.94 | 32.05 | 33.86 | 35.03 | 25.84 | 22.98 | 21.58 | 22.16 | 18.57 | 23.46 | 29.99
HAYPRS_6_HAYHD1 | Haypress Lower | GEN | 2021-03-03 | 2021 | WATER | HYDRO |  | 5.8 | 6.1 | PGAE | NQC | FC | 1.85 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8
HAYPRS_6_HAYHD2 | Haypress Middle | GEN | 2021-04-08 | 2021 | WATER | HYDRO |  | 6.7 | 8.7 | PGAE | NQC | FC | 2.13 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
HELMPG_7_UNIT 1 | HELMS PUMP-GEN UNIT 1 | GEN | 1984-01-01 | 1984 | WATER | PUMPED STORAGE |  | 407 | 407 | PGAE | NQC | FC | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 407
HELMPG_7_UNIT 2 | HELMS PUMP-GEN UNIT 2 | GEN | 1984-01-01 | 1984 | WATER | PUMPED STORAGE |  | 407 | 407 | PGAE | NQC | FC | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 407
HELMPG_7_UNIT 3 | HELMS PUMP-GEN UNIT 3 | GEN | 1984-01-01 | 1984 | WATER | PUMPED STORAGE |  | 404 | 404 | PGAE | NQC | FC | 404 | 404 | 404 | 404 | 404 | 404 | 404 | 404 | 404 | 404 | 404 | 404
HENRTA_6_ACDSR3 | Avenal Cutoff Dac Spring Solar | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 3 | 3 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HENRTA_6_HDEBT1 | Henrietta D Energy Storage | GEN | 2021-11-04 | 2021 | LESR | OTHER |  | 10 | 10 | PGAE | NQC | ID | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
HENRTA_6_SOLAR1 | Lemoore 1 | GEN | 2016-01-29 | 2016 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | ID | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
HENRTA_6_SOLAR2 | Westside Solar Power PV1 | GEN | 2016-05-07 | 2016 | SUN | PHOTO VOLTAIC |  | 2 | 2 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HENRTA_6_UNITA1 | GWF HENRIETTA PEAKER PLANT UNIT 1 | GEN | 2002-07-01 | 2002 | NATURAL GAS | COMBUSTION TURBINE |  | 49.98 | 50 | PGAE | NQC | FC | 49.98 | 49.98 | 49.98 | 49.98 | 49.98 | 49.98 | 49.98 | 49.98 | 49.98 | 49.98 | 49.98 | 49.98
HENRTA_6_UNITA2 | GWF HENRIETTA PEAKER PLANT UNIT 2 | GEN | 2002-07-01 | 2002 | NATURAL GAS | COMBUSTION TURBINE |  | 49.42 | 50 | PGAE | NQC | FC | 49.42 | 49.42 | 49.42 | 49.42 | 49.42 | 49.42 | 49.42 | 49.42 | 49.42 | 49.42 | 49.42 | 49.42
HENRTS_1_SOLAR | Henrietta Solar Project | GEN | 2016-08-19 | 2016 | SUN | PHOTO VOLTAIC |  | 100 | 102 | PGAE | NQC | FC | 0.4 | 3 | 3.5 | 4.4 | 6.4 | 13.1 | 14.4 | 12.4 | 11.1 | 7.4 | 5.7 | 3.5
HERDLN_6_BYHSR1 | Byron Highway Solar | GEN | 2022-11-23 | 2022 | SUN | PHOTO VOLTAIC |  | 5 | 5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HIDSRT_2_UNITS | HIGH DESERT POWER PROJECT AGGREGATE | GEN | 2003-04-21 | 2003 | NATURAL GAS | COMBINED CYCLE |  | 850 | 0 | SCE | NQC | FC | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850 | 850
HIDSRT_7_CTG1 | HIGH DESERT COMBUSTION TURBINE UNIT 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 177.3 | 177.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HIDSRT_7_CTG2 | HIGH DESERT COMBUSTION TURBINE UNIT 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 177.3 | 177.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HIDSRT_7_CTG3 | HIGH DESERT COMBUSTION TURBINE UNIT 3 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 177.3 | 177.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HIDSRT_7_STG | HIGH DESERT STEAM TURBINE | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 323 | 323 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HIGGNS_1_COMBIE | Combie South | GEN | 2020-05-05 | 2020 | WATER | HYDRO |  | 1.5 | 1.5 | PGAE | NQC | FC | 0.88 | 0.68 | 0.53 | 0.76 | 0.65 | 0.24 | 0.12 | 0.01 | 0.04 | 0.04 | 0.67 | 0.78
HIGGNS_7_QFUNTS | HIGGNS_7_QFUNTS | GEN | 0 |  | WATER | HYDRO |  | 0.5 | 0.3 | PGAE | NQC | FC | 0.11 | 0.03 | 0.02 | 0.11 | 0.21 | 0.24 | 0.24 | 0.24 | 0.23 | 0.1 | 0.05 | 0.08
HIGHDS_2_H5SBT1 | High 5 Solar BESS | GEN | 2021-12-08 | 2021 | LESR | OTHER |  | 50 | 50 | SCE | NQC | FC | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
HIGHDS_2_H5SSR1 | High 5 Solar | GEN | 2021-08-09 | 2021 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE | NQC | FC | 0.25 | 2.13 | 2.58 | 3.38 | 5.09 | 10.45 | 11.36 | 9.47 | 8.28 | 5.27 | 3.52 | 1.8
HILAND_7_YOLOWD | CLEAR LAKE UNIT 1 | GEN | 1985-09-07 | 1985 | WATER | HYDRO |  | 3.75 | 3.8 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HINSON_6_LBECH1 | Long Beach Unit 1 | GEN | 2007-08-01 | 2007 | NATURAL GAS | FTUR |  | 63 | 70 | SCE | NQC | FC | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
HINSON_6_LBECH2 | Long Beach Unit 2 | GEN | 2007-08-01 | 2007 | NATURAL GAS | FTUR |  | 63 | 70 | SCE | NQC | FC | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
HINSON_6_LBECH3 | Long Beach Unit 3 | GEN | 2007-08-01 | 2007 | NATURAL GAS | FTUR |  | 63 | 70 | SCE | NQC | FC | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
HINSON_6_LBECH4 | Long Beach Unit 4 | GEN | 2007-08-01 | 2007 | NATURAL GAS | FTUR |  | 63 | 70 | SCE | NQC | FC | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
HINSON_6_SERRGN | Southeast Resource Recovery | GEN | 1988-01-01 | 1988 | WASTE TO POWER | STEAM |  | 34 | 41.3 | SCE | NQC | FC | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34
HNTGBH_2_PL1X3 | Huntington Beach Energy | GEN | 2020-02-04 | 2020 | NATURAL GAS | COMBINED CYCLE |  | 673.8 | 0 | SCE | NQC | FC | 673.8 | 673.8 | 673.8 | 673.8 | 673.8 | 673.8 | 673.8 | 673.8 | 673.8 | 673.8 | 673.8 | 673.8
HNTGBH_7_CTG1A | HNTGBH_7_CTG1A | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 234.5 | 234.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HNTGBH_7_CTG1B | HNTGBH_7_CTG1B | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 234.5 | 234.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HNTGBH_7_STG1S | HNTGBH_7_STG1S | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 241.5 | 241.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HNTGBH_7_UNIT 2 | HUNTINGTON BEACH GEN STA. UNIT 2 | GEN | 1998-05-05 | 1998 | NATURAL GAS | STEAM | Yes | 226.84 | 226 | SCE | NQC | FC | 226.84 | 226.84 | 226.84 | 226.84 | 226.84 | 226.84 | 226.84 | 226.84 | 226.84 | 226.84 | 226.84 | 226.84
HOLGAT_1_BORAX | U.S. Borax, Unit 1 | GEN | 1984-06-01 | 1984 | OTHER | 0 |  | 48.2 | 48.2 | SCE | NQC | FC | 17.17 | 15.12 | 13.09 | 4.87 | 7.33 | 13.88 | 12.08 | 11.68 | 13.9 | 14.74 | 15.84 | 14.94
HOLSTR_1_SOLAR | San Benito Smart Park | GEN | 2014-06-16 | 2014 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOLSTR_1_SOLAR2 | Hollister Solar | GEN | 2015-04-17 | 2015 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | FC | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
HOOV_2_ANAPT | Hoover Power Plant | TG | 2022-12-15 | 2022 | WATER | HYDRO |  | 40.39 | 41 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOOVER_2_MWDPT | HOOVER MWD | TG | 2023-01-25 | 2023 | WATER | HYDRO |  | 249 | 250 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOOVER_2_SCEPT | Hoover DAM - SCE Share | TG | 2023-01-25 | 2023 | WATER | HYDRO |  | 287 | 288 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOOVER_2_VEAPT | HOOVER VEA | TG | 2023-01-25 | 2023 | WATER | HYDRO |  | 16 | 18 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HUMBPP_1_UNITS3 | Humboldt Bay Generating Station 3 | GEN | 2010-09-29 | 2010 | NATURAL GAS | RECIPROCATING ENGINE |  | 65.08 | 83.2 | PGAE | NQC | FC | 65.08 | 65.08 | 65.08 | 65.08 | 65.08 | 65.08 | 65.08 | 65.08 | 65.08 | 65.08 | 65.08 | 65.08
HUMBPP_6_UNITS | Humboldt Bay Generating Station 1 | GEN | 2010-09-29 | 2010 | NATURAL GAS | RECIPROCATING ENGINE |  | 97.62 | 0 | PGAE | NQC | FC | 97.62 | 97.62 | 97.62 | 97.62 | 97.62 | 97.62 | 97.62 | 97.62 | 97.62 | 97.62 | 97.62 | 97.62
HUMBPP_6_UNITS1 | Humboldt Bay Generating Station 1 | GEN | 0 |  | NATURAL GAS | RECIPROCATING ENGINE |  | 83.2 | 83.2 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HUMBPP_6_UNITS2 | Humboldt Bay Generating Station 2 | GEN | 0 |  | NATURAL GAS | RECIPROCATING ENGINE |  | 83.2 | 83.2 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HURON_6_SOLAR | Huron Solar Station | GEN | 2012-08-30 | 2012 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
HYATT_2_UNIT 1 | Edward Hyatt Gen Unit 1 | GEN | 0 |  | WATER | HYDRO |  | 141.6 | 141.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HYATT_2_UNIT 2 | Edward Hyatt P-G Unit 2 | GEN | 0 |  | WATER | HYDRO |  | 132.2 | 132.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HYATT_2_UNIT 3 | Edward Hyatt Gen Unit 3 | GEN | 0 |  | WATER | HYDRO |  | 141.6 | 141.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HYATT_2_UNIT 4 | Edward Hyatt P-G Unit 4 | GEN | 0 |  | WATER | HYDRO |  | 132.2 | 132.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HYATT_2_UNIT 5 | Edward Hyatt Gen Unit 5 | GEN | 0 |  | WATER | HYDRO |  | 141.6 | 141.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HYATT_2_UNIT 6 | Edward Hyatt P-G Unit 6 | GEN | 0 |  | WATER | HYDRO |  | 132.2 | 132.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HYTTHM_2_UNITS | HYATT-THERMALITO PUMP-GEN (AGGREGATE) | GEN | 1968-01-01 | 1968 | WATER | HYDRO |  | 933.1 | 0 | PGAE | NQC | FC | 56.34 | 149.29 | 371.98 | 238.3 | 220.41 | 291.85 | 632.49 | 567.92 | 501.49 | 283.45 | 199.11 | 303.1
IGNACO_1_QF | SMALL QF AGGREGATION - VALLEJO/DINSMORE | GEN | 1985-01-01 | 1985 | OTHER | OTHER |  | 0.5 | 1 | PGAE | NQC | FC | 0.01 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
INDIGO_1_UNIT 1 | INDIGO PEAKER UNIT 1 | GEN | 2001-09-19 | 2001 | NATURAL GAS | COMBUSTION TURBINE |  | 45.3 | 45.3 | SCE | NQC | FC | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3
INDIGO_1_UNIT 2 | INDIGO PEAKER UNIT 2 | GEN | 2001-09-19 | 2001 | NATURAL GAS | COMBUSTION TURBINE |  | 45.3 | 45.3 | SCE | NQC | FC | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3
INDIGO_1_UNIT 3 | INDIGO PEAKER UNIT 3 | GEN | 2001-09-19 | 2001 | NATURAL GAS | COMBUSTION TURBINE |  | 45.3 | 45.3 | SCE | NQC | FC | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3
INDVLY_1_UNITS | Indian Valley Hydro | GEN | 1983-09-15 | 1983 | WATER | HYDRO |  | 3.01 | 5 | PGAE | NQC | FC | 0 | 0 | 0.53 | 1.03 | 1.01 | 0.71 | 0.62 | 0.61 | 0.56 | 0.02 | 0 | 0
INTKEP_2_HOLM 1 | HOLM HYDRO UNIT 1 | GEN | 0 |  | 0 | 0 |  | 83 | 83 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INTKEP_2_HOLM 2 | HOLM HYDRO UNIT 2 | GEN | 0 |  | 0 | 0 |  | 83 | 83 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INTKEP_2_KIRKW1 | KIRKWOOD HYDRO UNIT 1 | GEN | 0 |  | 0 | 0 |  | 45 | 45 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INTKEP_2_KIRKW2 | KIRKWOOD HYDRO UNIT 2 | GEN | 0 |  | 0 | 0 |  | 47.8 | 47.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INTKEP_2_KIRKW3 | KIRKWOOD HYDRO UNIT 3 | GEN | 0 |  | 0 | 0 |  | 45 | 45 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INTKEP_2_UNITS | CCSF Hetch_Hetchy Hydro Aggregate | GEN | 2006-07-01 | 2006 | WATER | HYDRO |  | 405 | 0 | PGAE | NQC | FC | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 239 | 300 | 307 | 307
INTMNT_3_ANAHEIM | Intermountain Power Project | TG | 0 |  | COAL | STEAM |  | 234 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INTMNT_3_PASADENA | Intermountain Power Project | TG | 0 |  | COAL | STEAM |  | 107 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INTMNT_3_RIVERSIDE | IPPDYN | TG | 0 |  | COAL | STEAM |  | 136 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INTTRB_6_UNIT | International Turbine Research | GEN | 0 |  | WIND | WIND |  | 18.4 | 21.3 | PGAE | NQC | FC | 6.04 | 6.48 | 5.78 | 6.11 | 6.32 | 4.66 | 4.15 | 3.89 | 4 | 3.35 | 4.23 | 5.41
IVANPA_1_UNIT1 | Ivanpah 1 | GEN | 2013-11-17 | 2013 | SUN | STEAM |  | 126 | 126 | SCE | NQC | FC | 0.5 | 3.78 | 4.41 | 5.54 | 8.06 | 16.51 | 18.14 | 15.62 | 13.99 | 9.32 | 7.18 | 4.41
IVANPA_1_UNIT2 | Ivanpah 2 | GEN | 2013-12-30 | 2013 | SUN | STEAM |  | 133 | 133.4 | SCE | NQC | FC | 0.53 | 3.99 | 4.66 | 5.85 | 8.51 | 17.42 | 19.15 | 16.49 | 14.76 | 9.84 | 7.58 | 4.66
IVANPA_1_UNIT3 | Ivanpah 3 | GEN | 2013-12-26 | 2013 | SUN | STEAM |  | 133 | 133.4 | SCE | NQC | FC | 0.53 | 3.99 | 4.66 | 5.85 | 8.51 | 17.42 | 19.15 | 16.49 | 14.76 | 9.84 | 7.58 | 4.66
IVSLR2_2_SM2SR1 | Silver Ridge Mount Signal 2 | GEN | 2019-12-06 | 2019 | SUN | PHOTO VOLTAIC |  | 150 | 150 | SDGE | NQC | FC | 0.6 | 4.5 | 5.25 | 6.6 | 9.6 | 19.65 | 21.6 | 18.6 | 16.65 | 11.1 | 8.55 | 5.25
IVSLRP_2_SOLAR1 | Silver Ridge Mount Signal | GEN | 2013-10-28 | 2013 | SUN | PHOTO VOLTAIC |  | 200 | 200 | SDGE | NQC | FC | 0.8 | 6 | 7 | 8.8 | 12.8 | 26.2 | 28.8 | 24.8 | 22.2 | 14.8 | 11.4 | 7
IVWEST_2_SOLAR1 | Imperial Valley West ( Q # 608) | GEN | 2015-09-30 | 2015 | SUN | PHOTO VOLTAIC |  | 150 | 0 | SDGE | NQC | FC | 0.6 | 4.5 | 5.25 | 6.6 | 9.6 | 19.65 | 21.6 | 18.6 | 16.65 | 11.1 | 8.55 | 5.25
IVWEST_2_SOLR1A | IVWEST_2_SOLR1A | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 75 | 75 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IVWEST_2_SOLR1B | IVWEST_2_SOLR1B | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 75 | 75 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JACMSR_1_JACSR1 | Jacumba Solar Farm | GEN | 2017-07-25 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 19.7 | SDGE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
JANCRK_6_RCABT1 | Redwood Coast Airport Microgrid | GEN | 2021-12-22 | 2021 | HYBD | OTHER |  | 1.75 | 1.8 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JAVASR_1_JAVSR1 | Java Solar | GEN | 2022-11-18 | 2022 | SUN | PHOTO VOLTAIC |  | 13.5 | 14 | PGAE | NQC | ID | 0.05 | 0.41 | 0.47 | 0.59 | 0.86 | 1.77 | 1.94 | 1.67 | 1.5 | 1 | 0.77 | 0.47
JAWBNE_2_NSRWND | North Sky River Wind Project | GEN | 2012-12-08 | 2012 | WIND | WIND |  | 160 | 162 | SCE | NQC | FC | 28.27 | 30.07 | 26.42 | 25.31 | 26.92 | 24.67 | 22.92 | 17.42 | 17.99 | 16.69 | 22.5 | 27.25
JAWBNE_2_SRWND | Sky River Wind Repower A | GEN | 2021-09-01 | 2021 | WIND | WIND |  | 30 | 30 | SCE | NQC | FC | 6.55 | 6.71 | 6.9 | 12.14 | 13.03 | 11.56 | 9.87 | 8.67 | 6.42 | 6.84 | 7.36 | 6.74
JAWBNE_2_SRWWD2 | Sky River Wind Repower B | GEN | 2021-09-17 | 2021 | WIND | WIND |  | 30.2 | 30.2 | SCE | NQC | FC | 5.34 | 5.68 | 4.99 | 4.78 | 5.08 | 4.66 | 4.33 | 3.29 | 3.4 | 3.15 | 4.25 | 5.14
JAYNE_6_WLSLR | Westlands Solar Farm PV 1 | GEN | 2014-02-14 | 2014 | SUN | PHOTO VOLTAIC |  | 18 | 18 | PGAE | NQC | ID | 0.07 | 0.54 | 0.63 | 0.79 | 1.15 | 2.36 | 2.59 | 2.23 | 2 | 1.33 | 1.03 | 0.63
JOANEC_2_ST3BT3 | Santa Ana Storage 3 | GEN | 2023-06-02 | 2023 | LESR | OTHER |  | 40 | 40 | SCE | NQC | FC | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
JOANEC_2_STABT1 | Santa Ana Storage 1 | GEN | 2021-06-11 | 2021 | LESR | OTHER |  | 20 | 20 | SCE | NQC | FC | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
JOANEC_2_STABT2 | Santa Ana Storage 2 | GEN | 2022-06-06 | 2022 | LESR | OTHER |  | 20 | 20 | SCE | NQC | FC | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
JOHANN_2_JOSBT1 | Johanna Storage 1 | GEN | 2021-10-29 | 2021 | LESR | OTHER |  | 10 | 10 | SCE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
JOHANN_2_JOSBT2 | Johanna Storage 2 | GEN | 2021-10-29 | 2021 | LESR | OTHER |  | 10 | 10 | SCE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
JOHANN_2_OCEBT2 | Orange County Energy Storage 2 | GEN | 2021-12-07 | 2021 | LESR | OTHER |  | 9 | 9 | SCE | NQC | FC | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
JOHANN_2_OCEBT3 | Orange County Energy Storage 3 | GEN | 2021-12-07 | 2021 | LESR | OTHER |  | 6 | 6 | SCE | NQC | FC | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
JOHANN_2_T1BBT1 | Titanium 1 BESS | GEN | 0 |  | LESR | OTHER |  | 1.4 | 1.4 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KANSAS_6_SOLAR | RE Kansas South | GEN | 2013-06-06 | 2013 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | ID | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
KEARNY_6_NESBT1 | Kearny North Energy Storage | GEN | 2022-03-10 | 2022 | LESR | OTHER |  | 10 | 10 | SDGE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
KEARNY_6_SESBT2 | Kearny South Energy Storage | GEN | 2022-03-10 | 2022 | LESR | OTHER |  | 10 | 10 | SDGE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
KEKAWK_6_UNIT | STS HYDROPOWER LTD. (KEKAWAKA) | GEN | 1989-12-27 | 1989 | WATER | HYDRO |  | 5.5 | 6 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KELSO_2_GTG6 | Mariposa Energy Project | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49.4 | 49.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KELSO_2_GTG7 | Mariposa Energy Project | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49.4 | 49.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KELSO_2_UNITS | Mariposa Energy | GEN | 2012-10-01 | 2012 | NATURAL GAS | COMBUSTION TURBINE |  | 198.03 | 0 | PGAE | NQC | FC | 198.03 | 198.03 | 198.03 | 198.03 | 198.03 | 198.03 | 198.03 | 198.03 | 198.03 | 198.03 | 198.03 | 198.03
KELSO_3_GTG8 | Mariposa Energy Project | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49.4 | 49.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KELSO_3_GTG9 | Mariposa Energy Project | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49.4 | 49.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KELYRG_6_UNIT | KELLY RIDGE HYDRO | GEN | 1963-01-01 | 1963 | WATER | HYDRO |  | 11 | 11 | PGAE | NQC | FC | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
KERKH2_7_UNIT 1 | KERKHOFF PH 2 UNIT #1 | GEN | 1983-01-01 | 1983 | WATER | HYDRO |  | 153.9 | 153.9 | PGAE | NQC | FC | 7.79 | 22.24 | 36 | 36 | 96.67 | 74.8 | 75.8 | 75 | 75 | 0 | 0 | 4
KERMAN_6_SOLAR1 | Fresno Solar South | GEN | 2015-10-21 | 2015 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KERMAN_6_SOLAR2 | Fresno Solar West | GEN | 2015-10-20 | 2015 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KERNEY_6_FCSSR1 | Fresno Community Solar | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 10 | 10 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KERNFT_1_UNITS | KERN FRONT LIMITED | GEN | 1989-01-07 | 1989 | NATURAL GAS | COMBUSTION TURBINE |  | 52.4 | 60 | PGAE | NQC | FC | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4
KERNRG_1_UNITS | South Belridge Cogen Facility | GEN | 1985-01-01 | 1985 | NATURAL GAS | COMBUSTION TURBINE |  | 55.2 | 69.6 | PGAE | NQC | FC | 0.87 | 0.44 | 0.21 | 0.87 | 0.79 | 0.79 | 0.68 | 0.62 | 0.46 | 0.46 | 0.84 | 0.98
KERRGN_1_UNIT 1 | KERN RIVER HYDRO UNITS 1-4 AGGREGATE | GEN | 1907-01-01 | 1907 | WATER | HYDRO |  | 25.6 | 26.3 | SCE | NQC | FC | 10 | 11.97 | 16.94 | 24.01 | 24 | 23.81 | 21.4 | 15.54 | 8.03 | 8.06 | 8.72 | 9.66
KINGCO_1_KINGBR | Kingsburg Cogen | GEN | 1990-12-05 | 1990 | NATURAL GAS | COMBUSTION TURBINE |  | 34.5 | 34.5 | PGAE | NQC | FC | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5
KINGRV_7_UNIT 1 | KINGS RIVER HYDRO UNIT 1 | GEN | 1962-01-01 | 1962 | WATER | HYDRO |  | 51.2 | 51.2 | PGAE | NQC | FC | 38.98 | 32 | 11.2 | 32 | 11.2 | 40.96 | 39.03 | 40.8 | 42.96 | 40.96 | 40.96 | 40.96
KIRKER_7_KELCYN | KELLER CANYON LANDFILL GEN FACILICITY | GEN | 2009-08-01 | 2009 | BIOGAS | RECIPROCATING ENGINE |  | 3.56 | 3.8 | PGAE | NQC | FC | 3.48 | 3.51 | 3.56 | 3.42 | 3.56 | 3.56 | 3.55 | 3.41 | 3.55 | 3.56 | 3.56 | 3.56
KNGBRD_2_SOLAR1 | Kingbird Solar A | GEN | 2016-04-30 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
KNGBRD_2_SOLAR2 | Kingbird Solar B | GEN | 2016-04-30 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
KNGBRG_1_KBSLR1 | Kingsburg1 | GEN | 2013-12-06 | 2013 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KNGBRG_1_KBSLR2 | Kingsburg2 | GEN | 2013-12-06 | 2013 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KNGCTY_6_UNITA1 | King City Energy Center, Unit 1 | GEN | 2002-01-14 | 2002 | NATURAL GAS | COMBUSTION TURBINE |  | 44.6 | 49.9 | PGAE | NQC | FC | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
KNTSTH_6_SOLAR | Kent South | GEN | 2014-12-24 | 2014 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | ID | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
KNTSTH_6_WALSR1 | Westlands Almond | GEN | 2023-09-26 | 2023 | SUN | PHOTO VOLTAIC |  | 19.88 | 20 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R1BBT1 | Resurgence 1 BESS | GEN | 0 |  | LESR | OTHER |  | 25 | 25 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R1BBT2 | Resurgence 1 BESS | GEN | 0 |  | LESR | OTHER |  | 25 | 25 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R1BBT3 | Resurgence 1 BESS | GEN | 0 |  | LESR | OTHER |  | 25 | 25 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R1BX3 | Resurgence 1 BESS | GEN | 2023-07-01 | 2023 | LESR | OTHER |  | 75 | 0 | SCE | NQC | FC | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
KRAMER_1_R1PSR1 | Resurgence 1 PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 30 | 30 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R1PSR2 | Resurgence 1 PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 30 | 30 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R1PSR3 | Resurgence 1 PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 30 | 30 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R1PX3 | Resurgence 1 PV | GEN | 2023-08-02 | 2023 | SUN | PHOTO VOLTAIC |  | 90 | 0 | SCE | NQC | FC | 0.12 | 1.35 | 1.68 | 2.42 | 3.72 | 7.67 | 8.29 | 6.9 | 5.76 | 3.42 | 2.09 | 0.57
KRAMER_1_R2BBT1 | Resurgence 2 BESS | GEN | 0 |  | LESR | OTHER |  | 20 | 20 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R2BBT2 | Resurgence 2 BESS | GEN | 0 |  | LESR | OTHER |  | 20 | 20 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R2BX2 | Resurgence 2 BESS | GEN | 2023-08-30 | 2023 | LESR | OTHER |  | 40 | 0 | SCE | NQC | FC | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
KRAMER_1_R2PSR1 | Resurgence 2 PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 24 | 24 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R2PSR2 | Resurgence 2 PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 24 | 24 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KRAMER_1_R2PX2 | Resurgence 2 PV | GEN | 2023-09-14 | 2023 | SUN | PHOTO VOLTAIC |  | 48 | 0 | SCE | NQC | FC | 0.06 | 0.72 | 0.9 | 1.29 | 1.98 | 4.09 | 4.42 | 3.68 | 3.07 | 1.83 | 1.11 | 0.3
KRAMER_2_SEGS 9 | Kramer Junction 9 | GEN | 2021-04-23 | 2021 | SUN | STEAM |  | 80 | 92 | SCE | NQC | FC | 0.32 | 2.4 | 2.8 | 3.52 | 5.12 | 10.48 | 11.52 | 9.92 | 8.88 | 5.92 | 4.56 | 2.8
KRNCNY_6_UNIT | KERN CANYON POWERHOUSE | GEN | 2021-06-09 | 2021 | WATER | HYDRO |  | 10.6 | 11.5 | PGAE | NQC | FC | 3.38 | 3.56 | 4.14 | 7.52 | 6.88 | 6.16 | 5.47 | 3.36 | 2.21 | 1.51 | 1.61 | 1.55
KYCORA_6_KMSBT1 | Kearny Mesa Storage | GEN | 2020-02-13 | 2020 | LESR | OTHER |  | 1 | 1 | SDGE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LACIEN_2_VENICE | MWD Venice Hydroelectric Recovery Plant | GEN | 1982-01-01 | 1982 | WATER | HYDRO |  | 9.95 | 10.1 | SCE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LAGBEL_2_CBPBT1 | CALD BESS I | GEN | 0 |  | LESR | OTHER |  | 100 | 100 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LAKHDG_6_UNIT 1 | Lake Hodges Pumped Storage-Unit1 | GEN | 2012-08-26 | 2012 | WATER | PUMPED STORAGE |  | 20 | 20.4 | SDGE | NQC | FC | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LAKHDG_6_UNIT 2 | Lake Hodges Pumped Storage-Unit2 | GEN | 2012-08-26 | 2012 | WATER | PUMPED STORAGE |  | 20 | 20.4 | SDGE | NQC | FC | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LAMONT_1_SOLAR1 | Regulus Solar | GEN | 2014-09-02 | 2014 | SUN | PHOTO VOLTAIC |  | 60 | 60 | PGAE | NQC | FC | 0.24 | 1.8 | 2.1 | 2.64 | 3.84 | 7.86 | 8.64 | 7.44 | 6.66 | 4.44 | 3.42 | 2.1
LAMONT_1_SOLAR2 | Redwood Solar Farm 4 | GEN | 2018-01-06 | 2018 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
LAMONT_1_SOLAR3 | Woodmere Solar Farm | GEN | 2015-12-23 | 2015 | SUN | PHOTO VOLTAIC |  | 14.99 | 15 | PGAE | NQC | FC | 0.06 | 0.45 | 0.52 | 0.66 | 0.96 | 1.96 | 2.16 | 1.86 | 1.66 | 1.11 | 0.85 | 0.52
LAMONT_1_SOLAR4 | Hayworth Solar Farm | GEN | 2015-12-23 | 2015 | SUN | PHOTO VOLTAIC |  | 26.66 | 27 | PGAE | NQC | FC | 6.73 | 10.6 | 12.92 | 16.98 | 18.76 | 19.44 | 18.53 | 17.37 | 11.77 | 9.69 | 6.36 | 4.4
LAMONT_1_SOLAR5 | Redcrest Solar Farm | GEN | 2015-10-30 | 2015 | SUN | PHOTO VOLTAIC |  | 16.66 | 20 | PGAE | NQC | FC | 0.07 | 0.5 | 0.58 | 0.73 | 1.07 | 2.18 | 2.4 | 2.07 | 1.85 | 1.23 | 0.95 | 0.58
LAPLMA_2_UNIT 1 | La Paloma Generating Plant Unit #1 | GEN | 2003-01-10 | 2003 | NATURAL GAS | COMBINED CYCLE |  | 267 | 295 | PGAE | NQC | FC | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267
LAPLMA_2_UNIT 2 | La Paloma Generating Plant Unit #2 | GEN | 2003-03-05 | 2003 | NATURAL GAS | COMBINED CYCLE |  | 266 | 295 | PGAE | NQC | FC | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266
LAPLMA_2_UNIT 3 | La Paloma Generating Plant Unit #3 | GEN | 2003-01-13 | 2003 | NATURAL GAS | COMBINED CYCLE |  | 266 | 295 | PGAE | NQC | FC | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266
LAPLMA_2_UNIT 4 | LA PALOMA GENERATING PLANT, UNIT #4 | GEN | 2003-03-05 | 2003 | NATURAL GAS | COMBINED CYCLE |  | 267 | 295 | PGAE | NQC | FC | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267
LARKSP_6_UNIT 1 | LARKSPUR PEAKER UNIT 1 | GEN | 2001-09-13 | 2001 | NATURAL GAS | COMBUSTION TURBINE |  | 49 | 49 | SDGE | NQC | FC | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
LARKSP_6_UNIT 2 | LARKSPUR PEAKER UNIT 2 | GEN | 2001-09-13 | 2001 | NATURAL GAS | COMBUSTION TURBINE |  | 49 | 49 | SDGE | NQC | FC | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
LAROA2_2_CTG 2S | CENTRAL LA ROSITA II COMBUSTION TURBINE | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 181.5 | 181.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LAROA2_2_STG 2C | CENTRAL LA ROSITA II STEAM TURBINE | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 155 | 155 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LAROA2_2_UNITA1 | LR2 | GEN | 2003-07-22 | 2003 | NATURAL GAS | COMBINED CYCLE |  | 322 | 0 | SDGE | NQC | FC | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322
LASSEN_6_UNITS | Honey Lake Power | GEN | 2017-06-27 | 2017 | BIOMASS | STEAM |  | 30 | 50.4 | PGAE | NQC | FC | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LAWRNC_7_SUNYVL | City of Sunnyvale Unit 1 and 2 | GEN | 1999-01-01 | 1999 | BIOGAS | RECIPROCATING ENGINE |  | 0.3 | 1.6 | PGAE | NQC | FC | 0.11 | 0.04 | 0.07 | 0.14 | 0.16 | 0.13 | 0.12 | 0.15 | 0.13 | 0.07 | 0.09 | 0.18
LCKHT1_2_LH1BT1 | Lockhart Solar BESS 1 | GEN | 0 |  | LESR | OTHER |  | 45 | 45 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LCKHT1_2_LH1SR1 | Lockhart Solar 1 PV | GEN | 2023-07-18 | 2023 | SUN | PHOTO VOLTAIC |  | 85 | 85 | SCE | NQC | ID | 0.34 | 2.55 | 2.98 | 3.74 | 5.44 | 11.14 | 12.24 | 10.54 | 9.44 | 6.29 | 4.84 | 2.98
LCKHT1_2_LH1SR2 | Lockhart Solar 2 | GEN | 2023-07-26 | 2023 | SUN | PHOTO VOLTAIC |  | 75 | 75 | SCE | NQC | ID | 0.3 | 2.25 | 2.63 | 3.3 | 4.8 | 9.83 | 10.8 | 9.3 | 8.32 | 5.55 | 4.28 | 2.63
LEBECS_2_UNITS | Pastoria Energy Facility | GEN | 2005-05-04 | 2005 | NATURAL GAS | COMBINED CYCLE |  | 799.47 | 0 | SCE | NQC | FC | 799.47 | 799.47 | 795 | 785 | 775 | 775 | 775 | 775 | 775 | 785 | 799.47 | 799.47
LEBECS_7_CTG1 | CC Power Block 1 CTG1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 198.9 | 198.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEBECS_7_CTG2 | CC Power Block 1 CTG2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 198.9 | 198.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEBECS_7_CTG4 | CC Power Block 2 CTG4 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 198.9 | 198.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEBECS_7_STG3 | CC Power Block 1 STG3 | GEN | 0 |  | NATURAL GAS | STEAM |  | 184 | 184 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEBECS_7_STG5 | CC Power Block 2 STG5 | GEN | 0 |  | NATURAL GAS | STEAM |  | 92 | 92 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LECEF_1_CGT 1 | LOS ESTEROS ENERGY FACILITY CTG 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49.9 | 49.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LECEF_1_CGT 2 | LOS ESTEROS ENERGY FACILITY CTG 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49.9 | 49.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LECEF_1_CGT 3 | LOS ESTEROS ENERGY FACILITY CTG 3 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49.9 | 49.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LECEF_1_CGT 4 | LOS ESTEROS ENERGY FACILITY CTG 4 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49.9 | 49.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LECEF_1_STG1 | LOS ESTEROS ENERGY FACILITY STG1 | GEN | 0 |  | NATURAL GAS | STEAM |  | 120 | 120 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LECEF_1_UNITS | LOS ESTEROS ENERGY FACILITY AGGREGATE | GEN | 2013-07-31 | 2013 | NATURAL GAS | COMBINED CYCLE |  | 309.84 | 0 | PGAE | NQC | FC | 304 | 304 | 304 | 303 | 303 | 302 | 302 | 299 | 302 | 303 | 303 | 303
LECONT_2_LESBT1 | LeConte Energy Storage | GEN | 2022-09-01 | 2022 | LESR | OTHER |  | 125 | 125 | SDGE | NQC | PD | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
LEPRFD_1_KANSAS | Kansas | GEN | 2014-12-18 | 2014 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
LGHTHP_6_ICEGEN | CARSON COGENERATION | GEN | 1989-12-22 | 1989 | NATURAL GAS | COMBINED CYCLE |  | 48 | 54.7 | SCE | NQC | FC | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LHILLS_6_SOLAR1 | Lost Hills Solar | GEN | 2015-04-10 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
LILIAC_6_SOLAR | Mesa Crest | GEN | 2016-09-17 | 2016 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SDGE | NQC | FC | 0.01 | 0.09 | 0.11 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.11
LITLRK_6_GBCSR1 | Green Beanworks C | GEN | 2018-08-18 | 2018 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE | NQC | FC | 0.01 | 0.09 | 0.11 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.11
LITLRK_6_SEPV01 | Gestamp Solar 1 | GEN | 2012-05-08 | 2012 | SUN | PHOTO VOLTAIC |  | 2 | 2 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LITLRK_6_SOLAR1 | Lancaster Little Rock C | GEN | 2015-01-17 | 2015 | SUN | PHOTO VOLTAIC |  | 5 | 5 | SCE | NQC | FC | 0.02 | 0.15 | 0.18 | 0.22 | 0.32 | 0.66 | 0.72 | 0.62 | 0.56 | 0.37 | 0.29 | 0.18
LITLRK_6_SOLAR2 | Palmdale 18 | GEN | 2016-01-13 | 2016 | SUN | PHOTO VOLTAIC |  | 2 | 2 | SCE | NQC | FC | 0.01 | 0.06 | 0.07 | 0.09 | 0.13 | 0.26 | 0.29 | 0.25 | 0.22 | 0.15 | 0.11 | 0.07
LITLRK_6_SOLAR3 | One Ten Partners | GEN | 2017-09-30 | 2017 | SUN | PHOTO VOLTAIC |  | 2 | 2 | SCE | NQC | FC | 0.01 | 0.06 | 0.07 | 0.09 | 0.13 | 0.26 | 0.29 | 0.25 | 0.22 | 0.15 | 0.11 | 0.07
LITLRK_6_SOLAR4 | Little Rock Pham Solar | GEN | 2016-03-22 | 2016 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE | NQC | FC | 0.01 | 0.09 | 0.11 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.11
LIVEOK_6_SOLAR | Harris | GEN | 2014-11-27 | 2014 | SUN | PHOTO VOLTAIC |  | 1.25 | 1.3 | PGAE | NQC | PD | 0 | 0.02 | 0.02 | 0.02 | 0.03 | 0.06 | 0.07 | 0.06 | 0.06 | 0.04 | 0.03 | 0.02
LIVOAK_1_UNIT 1 | LIVE OAK LIMITED | GEN | 1991-03-16 | 1991 | NATURAL GAS | COMBUSTION TURBINE |  | 49.7 | 55.3 | PGAE | NQC | FC | 49.7 | 49.7 | 49.7 | 49.7 | 49.7 | 49.7 | 49.7 | 49.7 | 49.7 | 49.7 | 49.7 | 49.7
LMBEPK_2_UNITA1 | Lambie Energy Center, Unit #1 | GEN | 2003-01-06 | 2003 | NATURAL GAS | COMBUSTION TURBINE |  | 47.5 | 49.9 | PGAE | NQC | FC | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5
LMBEPK_2_UNITA2 | Creed Energy Center, Unit #1 | GEN | 2003-01-06 | 2003 | NATURAL GAS | COMBUSTION TURBINE |  | 47.6 | 49.9 | PGAE | NQC | FC | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6
LMBEPK_2_UNITA3 | Goose Haven Energy Center, Unit #1 | GEN | 2003-01-06 | 2003 | NATURAL GAS | COMBUSTION TURBINE |  | 47.75 | 49.9 | PGAE | NQC | FC | 47.75 | 47.75 | 47.75 | 47.75 | 47.75 | 47.75 | 47.75 | 47.75 | 47.75 | 47.75 | 47.75 | 47.75
LMEC_1_CTG1 | LOS MEDANOS CTG UNIT 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 172 | 172 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LMEC_1_CTG2 | LOS MEDANOS CTG UNIT 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 172 | 172 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LMEC_1_PL1X3 | Los Medanos Energy Center AGGREGATE | GEN | 2001-06-09 | 2001 | NATURAL GAS | COMBINED CYCLE |  | 580 | 0 | PGAE | NQC | FC | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580
LMEC_1_STG | LOS MEDANOS STG UNIT | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 236 | 236 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LNCSTR_6_CREST | Lanacaster Aggregate Solar Resources | GEN | 2017-06-23 | 2017 | SUN | PHOTO VOLTAIC |  | 5.5 | 5.7 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LNCSTR_6_SOLAR2 | SEPV Sierra NGR | GEN | 2021-12-22 | 2021 | HYBD | OTHER |  | 8.25 | 8.25 | SCE | NQC | PD | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9
LOCKFD_1_BEARCK | Bear Creek Solar | GEN | 2014-02-05 | 2014 | SUN | PHOTO VOLTAIC |  | 1.5 | 2.5 | PGAE | NQC | FC | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
LOCKFD_1_KSOLAR | Kettleman Solar | GEN | 2014-03-14 | 2014 | SUN | PHOTO VOLTAIC |  | 1 | 1 | PGAE | NQC | FC | 0 | 0.03 | 0.04 | 0.04 | 0.06 | 0.13 | 0.14 | 0.12 | 0.11 | 0.07 | 0.06 | 0.04
LODI25_2_UNIT 1 | LODI GAS TURBINE | GEN | 1986-01-01 | 1986 | NATURAL GAS | FTUR |  | 25 | 25.4 | PGAE | NQC | FC | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8
LODI25_6_ERKNG1 | LODI STRATEGIC RESERVE | GEN | 0 |  | NATURAL GAS | FTUR |  | 47.97 | 47.97 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LODIEC_2_CTG | Lodi Energy Center | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 220 | 220 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LODIEC_2_PL1X2 | Lodi Energy Center | GEN | 2012-11-27 | 2012 | NATURAL GAS | COMBINED CYCLE |  | 302.58 | 0 | PGAE | NQC | FC | 302.58 | 302.58 | 302.58 | 302.58 | 302.58 | 302.58 | 302.58 | 302.58 | 302.58 | 302.58 | 302.58 | 302.58
LODIEC_2_STG | Lodi Energy Center | GEN | 0 |  | NATURAL GAS | STEAM |  | 116.9 | 116.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LOTUS_6_LSFSR1 | Lotus Solar Farm | GEN | 2020-05-30 | 2020 | SUN | PHOTO VOLTAIC |  | 50 | 50 | PGAE | NQC | FC | 0.2 | 1.5 | 1.75 | 2.2 | 3.2 | 6.55 | 7.2 | 6.2 | 5.55 | 3.7 | 2.85 | 1.75
LOWGAP_1_SUPHR | Mill & Sulphur Creek Hydro | GEN | 1988-02-23 | 1988 | WATER | HYDRO |  | 0.99 | 1 | PGAE | NQC | FC | 0.4 | 0.33 | 0.13 | 0.24 | 0.19 | 0 | 0 | 0 | 0 | 0.05 | 0.04 | 0.1
LOWGAP_7_QFUNTS | Matthews Dam Hydro | GEN | 2017-05-10 | 2017 | WATER | HYDRO |  | 1.35 | 3.5 | PGAE | NQC | FC | 0.66 | 0.77 | 0.59 | 0.67 | 0.67 | 0.33 | 0.19 | 0.14 | 0.3 | 0.27 | 0.71 | 0.49
LTBEAR_1_LB3SR3 | Little Bear 3 Solar | GEN | 2020-12-03 | 2020 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | ID | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
LTBEAR_1_LB4SR4 | Little Bear 4 | GEN | 2020-12-03 | 2020 | SUN | PHOTO VOLTAIC |  | 50 | 50 | PGAE | NQC | ID | 0.2 | 1.5 | 1.75 | 2.2 | 3.2 | 6.55 | 7.2 | 6.2 | 5.55 | 3.7 | 2.85 | 1.75
LTBEAR_1_LB4SR5 | Little Bear 4 Solar 5 | GEN | 2020-12-03 | 2020 | SUN | PHOTO VOLTAIC |  | 50 | 50 | PGAE | NQC | ID | 0.2 | 1.5 | 1.75 | 2.2 | 3.2 | 6.55 | 7.2 | 6.2 | 5.55 | 3.7 | 2.85 | 1.75
LTBERA_1_LB1SR1 | Little Bear Solar 1 | GEN | 2020-12-03 | 2020 | SUN | PHOTO VOLTAIC |  | 40 | 40 | PGAE | NQC | ID | 0.16 | 1.2 | 1.4 | 1.76 | 2.56 | 5.24 | 5.76 | 4.96 | 4.44 | 2.96 | 2.28 | 1.4
MAGNLA_6_ANAHEIM | Magnolia Power Plant Anaheim | TG | 2020-01-15 | 2020 | NATURAL GAS | COMBINED CYCLE |  | 109 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAGNLA_6_CERRITOS | Magnolia Power Plant Cerritos | TG | 2020-01-15 | 2020 | NATURAL GAS | COMBINED CYCLE |  | 12 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAGNLA_6_COLTON | Magnolia Power Project | TG | 2020-01-15 | 2020 | NATURAL GAS | COMBINED CYCLE |  | 12 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAGNLA_6_PASADENA | Magnolia Power Plant - PASADENA | TG | 2020-01-15 | 2020 | NATURAL GAS | COMBINED CYCLE |  | 18 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAGUND_1_BKISR1 | Bakersfield Industrial 1 | GEN | 2017-12-27 | 2017 | SUN | PHOTO VOLTAIC |  | 1 | 1 | PGAE | NQC | FC | 0 | 0.03 | 0.04 | 0.04 | 0.06 | 0.13 | 0.14 | 0.12 | 0.11 | 0.07 | 0.06 | 0.04
MAGUND_1_BKSSR2 | Bakersfield Solar 1 | GEN | 2017-12-26 | 2017 | SUN | PHOTO VOLTAIC |  | 5.25 | 5.3 | PGAE | NQC | FC | 0.02 | 0.16 | 0.18 | 0.23 | 0.34 | 0.69 | 0.76 | 0.65 | 0.58 | 0.39 | 0.3 | 0.18
MALAGA_1_PL1X2 | Malaga Power Aggregate | GEN | 2005-09-19 | 2005 | NATURAL GAS | COMBUSTION TURBINE |  | 96.61 | 0 | PGAE | NQC | FC | 96.61 | 96.61 | 96.61 | 96.61 | 96.61 | 96.61 | 96.61 | 96.61 | 96.61 | 96.61 | 96.61 | 96.61
MALAGA_7_CTG1 | KRCD Malaga Peaking Plant CTG1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 48.5 | 48.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MALAGA_7_CTG2 | KRCD Malaga Peaking Plant CTG2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 48.5 | 48.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MALCHQ_7_UNIT 1 | MALACHA HYDRO L.P. | GEN | 1988-12-07 | 1988 | WATER | HYDRO |  | 32.5 | 32.5 | PGAE | NQC | FC | 10 | 10.57 | 3.98 | 4.18 | 0.62 | 0.09 | 0.17 | 0 | 0 | 0.26 | 0.67 | 2.19
MALIN_5_BPADYN | MALIN_5_BPADYN | TG | 0 |  | WATER | 0 |  | 700 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MALIN_5_GCPDDYN | Grant County Hydro Facilities | TG | 2018-02-09 | 2018 | WATER | HYDRO |  | 125 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MALIN_5_HERMDYN | MALIN_5_HERMDYN | TG | 2021-04-13 | 2021 | NATURAL GAS | COMBINED CYCLE |  | 308 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MALIN_5_IBERDR | Iberdrola Centroid Sytem Resource | TG | 0 |  | WIND | WIND |  | 100 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MALIN_5_INHRED | CSF Columbia Gorge | TG | 0 |  | WIND | WIND |  | 50 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MALIN_5_INHRPG | BIGLOW CANYON | TG | 0 |  | WIND | WIND |  | 50 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAMMTH_7_UNIT 1 | MAMMOTH POOL UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 95 | 95 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAMMTH_7_UNIT 2 | MAMMOTH POOL UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 95 | 95 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MANTEC_1_ML1SR1 | Manteca Land 1 | GEN | 2017-12-28 | 2017 | SUN | PHOTO VOLTAIC |  | 1 | 1 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MANZNA_2_WIND | Manzana Wind | GEN | 2012-12-20 | 2012 | WIND | WIND |  | 189 | 300 | SCE | NQC | FC | 33.4 | 35.52 | 31.21 | 29.9 | 31.8 | 29.14 | 27.08 | 20.57 | 21.25 | 19.72 | 26.57 | 32.19
MARCPW_6_SOLAR1 | Maricopa West Solar PV | GEN | 2015-12-12 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
MARTIN_1_SUNSET | Sunset Reservoir - North Basin | GEN | 2010-10-29 | 2010 | SUN | PHOTO VOLTAIC |  | 4.5 | 4.5 | PGAE | NQC | FC | 0.02 | 0.14 | 0.16 | 0.2 | 0.29 | 0.59 | 0.65 | 0.56 | 0.5 | 0.33 | 0.26 | 0.16
MARVEL_2_MARBT1 | Marvel | GEN | 0 |  | LESR | OTHER |  | 162.5 | 162.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MARVEL_2_MARBT2 | Marvel | GEN | 0 |  | LESR | OTHER |  | 162.5 | 162.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MARVEL_2_MARBT3 | Marvel 2 | GEN | 2023-07-24 | 2023 | LESR | OTHER |  | 74.94 | 75 | SCE | NQC | ID | 74.93 | 74.93 | 74.93 | 74.93 | 74.93 | 74.93 | 74.93 | 74.93 | 74.93 | 74.93 | 74.93 | 74.93
MARVEL_2_MARBX2 | Marvel | GEN | 2023-07-18 | 2023 | LESR | OTHER |  | 325 | 0 | SCE | NQC | ID | 324.99 | 324.99 | 324.99 | 324.99 | 324.99 | 324.99 | 324.99 | 324.99 | 324.99 | 324.99 | 324.99 | 324.99
MCARTH_6_FRIVRB | Fall River Mills Project B | GEN | 2014-03-05 | 2014 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | ID | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
MCCALL_1_QF | Fish Water | GEN | 1990-01-01 | 1990 | WATER | HYDRO |  | 0.52 | 2.5 | PGAE | NQC | FC | 0.3 | 0.39 | 0.27 | 0.29 | 0.33 | 0.32 | 0.3 | 0.2 | 0.24 | 0.35 | 0.32 | 0.23
MCFLND_5_MFAUXL1 | McFarland Solar | TG | 0 |  | OTHER | OTHER |  | 6 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MCFLND_5_MFSBT1 | McFarland Solar A BESS | GEN | 2023-12-22 | 2023 | LESR | OTHER |  | 100 | 100 | SDGE | NQC | FC |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MCFLND_5_MFSSR1 | McFarland Solar A PV | GEN | 2023-12-22 | 2023 | SUN | PHOTO VOLTAIC |  | 200 | 200 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MCFLND_5_MSBBT1 | McFarland Solar B BESS | GEN | 0 |  | LESR | OTHER |  | 25 | 25 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MCFLND_5_MSBBT2 | McFarland Solar B BESS | GEN | 0 |  | LESR | OTHER |  | 125 | 125 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MCFLND_5_MSBBX2 | McFarland Solar B BESS | GEN | 0 |  | LESR | OTHER |  | 150 | 0 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MCFLND_5_MSBSR1 | McFarland Solar B PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 50 | 50 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MCFLND_5_MSBSR2 | McFarland Solar B PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 250 | 250 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MCFLND_5_MSBSX2 | McFarland Solar B PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 300 | 0 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MCSWAN_6_UNITS | MC SWAIN HYDRO | GEN | 1967-01-01 | 1967 | WATER | HYDRO |  | 9 | 10 | PGAE | NQC | FC | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
MDFKRL_2_PROJCT | MIDDLE FORK AND RALSTON PSP | GEN | 1966-01-01 | 1966 | WATER | HYDRO |  | 210 | 0 | PGAE | NQC | FC | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
MELRSE_6_MELBT1 | Melrose BESS 1 | GEN | 0 |  | LESR | OTHER |  | 10 | 10 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MELRSE_6_MELBT2 | Melrose BESS 2 | GEN | 0 |  | LESR | OTHER |  | 10 | 10 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MENBIO_6_RENEW1 | CalRENEW - 1(A) | GEN | 2010-04-30 | 2010 | SUN | PHOTO VOLTAIC |  | 5 | 5 | PGAE | NQC | FC | 0.02 | 0.15 | 0.18 | 0.22 | 0.32 | 0.66 | 0.72 | 0.62 | 0.56 | 0.37 | 0.29 | 0.18
MERCED_1_SOLAR1 | Mission Solar | GEN | 2015-05-23 | 2015 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MERCED_1_SOLAR2 | Merced Solar | GEN | 2015-05-12 | 2015 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MERCFL_6_UNIT | Merced Falls Powerhouse | GEN | 1930-01-01 | 1930 | WATER | HYDRO |  | 3.5 | 3.5 | PGAE | NQC | FC | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
MESAP_1_QF | SMALL QF AGGREGATION - SAN LUIS OBISPO | GEN | 0 |  | OTHER | OTHER |  | 1 | 1 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MESAS_2_CADBT1 | Cadillac 1 BESS | GEN | 0 |  | LESR | OTHER |  | 3.5 | 3.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MESAS_2_YORBT1 | Yorktown 1 BESS | GEN | 0 |  | LESR | OTHER |  | 3 | 3 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
METEC_2_PL1X3 | Metcalf Energy Center | GEN | 2005-05-27 | 2005 | NATURAL GAS | COMBINED CYCLE |  | 597.05 | 0 | PGAE | NQC | FC | 597.05 | 597.05 | 597.05 | 597.05 | 597.05 | 597.05 | 597.05 | 597.05 | 597.05 | 597.05 | 597.05 | 597.05
METEC_7_CTG1 | Metcalf Energy Center Unit 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 193 | 193 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
METEC_7_CTG2 | Metcalf Energy Center Unit 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 193 | 193 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
METEC_7_STG3 | Metcalf Energy Center Unit 3 | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 231 | 231 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIDFRK_7_UNIT 1 | MIDDLE FORK UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 65.7 | 65.7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIDFRK_7_UNIT 2 | MIDDLE FORK UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 69 | 69 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIDSUN_1_CT5A | MIDSUN_1_CT5A | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 4.8 | 4.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIDSUN_1_CT5B | MIDSUN_1_CT5B | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 4.8 | 4.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIDSUN_1_PL1X2 | North Midway Cogens 5A 5B | GEN | 2022-03-17 | 2022 | NATURAL GAS | COMBUSTION TURBINE |  | 9.6 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIDWD_2_WIND2 | Coram Energy | GEN | 2015-12-23 | 2015 | WIND | WIND |  | 3 | 3 | SCE | NQC | FC | 0.53 | 0.56 | 0.5 | 0.47 | 0.5 | 0.46 | 0.43 | 0.33 | 0.34 | 0.31 | 0.42 | 0.51
MIDWD_7_CORAMB | CELLC 7.5 MW Tehachapi Project | GEN | 1983-12-01 | 1983 | WIND | WIND |  | 7.5 | 7.5 | SCE | NQC | FC | 1.33 | 1.41 | 1.24 | 1.19 | 1.26 | 1.16 | 1.07 | 0.82 | 0.84 | 0.78 | 1.05 | 1.28
MIDWY3_2_MDSSR1 | Midway South Solar Farm | TG | 2018-09-06 | 2018 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIDWYS_2_MIDSL1 | Midway Solar Farm | TG | 2018-01-13 | 2018 | SUN | PHOTO VOLTAIC |  | 49.9 | 50 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MILFRD_7_PASADENA | Milford I | TG | 2016-03-01 | 2016 | WIND | WIND |  | 5 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIRLOM_2_CORONA | MWD Corona Hydroelectric Recovery Plant | GEN | 1987-01-01 | 1987 | WATER | HYDRO |  | 2.85 | 2.8 | SCE | NQC | FC | 1.5 | 0.98 | 0.86 | 0.93 | 1.85 | 1.51 | 0.33 | 0.64 | 0.53 | 0.78 | 0.82 | 1.24
MIRLOM_2_CREST | Temescal Canyon RV | GEN | 2020-03-25 | 2020 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIRLOM_2_LNDFL | Milliken Landfill Solar | GEN | 2017-06-23 | 2017 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE | NQC | FC | 0.01 | 0.09 | 0.11 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.11
MIRLOM_2_MLBBTA | Mira Loma BESS A | GEN | 2016-12-30 | 2016 | LESR | OTHER |  | 10 | 10 | SCE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
MIRLOM_2_MLBBTB | Mira Loma BESS B | GEN | 2016-12-30 | 2016 | LESR | OTHER |  | 10 | 10 | SCE | NQC | FC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
MIRLOM_2_TEMESC | MWD Temescal Hydroelectric Recovery Plan | GEN | 1987-01-01 | 1987 | WATER | HYDRO |  | 2.85 | 2.8 | SCE | NQC | FC | 1.33 | 0.58 | 1.07 | 1.65 | 1.71 | 1.01 | 0.06 | 0.77 | 0.92 | 0.73 | 0.85 | 1.43
MIRLOM_6_PEAKER | Mira Loma Peaker | GEN | 2007-09-20 | 2007 | NATURAL GAS | COMBUSTION TURBINE |  | 47.18 | 59 | SCE | NQC | FC | 47.18 | 47.18 | 47.18 | 47.18 | 47.18 | 47.18 | 47.18 | 47.18 | 47.18 | 47.18 | 47.18 | 47.18
MIRLOM_7_MWDLKM | Lake Mathews Hydroelectric Recovery Plan | GEN | 1980-01-01 | 1980 | WATER | HYDRO |  | 5 | 5 | SCE | NQC | FC | 2.4 | 2.4 | 1.6 | 2.4 | 2.4 | 3.2 | 3.2 | 3.6 | 2.8 | 2.4 | 2.4 | 1.6
MISSIX_1_QF | SMALL QF AGGREGATION - SAB FRABCUSCI | GEN | 1987-01-01 | 1987 | NATURAL GAS | FTUR |  | 1 | 15 | PGAE | NQC | FC | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
MKTRCK_1_UNIT 1 | MCKITTRICK LIMITED | GEN | 1991-10-16 | 1991 | NATURAL GAS | COMBUSTION TURBINE |  | 47.72 | 57.9 | PGAE | NQC | FC | 47.72 | 47.72 | 47.72 | 47.72 | 47.72 | 47.72 | 47.72 | 47.72 | 47.72 | 47.72 | 47.72 | 47.72
MLPTAS_7_QFUNTS | MLPTAS_7_QFUNTS | GEN | 0 |  | OTHER | OTHER |  | 1 | 2 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MNDALY_6_MCGRTH | McGrath Beach Peaker | GEN | 2012-11-01 | 2012 | NATURAL GAS | COMBUSTION TURBINE |  | 48.56 | 59 | SCE | NQC | FC | 48.56 | 48.56 | 48.56 | 48.56 | 48.56 | 48.56 | 48.56 | 48.56 | 48.56 | 48.56 | 48.56 | 48.56
MNDOTA_1_SOLAR1 | North Star Solar 1 | GEN | 2015-06-20 | 2015 | SUN | PHOTO VOLTAIC |  | 60 | 60 | PGAE | NQC | FC | 0.24 | 1.8 | 2.1 | 2.64 | 3.84 | 7.86 | 8.64 | 7.44 | 6.66 | 4.44 | 3.42 | 2.1
MNDOTA_1_SOLAR2 | Citizen Solar B | GEN | 2015-12-11 | 2015 | SUN | PHOTO VOLTAIC |  | 5 | 5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MOCCPH_7_UNIT 1 | MOCCASIN HYDRO UNIT 1 | GEN | 0 |  | 0 | 0 |  | 52 | 52 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MOCCPH_7_UNIT 2 | MOCCASIN HYDRO UNIT 2 | GEN | 0 |  | 0 | 0 |  | 52 | 52 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MOJAVE_1_SIPHON | MOJAVE SIPHON POWER PLANT | GEN | 1996-01-01 | 1996 | WATER | HYDRO |  | 14.36 | 34.5 | SCE | NQC | FC | 10.52 | 5.92 | 7.78 | 10.32 | 10.12 | 10.96 | 10.38 | 9.85 | 10.98 | 9.68 | 11.13 | 10.06
MOJAVW_2_SOLAR | Mojave West | GEN | 2016-06-15 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
MONTPH_7_UNIT 1 | MONTICELLO Unit 1 | GEN | 0 |  | 0 | 0 |  | 5.7 | 5.7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MONTPH_7_UNIT 2 | MONTICELLO Unit 2 | GEN | 0 |  | 0 | 0 |  | 5.7 | 5.7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MONTPH_7_UNIT 3 | MONTICELLO Unit 3 | GEN | 0 |  | 0 | 0 |  | 1.5 | 1.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MONTPH_7_UNITS | MONTICELLO HYDRO AGGREGATE | GEN | 1974-01-01 | 1974 | WATER | HYDRO |  | 12.5 | 0 | PGAE | NQC | FC | 0.28 | 0.47 | 2.27 | 4.03 | 5.12 | 7.93 | 8.52 | 6.81 | 5.5 | 2.5 | 0.73 | 0.48
MOORPK_2_ACOBT1 | Acorn I BESS | GEN | 2021-03-31 | 2021 | LESR | OTHER |  | 1.95 | 2 | SCE | NQC | FC | bar: 2024-01-01 to 2024-12-01
MOORPK_2_CALABS | Calabasas Gas-to-Energy Facility | GEN | 2010-09-20 | 2010 | BIOGAS | COMBUSTION TURBINE |  | 6.96 | 13.8 | SCE | NQC | FC | 4.4 | 4.26 | 3.84 | 3.98 | 4.21 | 4.16 | 4.04 | 3.44 | 3.76 | 4.21 | 4.1 | 4.11
MOORPK_6_QF | MOORPARK QFS | GEN | 1976-01-01 | 1976 | OTHER | OTHER |  | 0.8 | 35.8 | SCE | NQC | FC | 0.01 | 0.06 | 0.02 | 0 | 0 | 0.04 | 0.04 | 0.28 | 0.4 | 0.4 | 0.4 | 0.39
MORWD_6_QF | Morwind | GEN | 2017-01-17 | 2017 | WIND | WIND |  | 38.16 | 56 | SCE | NQC | FC | 6.74 | 7.17 | 6.3 | 6.04 | 6.42 | 5.88 | 5.47 | 4.15 | 4.29 | 3.98 | 5.37 | 6.5
MOSSLD_2_PSP1 | MOSS LANDING POWER BLOCK 1 | GEN | 2002-07-01 | 2002 | NATURAL GAS | COMBINED CYCLE |  | 510 | 0 | PGAE | NQC | FC | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510
MOSSLD_2_PSP1G1 | MOSS LANDING CC PLANT 1, CTG UNIT 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 176 | 176 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MOSSLD_2_PSP1G2 | MOSS LANDING CC PLANT 1, CTG UNIT 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 176 | 176 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MOSSLD_2_PSP1G3 | MOSS LANDING CC PLANT 1, STG UNIT | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 198 | 198 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MOSSLD_2_PSP2 | MOSS LANDING POWER BLOCK 2 | GEN | 2002-07-11 | 2002 | NATURAL GAS | COMBINED CYCLE |  | 510 | 0 | PGAE | NQC | FC | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510
MOSSLD_2_PSP2G1 | MOSS LANDING CC PLANT 2, CTG UNIT 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 176 | 176 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MOSSLD_2_PSP2G2 | MOSS LANDING CC PLANT 2, CTG UNIT 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 176 | 176 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MOSSLD_2_PSP2G3 | MOSS LANDING CC PLANT 2, STG UNIT | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 198 | 198 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MRCHNT_2_CTG1 | Desert Star Energy Center CT1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 230 | 230 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MRCHNT_2_CTG2 | Desert Star Energy Center CT2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 201 | 201 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MRCHNT_2_PL1X3 | Desert Star Energy Center | GEN | 2012-06-18 | 2012 | NATURAL GAS | COMBINED CYCLE |  | 494.58 | 0 | SCE | NQC | PD | 419.25 | 419.25 | 419.25 | 419.25 | 419.25 | 419.25 | 419.25 | 419.25 | 419.25 | 419.25 | 419.25 | 419.25
MRCHNT_2_STG | Desert Star Energy Center ST1 | GEN | 0 |  | NATURAL GAS | STEAM |  | 201 | 201 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MRGT_6_MEF2 | Miramar Energy Facility II | GEN | 2009-08-07 | 2009 | NATURAL GAS | COMBUSTION TURBINE |  | 44 | 67.5 | SDGE | NQC | FC | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
MRGT_6_MMAREF | Miramar Energy Facility | GEN | 2005-07-27 | 2005 | NATURAL GAS | COMBUSTION TURBINE |  | 45 | 68 | SDGE | NQC | FC | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
MRGT_6_TGEBT1 | Top Gun Energy Storage | GEN | 2021-06-30 | 2021 | LESR | OTHER |  | 30 | 30 | SDGE | NQC | FC | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
MRLSDS_6_SOLAR1 | Morelos Solar | GEN | 2015-11-25 | 2015 | SUN | PHOTO VOLTAIC |  | 15 | 15 | PGAE | NQC | FC | 0.06 | 0.45 | 0.53 | 0.66 | 0.96 | 1.97 | 2.16 | 1.86 | 1.67 | 1.11 | 0.86 | 0.53
MSHGTS_6_MMARLF | MIRAMAR LANDFILL | GEN | 2003-05-21 | 2003 | BIOGAS | RECIPROCATING ENGINE |  | 5 | 3 | SDGE | NQC | FC | 3.63 | 3.82 | 3.75 | 4.1 | 4.19 | 4.15 | 4.16 | 4.08 | 4.31 | 4.01 | 3.9 | 3.6
MSOLAR_2_MS4BT1 | Mesquite Solar 4 BESS | GEN | 2024-01-26 | 2024 | LESR | OTHER |  | 10 | 10 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MSOLAR_2_MS4SR4 | Mesquite Solar 4 | GEN | 2024-01-18 | 2024 | SUN | PHOTO VOLTAIC |  | 52.5 | 52.5 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MSOLAR_2_SOLAR1 | Mesquite Solar 1 | GEN | 2014-01-01 | 2014 | SUN | PHOTO VOLTAIC |  | 165 | 170 | SDGE | NQC | FC | 0.66 | 4.95 | 5.78 | 7.26 | 10.56 | 21.62 | 23.76 | 20.46 | 18.32 | 12.21 | 9.41 | 5.78
MSOLAR_2_SOLAR2 | Mesquite Solar 2 | GEN | 2017-10-12 | 2017 | SUN | PHOTO VOLTAIC |  | 100.81 | 165 | SDGE | NQC | FC | 0.4 | 3.02 | 3.53 | 4.44 | 6.45 | 13.21 | 14.52 | 12.5 | 11.19 | 7.46 | 5.75 | 3.53
MSOLAR_2_SOLAR3 | Mesquite Solar 3, LLC | GEN | 2016-12-06 | 2016 | SUN | PHOTO VOLTAIC |  | 152 | 152 | SDGE | NQC | FC | 0.61 | 4.56 | 5.32 | 6.69 | 9.73 | 19.91 | 21.89 | 18.85 | 16.87 | 11.25 | 8.66 | 5.32
MSQUIT_5_SERDYN | MSQUIT_5_SERDYN | TG | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 625 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MSSION_2_QF | SMALL QF AGGREGATION - SAN DIEGO | GEN | 1980-01-01 | 1980 | OTHER | 0 |  | 2 | 50 | SDGE | NQC | FC | 0.15 | 0.15 | 0.15 | 0.19 | 0.29 | 0.33 | 0.3 | 0.32 | 0.32 | 0.28 | 0.26 | 0.16
MSTANG_2_MTGBT1 | Mustang 1 BESS | GEN | 2021-11-01 | 2021 | LESR | OTHER |  | 75 | 75 | PGAE | NQC | FC | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
MSTANG_2_SOLAR | Mustang | GEN | 2016-07-12 | 2016 | SUN | PHOTO VOLTAIC |  | 30 | 30 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MSTANG_2_SOLAR3 | Mustang 3 | GEN | 2016-05-03 | 2016 | SUN | PHOTO VOLTAIC |  | 40 | 40 | PGAE | NQC | PD | 0.06 | 0.45 | 0.52 | 0.66 | 0.96 | 1.96 | 2.15 | 1.85 | 1.66 | 1.11 | 0.85 | 0.52
MSTANG_2_SOLAR4 | Mustang 4 | GEN | 2016-06-09 | 2016 | SUN | PHOTO VOLTAIC |  | 30 | 30 | PGAE | NQC | FC | 0.12 | 0.9 | 1.05 | 1.32 | 1.92 | 3.93 | 4.32 | 3.72 | 3.33 | 2.22 | 1.71 | 1.05
MTNPOS_1_UNIT | MT.POSO COGENERATION CO. | GEN | 1989-04-01 | 1989 | BIOMASS | STEAM |  | 46.64 | 57 | PGAE | NQC | FC | 29.05 | 28.4 | 17.44 | 28.88 | 31.82 | 39.72 | 41.67 | 40.55 | 39.56 | 39.3 | 38.79 | 27.09
MTWIND_1_MVPWD1 | Mountain View Power Project I Repower | GEN | 2022-07-26 | 2022 | WIND | WIND |  | 66.6 | 66.6 | SCE | NQC | FC | 11.77 | 12.52 | 11 | 10.54 | 11.2 | 10.27 | 9.54 | 7.25 | 7.49 | 6.95 | 9.36 | 11.34
MTWIND_1_UNIT 3 | Mountain View Power Project III | GEN | 2003-12-15 | 2003 | WIND | WIND |  | 22.44 | 22.4 | SCE | NQC | FC | 3.97 | 4.22 | 3.71 | 3.55 | 3.78 | 3.46 | 3.21 | 2.44 | 2.52 | 2.34 | 3.15 | 3.82
MURRAY_6_UNIT | Grossmont Hospital | GEN | 2016-12-16 | 2016 | NATURAL GAS | FTUR |  | 4.12 | 4.6 | SDGE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NAROW1_2_UNIT | NARROWS PH 1 UNIT | GEN | 2020-09-21 | 2020 | WATER | HYDRO |  | 12 | 12 | PGAE | NQC | FC | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
NAROW2_2_UNIT | Narrows Powerhouse Unit 2 | GEN | 1969-01-01 | 1969 | WATER | HYDRO |  | 55 | 55 | PGAE | NQC | FC | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
NAVYII_2_UNIT 4 | COSO POWER DEVELOPERS (NAVY II) UNIT 4 | GEN | 0 |  | 0 | 0 |  | 33.3 | 33.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NAVYII_2_UNIT 5 | COSO Power Developers (Navy II) Unit 5 | GEN | 0 |  | 0 | 0 |  | 33.3 | 33.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NAVYII_2_UNIT 6 | COSO Power Developers (Navy II) Unit 6 | GEN | 0 |  | 0 | 0 |  | 33.3 | 33.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NAVYII_2_UNITS | COSO POWER DEVELOPER (NAVY II) AGGREGATE | GEN | 1989-12-23 | 1989 | GEOTHERMAL | STEAM |  | 90 | 0 | SCE | NQC | PD | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
NCPA_7_GP1UN1 | NCPA GEO PLANT 1 UNIT 1 | GEN | 1983-01-01 | 1983 | GEOTHERMAL | STEAM |  | 38.85 | 55 | PGAE | NQC | FC | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85
NCPA_7_GP1UN2 | NCPA GEO PLANT 1 UNIT 2 | GEN | 1983-01-01 | 1983 | GEOTHERMAL | STEAM |  | 50 | 55 | PGAE | NQC | FC | 39.94 | 39.94 | 39.94 | 39.94 | 39.94 | 39.94 | 39.94 | 39.94 | 39.94 | 39.94 | 39.94 | 39.94
NCPA_7_GP2UN3 | NCPA GEO PLANT 2 UNIT 3 | GEN | 1985-01-01 | 1985 | GEOTHERMAL | STEAM |  | 42.42 | 55 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NCPA_7_GP2UN4 | NCPA GEO PLANT 2 UNIT 4 | GEN | 1986-01-01 | 1986 | GEOTHERMAL | STEAM |  | 52.73 | 55 | PGAE | NQC | FC | 52.73 | 52.73 | 52.73 | 52.73 | 52.73 | 52.73 | 52.73 | 52.73 | 52.73 | 52.73 | 52.73 | 52.73
NEENCH_6_SOLAR | Alpine Solar | GEN | 2013-01-18 | 2013 | SUN | PHOTO VOLTAIC |  | 66 | 66 | SCE | NQC | FC | 0.26 | 1.98 | 2.31 | 2.9 | 4.22 | 8.65 | 9.5 | 8.18 | 7.33 | 4.88 | 3.76 | 2.31
NEWARK_1_QF | NEWARK 1 QF | GEN | 0 |  | OTHER | OTHER |  | 0.1 | 1.1 | PGAE | NQC | FC | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
NGILAA_5_SDGDYN | NGILAA_5_SDGDYN | TG | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 55 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NHOGAN_6_UNIT 1 | NEW HOGAN PH UNIT 1 | GEN | 0 |  | 0 | 0 |  | 2.2 | 2.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NHOGAN_6_UNIT 2 | NEW HOGAN PH UNIT 2 | GEN | 0 |  | 0 | 0 |  | 1.1 | 1.1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NHOGAN_6_UNITS | NEW HOGAN PH AGGREGATE | GEN | 1986-04-15 | 1986 | WATER | HYDRO |  | 4 | 0 | PGAE | NQC | FC | 0.13 | 0.02 | 0.09 | 0.52 | 1.15 | 0.96 | 1.53 | 1.17 | 0.98 | 0.02 | 0 | 0
NIMTG_6_NICOGN | NORTH ISLAND COGEN | GEN | 1989-01-01 | 1989 | OTHER | 0 |  | 4.05 | 5 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NOAKS_2_PESBT1 | Placerita BESS | GEN | 0 |  | LESR | OTHER |  | 80 | 80 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NORCNV_1_NCVBT1 | North Central Valley | GEN | 2023-08-30 | 2023 | LESR | OTHER |  | 132 | 132 | PGAE | NQC | ID | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
NORORC_2_NOSSB1 | Northern Orchard Solar | GEN | 0 |  | HYBD | OTHER |  | 133.6 | 133.6 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NORORC_2_NOSSB2 | Northern Orchard Solar | GEN | 0 |  | HYBD | OTHER |  | 108.4 | 108.4 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NOVATO_6_LNDFL | Redwood Renewable Energy | GEN | 2017-09-16 | 2017 | BIOGAS | RECIPROCATING ENGINE |  | 3.9 | 3.9 | PGAE | NQC | FC | 3.64 | 3.67 | 3.64 | 3.62 | 3.58 | 3.26 | 2.83 | 2.87 | 3.03 | 2.78 | 3.24 | 3.29
NWCSTL_7_UNIT 1 | NEWCASTLE HYDRO | GEN | 1986-01-01 | 1986 | WATER | HYDRO |  | 12 | 12 | PGAE | NQC | FC | 0.95 | 2.47 | 3.29 | 1.43 | 0.3 | 0 | 0.33 | 0 | 0 | 0.52 | 0 | 1.19
NZWIND_2_WDSTR5 | Windstream 6111 | GEN | 2016-03-08 | 2016 | WIND | WIND |  | 6.31 | 6.5 | SCE | NQC | FC | 1.11 | 1.19 | 1.04 | 1 | 1.06 | 0.97 | 0.9 | 0.69 | 0.71 | 0.66 | 0.89 | 1.07
NZWIND_6_CALWND | Wind Resource I | GEN | 2012-03-24 | 2012 | WIND | WIND |  | 9 | 8.7 | SCE | NQC | FC | 1.59 | 1.69 | 1.49 | 1.42 | 1.51 | 1.39 | 1.29 | 0.98 | 1.01 | 0.94 | 1.27 | 1.53
NZWIND_6_WDSTR | Windstream 39 | GEN | 1984-02-01 | 1984 | WIND | WIND |  | 3.35 | 6.2 | SCE | NQC | FC | 0.59 | 0.63 | 0.55 | 0.53 | 0.56 | 0.52 | 0.48 | 0.36 | 0.38 | 0.35 | 0.47 | 0.57
NZWIND_6_WDSTR2 | Windstream 6040 | GEN | 2014-11-30 | 2014 | WIND | WIND |  | 4.07 | 6.9 | SCE | NQC | FC | 0.72 | 0.76 | 0.67 | 0.64 | 0.68 | 0.63 | 0.58 | 0.44 | 0.46 | 0.42 | 0.57 | 0.69
NZWIND_6_WDSTR3 | Windstream 6041 | GEN | 2014-11-30 | 2014 | WIND | WIND |  | 3.86 | 6 | SCE | NQC | FC | 0.68 | 0.73 | 0.64 | 0.61 | 0.65 | 0.6 | 0.55 | 0.42 | 0.43 | 0.4 | 0.54 | 0.66
NZWIND_6_WDSTR4 | Windstream 6042 | GEN | 2015-12-11 | 2015 | WIND | WIND |  | 6.77 | 6.8 | SCE | NQC | FC | 1.2 | 1.27 | 1.12 | 1.07 | 1.14 | 1.04 | 0.97 | 0.74 | 0.76 | 0.71 | 0.95 | 1.15
OAK C_1_EBMUD | MWWTP PGS 1 - ENGINES | GEN | 2012-11-01 | 2012 | BIOGAS | RECIPROCATING ENGINE |  | 6.9 | 6.9 | PGAE | NQC | FC | 1.67 | 1.56 | 1.51 | 1.68 | 1.23 | 1.46 | 1.39 | 1.7 | 1.89 | 1.67 | 1.6 | 1.96
OAK C_7_UNIT 1 | OAKLAND STATION C GT UNIT 1 | GEN | 1978-01-01 | 1978 | DISTILLATE | COMBUSTION TURBINE |  | 55 | 55 | PGAE | NQC | FC | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OAK C_7_UNIT 3 | OAKLAND STATION C GT UNIT 3 | GEN | 1978-01-01 | 1978 | DISTILLATE | COMBUSTION TURBINE |  | 55 | 55 | PGAE | NQC | FC | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OAK L_1_GTG1 | MWWTP PGS 2 - Turbine | GEN | 1991-10-21 | 1991 | BIOGAS | COMBUSTION TURBINE |  | 4.6 | 5.8 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OAKWD_6_QF | Oak Creek | GEN | 2017-12-12 | 2017 | WIND | WIND |  | 27.87 | 30.3 | SCE | NQC | FC | 4.92 | 5.24 | 4.6 | 4.41 | 4.69 | 4.3 | 3.99 | 3.03 | 3.13 | 2.91 | 3.92 | 4.75
OAKWD_6_ZEPHWD | Zephyr Park | GEN | 2014-02-07 | 2014 | WIND | WIND |  | 3.5 | 4.2 | SCE | NQC | FC | 0.62 | 0.66 | 0.58 | 0.55 | 0.59 | 0.54 | 0.5 | 0.38 | 0.39 | 0.37 | 0.49 | 0.6
OASIS_6_AR4SR1 | Arrache 4006 I | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1 | 1 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_AR4SR2 | Arrache 4006 II | GEN | 2023-12-22 | 2023 | SUN | PHOTO VOLTAIC |  | 1 | 1 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_AR4SR3 | Arrache 4013 | GEN | 2023-12-08 | 2023 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_AR8SR1 | Arrache 8083 I | GEN | 2023-06-28 | 2023 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_AR8SR2 | Arrache 8083 II | GEN | 2023-06-28 | 2023 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_AR8SR3 | Arrache 8083 III | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1 | 1 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_CREST | CREST Contracts | GEN | 2016-04-20 | 2016 | SUN | PHOTO VOLTAIC |  | 3 | 13.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_GBDSR4 | Green Beanworks D | GEN | 2018-08-25 | 2018 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE | NQC | FC | 0.01 | 0.09 | 0.11 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.11
OASIS_6_LPPSR1 | Lancaster Psomas PV | GEN | 2022-07-25 | 2022 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_MA4SR1 | Ma 4035 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_SOLAR1 | Morgan Lancaster I | GEN | 2015-12-09 | 2015 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_SOLAR2 | Oasis Solar | GEN | 2016-01-19 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
OASIS_6_SOLAR3 | Soccer Center | GEN | 2017-08-11 | 2017 | SUN | PHOTO VOLTAIC |  | 3 | 3.8 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OASIS_6_VINSR1 | Vinam | GEN | 2023-10-30 | 2023 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OBERON_5_O1BBT1 | Oberon 1 BESS | GEN | 0 |  | LESR | OTHER |  | 62.5 | 62.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OBERON_5_O1BBT2 | Oberon 1 BESS | GEN | 0 |  | LESR | OTHER |  | 62.5 | 62.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OBERON_5_O1BBX2 | Oberon 1 BESS | GEN | 2023-11-03 | 2023 | LESR | OTHER |  | 125 | 0 | SCE | NQC | ID | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
OBERON_5_O1SSR1 | Oberon 1A Solar | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 25 | 25 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OBERON_5_O1SSR2 | Oberon 1A Solar | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 125 | 125 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OBERON_5_O1SSR3 | Oberon 1B Solar | GEN | 2023-11-03 | 2023 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE | NQC | ID | 0.24 | 2.1 | 2.52 | 3.37 | 5.04 | 10.36 | 11.29 | 9.56 | 8.28 | 5.24 | 3.67 | 1.78
OBERON_5_O1SSX2 | Oberon 1A Solar | GEN | 2023-11-03 | 2023 | SUN | PHOTO VOLTAIC |  | 150 | 0 | SCE | NQC | ID | 0.36 | 3.15 | 3.78 | 5.06 | 7.56 | 15.53 | 16.93 | 14.34 | 12.42 | 7.86 | 5.51 | 2.67
OBERON_5_O2BBT3 | Oberon 2 BESS | GEN | 0 |  | LESR | OTHER |  | 62.5 | 62.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OBERON_5_O2BBT4 | Oberon 2 BESS | GEN | 0 |  | LESR | OTHER |  | 62.5 | 62.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OBERON_5_O2BBX2 | Oberon 2 BESS | GEN | 2023-11-03 | 2023 | LESR | OTHER |  | 125 | 0 | SCE | NQC | ID | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
OBERON_5_O2SSR4 | Oberon 2A Solar | GEN | 2023-11-08 | 2023 | SUN | PHOTO VOLTAIC |  | 125 | 125 | SCE | NQC | ID | 0.3 | 2.62 | 3.15 | 4.22 | 6.3 | 12.95 | 14.11 | 11.95 | 10.35 | 6.55 | 4.59 | 2.22
OBERON_5_O2SSR5 | Oberon 2B Solar | GEN | 2023-11-08 | 2023 | SUN | PHOTO VOLTAIC |  | 125 | 125 | SCE | NQC | ID | 0.3 | 2.62 | 3.15 | 4.22 | 6.3 | 12.95 | 14.11 | 11.95 | 10.35 | 6.55 | 4.59 | 2.22
OCOTLO_6_OCWSB1 | Ocotillo Wells Solar and BESS | TG | 2023-09-01 | 2023 | HYBD | OTHER |  | 50 | 50 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OCTILO_5_WIND | Ocotillo Wind Energy Facility | GEN | 2013-07-30 | 2013 | WIND | WIND |  | 265 | 265 | SDGE | NQC | FC | 46.83 | 49.8 | 43.76 | 41.92 | 44.58 | 40.86 | 37.97 | 28.85 | 29.8 | 27.65 | 37.26 | 45.13
OGROVE_6_CTG1 | Orange Grove | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 75 | 75 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OGROVE_6_CTG2 | Orange Grove | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 75 | 75 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OGROVE_6_PL1X2 | Orange Grove Energy Center | GEN | 2010-06-16 | 2010 | NATURAL GAS | COMBUSTION TURBINE |  | 96 | 0 | SDGE | NQC | FC | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
OILFLD_7_QFUNTS | Nacimiento Hydroelectric Plant | GEN | 2013-09-16 | 2013 | WATER | HYDRO |  | 3.8 | 4.4 | PGAE | NQC | FC | 0.1 | 0.11 | 0.69 | 1.88 | 1.41 | 0.99 | 0.95 | 0.81 | 0.37 | 0.05 | 0.04 | 0
OLDRIV_6_BIOGAS | Bidart Old River 1 | GEN | 2014-03-10 | 2014 | BIOGAS | RECIPROCATING ENGINE |  | 2 | 2 | PGAE | NQC | FC | 1.76 | 1.83 | 1.84 | 1.68 | 1.79 | 1.74 | 1.71 | 1.75 | 1.76 | 1.77 | 1.77 | 1.66
OLDRIV_6_CESDBM | Ces Dairy Biogas | GEN | 2018-02-02 | 2018 | BIOGAS | RECIPROCATING ENGINE |  | 1 | 1 | PGAE | NQC | FC | 0.95 | 0.97 | 0.94 | 0.93 | 0.95 | 0.91 | 0.92 | 0.93 | 0.94 | 0.96 | 0.96 | 0.97
OLDRIV_6_LKVBM1 | Lakeview Dairy Biogas | GEN | 2018-02-02 | 2018 | BIOGAS | RECIPROCATING ENGINE |  | 1 | 1 | PGAE | NQC | FC | 0.97 | 0.96 | 0.94 | 0.95 | 0.94 | 0.94 | 0.93 | 0.93 | 0.94 | 0.95 | 0.97 | 0.97
OLDRV1_6_SOLAR | Old River One | GEN | 2014-12-30 | 2014 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
OLINDA_2_COYCRK | MWD Coyote Creek Hydroelectric Recovery | GEN | 1979-02-21 | 1979 | WATER | HYDRO |  | 3.13 | 3.1 | SCE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0
OLINDA_2_LNDFL2 | Brea Power II | GEN | 2012-11-01 | 2012 | BIOGAS | COMBINED CYCLE |  | 28.1 | 35.7 | SCE | NQC | FC | 25.9 | 26.23 | 26.22 | 24.03 | 26.31 | 25.12 | 25.3 | 24.99 | 25.06 | 25.49 | 25.94 | 25.99
OLINDA_7_BLKSND | BlackSand Generating Facility | GEN | 2000-06-01 | 2000 | WASTE TO POWER | COMBUSTION TURBINE |  | 5.6 | 8 | SCE | NQC | FC | 0.11 | 0.1 | 0.15 | 0.22 | 0.29 | 0.38 | 0.36 | 0.25 | 0.98 | 1.28 | 1.04 | 1.48
OLIVEP_1_SOLAR | White River Solar | GEN | 2013-06-22 | 2013 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
OLIVEP_1_SOLAR2 | White River West | GEN | 2014-10-01 | 2014 | SUN | PHOTO VOLTAIC |  | 19.75 | 19.8 | PGAE | NQC | FC | 0.08 | 0.59 | 0.69 | 0.87 | 1.26 | 2.59 | 2.84 | 2.45 | 2.19 | 1.46 | 1.13 | 0.69
OLSEN_2_UNIT | OLSEN POWER PARTNERS | GEN | 1990-01-03 | 1990 | WATER | HYDRO |  | 5.5 | 5.8 | PGAE | NQC | FC | 1.16 | 0.88 | 0.97 | 2.3 | 2.06 | 0.57 | 0.02 | 0 | 0 | 0.11 | 0.09 | 0.35
OMAR_2_UNIT 1 | KERN RIVER COGENERATION CO. UNIT 1 | GEN | 1985-05-01 | 1985 | NATURAL GAS | FTUR |  | 75 | 85 | SCE | NQC | FC | 75 | 75 | 75 | 75 | 74.67 | 73.67 | 73 | 72.67 | 73.67 | 74.33 | 75 | 75
OMAR_2_UNIT 2 | KERN RIVER COGENERATION CO. UNIT 2 | GEN | 1985-05-01 | 1985 | NATURAL GAS | FTUR |  | 75 | 85 | SCE | NQC | FC | 75 | 75 | 75 | 75 | 74.67 | 73.67 | 73.33 | 73 | 73.67 | 74.67 | 75 | 75
OMAR_2_UNIT 3 | KERN RIVER COGENERATION CO. UNIT 3 | GEN | 1985-05-01 | 1985 | NATURAL GAS | FTUR |  | 75 | 85 | SCE | NQC | FC | 75 | 75 | 75 | 75 | 73.67 | 73.67 | 73.33 | 73 | 73.67 | 75 | 75 | 75
OMAR_2_UNIT 4 | KERN RIVER COGENERATION CO. UNIT 4 | GEN | 1985-05-01 | 1985 | NATURAL GAS | FTUR |  | 75 | 85 | SCE | NQC | FC | 75 | 75 | 75 | 75 | 74 | 73.33 | 73.67 | 73.67 | 74.33 | 75 | 75 | 75
ONLLPP_6_UNIT 1 | O'NEILL PUMP-GEN UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 4.2 | 4.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ONLLPP_6_UNIT 2 | O'NEILL PUMP-GEN UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 4.2 | 4.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ONLLPP_6_UNIT 3 | O'NEILL PUMP-GEN UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 4.2 | 4.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ONLLPP_6_UNIT 4 | O'NEILL PUMP-GEN UNIT 4 | GEN | 0 |  | WATER | HYDRO |  | 4.2 | 4.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ONLLPP_6_UNIT 5 | O'NEILL PUMP-GEN UNIT 5 | GEN | 0 |  | WATER | HYDRO |  | 4.2 | 4.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ONLLPP_6_UNIT 6 | O'NEILL PUMP-GEN UNIT 6 | GEN | 0 |  | WATER | HYDRO |  | 4.2 | 4.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ONLLPP_6_UNITS | O'NEILL PUMP-GEN (AGGREGATE) | GEN | 2017-11-30 | 2017 | WATER | 0 |  | 25.2 | 0 | PGAE | NQC | FC | 0 | 0.74 | 0.07 | 0.18 | 12.91 | 1.8 | 1.49 | 0.63 | 0.05 | 0.71 | 0.15 | 0
ORLND_6_HIGHLI | High Line Canal Hydro | GEN | 2014-06-11 | 2014 | WATER | HYDRO |  | 0.5 | 0.6 | PGAE | NQC | FC | 0 | 0 | 0 | 0.04 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ORLND_6_SOLAR1 | Enerparc California 2 | GEN | 2016-03-23 | 2016 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | FC | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
ORMOND_7_UNIT 1 | ORMOND BEACH GEN STA. UNIT 1 | GEN | 1971-01-01 | 1971 | NATURAL GAS | STEAM | Yes | 741.27 | 750 | SCE | NQC | FC | 741.27 | 741.27 | 741.27 | 741.27 | 741.27 | 741.27 | 741.27 | 741.27 | 741.27 | 741.27 | 741.27 | 741.27
ORMOND_7_UNIT 2 | ORMOND BEACH GEN STA. UNIT 2 | GEN | 1971-01-01 | 1971 | NATURAL GAS | STEAM | Yes | 750 | 750 | SCE | NQC | FC | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750
OROLOM_1_SOLAR1 | Oro Loma Solar 1 | GEN | 2017-01-28 | 2017 | SUN | PHOTO VOLTAIC |  | 10 | 10 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OROLOM_1_SOLAR2 | Oro Loma Solar 2 | GEN | 2017-01-28 | 2017 | SUN | PHOTO VOLTAIC |  | 10 | 10 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OROVIL_6_UNIT | Oroville Cogeneration, LP | GEN | 1989-12-18 | 1989 | NATURAL GAS | RECIPROCATING ENGINE |  | 7.5 | 9.8 | PGAE | NQC | FC | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
ORTGA_6_ME1SL1 | Merced 1 | GEN | 2018-04-12 | 2018 | SUN | PHOTO VOLTAIC |  | 3 | 3 | PGAE | NQC | FC | 0.01 | 0.09 | 0.11 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.11
OSO_6_NSPIN | OSO_6_NSPIN | GEN | 0 |  | WATER | PUMP |  | 70 | 70.8 | SCE | NQC | FC | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
OTAY_6_ECVBT1 | EnerSmart Chula Vista 1 | GEN | 0 |  | LESR | OTHER |  | 3 | 3 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTAY_6_ECVBT2 | Chula Vista 2 | GEN | 0 |  | LESR | OTHER |  | 3 | 3 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTAY_6_PL1X2 | Chula Vista Energy Center, LLC | GEN | 2006-06-08 | 2006 | NATURAL GAS | COMBUSTION TURBINE |  | 39.57 | 40 | SDGE | NQC | PD | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2
OTMESA_2_CTG1 | OTAY MESA COMBUSTION TURBINE 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 208 | 208 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTMESA_2_CTG2 | OTAY MESA COMBUSTION TURBINE 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 208 | 208 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTMESA_2_PL1X3 | OTAY MESA ENERGY CENTER | GEN | 2009-10-02 | 2009 | NATURAL GAS | COMBINED CYCLE |  | 603.68 | 689 | SDGE | NQC | FC | 603.6 | 603.6 | 603.6 | 603.6 | 603.6 | 603.6 | 603.6 | 603.6 | 603.6 | 603.6 | 603.6 | 603.6
OTMESA_2_STG3 | OTAY MESA STEAM TURBINE 3 | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 290.7 | 290.7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OXBOW_6_DRUM | OXBOW HYDRO | GEN | 1966-01-01 | 1966 | WATER | HYDRO |  | 5.8 | 6 | PGAE | NQC | FC | 2.1 | 1.45 | 1.51 | 2.92 | 1.54 | 1.24 | 1.83 | 2.41 | 1.64 | 0.02 | 0.97 | 1.18
OXMTN_6_LNDFIL | Ox Mountain Landfill Generating Plant | GEN | 2009-04-01 | 2009 | BIOGAS | RECIPROCATING ENGINE |  | 10.62 | 13.3 | PGAE | NQC | FC | 10.62 | 10.62 | 10.62 | 10.62 | 10.5 | 10.38 | 10.57 | 10.29 | 10.38 | 10.3 | 10.46 | 10.62
PACLUM_6_UNIT | Humboldt Redwood | GEN | 2017-06-01 | 2017 | BIOMASS | STEAM |  | 28.8 | 28.8 | PGAE | NQC | FC | 14.62 | 12.54 | 11.91 | 11.66 | 14.79 | 15.29 | 14.72 | 12.65 | 14.37 | 15.23 | 13.29 | 14.04
PADUA_2_ONTARO | ONTARIO/SIERRA HYDRO PSP | GEN | 1902-01-01 | 1902 | WATER | HYDRO |  | 1.92 | 1 | SCE | NQC | FC | 0.89 | 0.92 | 0.83 | 0.82 | 0.86 | 0.75 | 0.75 | 0.64 | 0.53 | 0.44 | 0.4 | 0.48
PADUA_2_SOLAR1 | Kona Solar - Rancho DC #1 | GEN | 2015-06-02 | 2015 | SUN | PHOTO VOLTAIC |  | 1.75 | 1.8 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PADUA_6_MWDSDM | San Dimas Hydroelectric Recovery Plant | GEN | 1981-01-01 | 1981 | WATER | HYDRO |  | 9.9 | 9.9 | SCE | NQC | FC | 0 | 0.8 | 3.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 1.6 | 1.6 | 6.4 | 4.8
PADUA_6_QF | PADUA QFS | GEN | 1984-01-01 | 1984 | OTHER | OTHER |  | 1.82 | 30.1 | SCE | NQC | FC | 0.17 | 0.29 | 0.24 | 0.28 | 0.35 | 0.39 | 0.4 | 0.34 | 0.36 | 0.32 | 0.32 | 0.22
PADUA_7_SDIMAS | San Dimas Wash Hydro | GEN | 1986-01-28 | 1986 | WATER | HYDRO |  | 1.05 | 2 | SCE | NQC | FC | 0 | 0 | 0 | 0 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
PAIGES_6_SOLAR | Paige Solar | GEN | 2017-03-09 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 22 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PALA_6_PGCBT1 | Pala Gomez Creek BESS | GEN | 0 |  | LESR | OTHER |  | 10 | 10 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PALOMR_2_PL1X3 | Palomar Energy Center | GEN | 2005-10-14 | 2005 | NATURAL GAS | COMBINED CYCLE |  | 588.21 | 0 | SDGE | NQC | FC | 588.21 | 588.21 | 588.21 | 588.21 | 588.21 | 588.21 | 588.21 | 588.21 | 588.21 | 588.21 | 588.21 | 588.21
PALOMR_7_CTG1 | PALOMR_7_CTG1 | GEN | 0 |  | 0 | COMBUSTION TURBINE |  | 188 | 188 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PALOMR_7_CTG2 | PALOMR_7_CTG2 | GEN | 0 |  | 0 | COMBUSTION TURBINE |  | 188 | 188 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PALOMR_7_STG3 | PALOMR_7_STG3 | GEN | 0 |  | 0 | STEAM |  | 260 | 260 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PANERO_2_MWPWD1 | Mesa Wind Project | GEN | 0 |  | WIND | WIND |  | 30 | 30 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PARDEB_2_UNIT 1 | PARDEE HYDRO UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 10 | 10 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PARDEB_2_UNIT 2 | PARDEE HYDRO UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 10 | 10 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PARDEB_2_UNIT 3 | PARDEE HYDRO UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 10 | 10 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PARDEB_6_UNITS | Pardee Power House | GEN | 1930-01-01 | 1930 | WATER | HYDRO |  | 30 | 0 | PGAE | NQC | FC | 15.76 | 14.96 | 15.76 | 23.6 | 24 | 24 | 14.96 | 14.96 | 14.96 | 14.96 | 14.16 | 15.76
PARDSE_6_PESBT1 | Paradise Energy Storage | GEN | 0 |  | LESR | OTHER |  | 9.75 | 9.75 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PBLOSM_2_SOLAR | PearBlossom | GEN | 2016-12-29 | 2016 | SUN | PHOTO VOLTAIC |  | 9.5 | 9.5 | SCE | NQC | FC | 0.04 | 0.29 | 0.33 | 0.42 | 0.61 | 1.24 | 1.37 | 1.18 | 1.05 | 0.7 | 0.54 | 0.33
PEABDY_2_LNDFIL | G2 Energy Hay Road Power Plant | GEN | 2013-07-09 | 2013 | BIOGAS | RECIPROCATING ENGINE |  | 1.6 | 1.6 | PGAE | NQC | FC | 1.54 | 1.54 | 1.49 | 1.53 | 1.52 | 1.51 | 1.51 | 1.51 | 1.51 | 1.52 | 1.53 | 1.52
PEABDY_2_LNDFL1 | Potrero Hills Energy Producers | GEN | 2016-04-07 | 2016 | BIOGAS | RECIPROCATING ENGINE |  | 8 | 8 | PGAE | NQC | FC | 7.7 | 7.67 | 7.54 | 7.57 | 7.03 | 7.39 | 7.56 | 7.54 | 7.52 | 7.41 | 7.47 | 7.22
PEARBL_2_NSPIN | PEARBL_2_NSPIN | GEN | 0 |  | WATER | PUMP |  | 118 | 151.2 | SCE | NQC | FC | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
PEASE_1_TBEBT1 | Tierra Buena Energy Storage | GEN | 2022-06-01 | 2022 | LESR | OTHER |  | 6 | 6 | PGAE | NQC | PD | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
PEORIA_1_SOLAR | Sonora 1 | GEN | 2013-12-23 | 2013 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | FC | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
PGEB_2_PDRP100 | PGEB_2_PDRP100 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGEB_2_PDRP101 | PGEB_2_PDRP101 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGEB_2_PDRP102 | PGEB_2_PDRP102 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGEB_2_PDRP103 | PGEB_2_PDRP103 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGEB_2_PDRP104 | PGEB_2_PDRP104 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGEB_2_PDRP105 | PGEB_2_PDRP105 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE | NQC | FC |  |  | 0.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGEB_2_PDRP107 | VLTS_PDR_PGEB_02 | GEN | 0 |  | OTHER | OTHER |  | 7.5 | 0 | PGAE | NQC | FC | 0.17 | 0.21 | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGEB_2_PDRP108 | PGEB | GEN | 0 |  | OTHER | OTHER |  | 9.9 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGEB_2_PDRP111 | VLTS_PDR_PGEB_03 | GEN | 0 |  | OTHER | OTHER |  | 4 | 0 | PGAE | NQC | FC | 0.14 | 0.16 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGEB_2_PDRP112 | PGEB_2_PDRP112 | GEN | 0 |  | OTHER | OTHER |  | 3 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGEB_2_PDRP113 | PGEB_2_PDRP113 | GEN | 0 |  | OTHER | OTHER |  | 3 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP101 | PGF1_2_PDRP101 | GEN | 0 |  | OTHER | OTHER |  | 0.51 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP103 | PGF1 | GEN | 0 |  | OTHER | OTHER |  | 9.9 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP104 | PGF1_2_PDRP104 | GEN | 0 |  | OTHER | OTHER |  | 4.8 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP105 | PGF1_2_PDRP105 | GEN | 0 |  | OTHER | OTHER |  | 4.8 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP106 | PGF1_2_PDRP106 | GEN | 0 |  | OTHER | OTHER |  | 4.8 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP107 | PGF1_2_PDRP107 | GEN | 0 |  | OTHER | OTHER |  | 4.8 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP108 | VLTS_PDR_PGF1_02 | GEN | 0 |  | OTHER | OTHER |  | 9.95 | 0 | PGAE | NQC | FC | 2.67 | 2.13 | 2.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP109 | PGF1_2_PDRP109 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE | NQC | FC | 0.59 | 0.24 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP110 | PGF1_2_PDRP110 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE | NQC | FC | 0.12 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP111 | VLTS_PDR_PGF1_03 | GEN | 0 |  | OTHER | OTHER |  | 9.9 | 0 | PGAE | NQC | FC | 3.2 | 3.2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGF1_2_PDRP116 | VLTS_PDR_PGF1_04 | GEN | 0 |  | OTHER | OTHER |  | 9.9 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGSB_1_PDRP101 | VLTS_PDR_PGSB_04 | GEN | 0 |  | OTHER | OTHER |  | 9.95 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGSB_1_PDRP102 | PGSB_1_PDRP102 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGSB_1_PDRP103 | PGSB_1_PDRP103 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGSB_1_PDRP104 | PGSB_1_PDRP104 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | PGAE | NQC | FC | 0.53 | 0.73 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGSB_1_PDRPCON01 | CVP Load Shift PGSB | GEN | 0 |  | DISPATCHABLE DEMAND RESPONSE | OTHER |  | 0 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGSB_1_PDRPCUR01 | CVP Load Shift PGSB | GEN | 0 |  | OTHER | OTHER |  | 0.1 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGSI_1_PDRP101 | PGSI_1_PDRP101 | GEN | 0 |  | OTHER | OTHER |  | 9 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHOENX_1_UNIT | PHOENIX PH | GEN | 1940-01-01 | 1940 | WATER | HYDRO |  | 2 | 2 | PGAE | NQC | FC | 0.62 | 0.51 | 0.71 | 0.87 | 0.77 | 0.79 | 0.96 | 1.02 | 1.06 | 0.59 | 0.19 | 0
PINFLT_7_UNIT 1 | Pine Flat Unit 1 | GEN | 0 |  | WATER | HYDRO |  | 63.3 | 63.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PINFLT_7_UNIT 2 | PINFLT_7_UNIT 2 | GEN | 0 |  | 0 | 0 |  | 63.3 | 63.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PINFLT_7_UNIT 3 | Pine Flat Unit 3 | GEN | 0 |  | WATER | HYDRO |  | 63.3 | 63.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PINFLT_7_UNITS | PINE FLAT HYDRO AGGREGATE | GEN | 1984-01-01 | 1984 | WATER | HYDRO |  | 198.51 | 0 | PGAE | NQC | FC | 0 | 24.35 | 36.6 | 65.5 | 104 | 165.54 | 176.65 | 120.84 | 36.57 | 11.5 | 0 | 0
PIOPIC_2_CTG1 | Pio Pico Unit 1 | GEN | 2016-11-03 | 2016 | NATURAL GAS | COMBUSTION TURBINE |  | 111.3 | 111.3 | SDGE | NQC | FC | 111.3 | 111.3 | 111.3 | 111.3 | 111.3 | 111.3 | 111.3 | 111.3 | 111.3 | 111.3 | 111.3 | 111.3
PIOPIC_2_CTG2 | Pio Pico Unit 2 | GEN | 2016-11-03 | 2016 | NATURAL GAS | COMBUSTION TURBINE |  | 112.7 | 112.7 | SDGE | NQC | FC | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7
PIOPIC_2_CTG3 | Pio Pico Unit 3 | GEN | 2016-11-03 | 2016 | NATURAL GAS | COMBUSTION TURBINE |  | 112 | 112 | SDGE | NQC | FC | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
PIT1_6_FRIVRA | Fall River Mills Project A | GEN | 2014-03-05 | 2014 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | ID | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
PIT1_7_UNIT 1 | PIT PH 1 UNIT 1 | GEN | 1922-01-01 | 1922 | WATER | HYDRO |  | 32 | 32 | PGAE | NQC | FC | 21.2 | 18.4 | 19 | 16 | 16.8 | 10.83 | 10.8 | 9.51 | 9.2 | 8 | 14.4 | 15.68
PIT1_7_UNIT 2 | PIT PH 1 UNIT 2 | GEN | 1922-01-01 | 1922 | WATER | HYDRO |  | 32 | 32 | PGAE | NQC | FC | 14.4 | 14.4 | 15.68 | 14.4 | 15.68 | 10.8 | 8.6 | 9.2 | 9.2 | 4.8 | 14.4 | 15.68
PIT3_7_PL1X3 | PIT PH 3 UNITS 1, 2 & 3 AGGREGATE | GEN | 1925-01-01 | 1925 | WATER | HYDRO |  | 70.6 | 0 | PGAE | NQC | FC | 36 | 35.68 | 28.8 | 34.4 | 42.4 | 46 | 52.4 | 47.6 | 26.4 | 28 | 29.6 | 36.6
PIT3_7_UNIT 1 | PIT PH 3 UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 24 | 24 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PIT3_7_UNIT 2 | Pit PH 3 Unit 2 | GEN | 0 |  | WATER | HYDRO |  | 26 | 26 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PIT3_7_UNIT 3 | Pit PH 3 Unit 3 | GEN | 0 |  | WATER | HYDRO |  | 25 | 25 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PIT4_7_PL1X2 | PIT PH 4 UNITS 1 & 2 AGGREGATE | GEN | 1955-01-01 | 1955 | WATER | HYDRO |  | 95 | 0 | PGAE | NQC | FC | 50.2 | 40.8 | 44 | 44.8 | 40.8 | 55.2 | 60.6 | 55.6 | 36.4 | 40.8 | 44.6 | 48.8
PIT4_7_UNIT 1 | PIT PH 4 UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 55 | 55 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PIT4_7_UNIT 2 | Pit PH 4 Unit 2 | GEN | 0 |  | WATER | HYDRO |  | 47 | 47 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PIT5_7_PL1X2 | PIT PH 5 UNITS 1 & 2 AGGREGATE | GEN | 1944-01-01 | 1944 | WATER | HYDRO |  | 82 | 0 | PGAE | NQC | FC | 36 | 31.2 | 32 | 31.2 | 32 | 32 | 34.4 | 32.8 | 28 | 18.4 | 44 | 40
PIT5_7_PL3X4 | PIT PH 5 UNITS 3 & 4 AGGREGATE | GEN | 1944-01-01 | 1944 | WATER | HYDRO |  | 82 | 0 | PGAE | NQC | FC | 32 | 36.8 | 28.8 | 32 | 32 | 32.8 | 36.8 | 39.2 | 34.4 | 43 | 28.8 | 32
PIT5_7_QFUNTS | GRASSHOPPER FLAT HYDRO | GEN | 1987-08-15 | 1987 | WATER | HYDRO |  | 1.1 | 3.8 | PGAE | NQC | FC | 0.26 | 0.29 | 0.15 | 0.3 | 0.08 | 0 | 0 | 0 | 0 | 0.01 | 0.05 | 0.03
PIT5_7_UNIT 1 | PIT PH 5 UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 41 | 41 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PIT5_7_UNIT 2 | Pit PH 5 Unit 2 | GEN | 0 |  | WATER | HYDRO |  | 41 | 41 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PIT5_7_UNIT 3 | PIT PH 5 UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 41 | 41 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PIT5_7_UNIT 4 | Pit PH 5 Unit 4 | GEN | 0 |  | WATER | HYDRO |  | 41 | 41 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PIT6_7_UNIT 1 | PIT PH 6 UNIT 1 | GEN | 1965-01-01 | 1965 | WATER | HYDRO |  | 39 | 39 | PGAE | NQC | FC | 30.85 | 30.62 | 31.14 | 37.78 | 38 | 37.16 | 37.52 | 37.62 | 30.62 | 30.71 | 37.06 | 38.12
PIT6_7_UNIT 2 | PIT PH 6 UNIT 2 | GEN | 1965-01-01 | 1965 | WATER | HYDRO |  | 40 | 40 | PGAE | NQC | FC | 36.97 | 37.74 | 38.4 | 38.03 | 31.1 | 37.58 | 37.45 | 37.7 | 37.44 | 30.42 | 37.13 | 38.18
PIT7_7_UNIT 1 | PIT PH 7 UNIT 1 | GEN | 1965-01-01 | 1965 | WATER | HYDRO |  | 55.7 | 55.7 | PGAE | NQC | FC | 53 | 51.72 | 52.76 | 52.21 | 51.56 | 52.34 | 53.04 | 53.55 | 53.4 | 51.38 | 42.4 | 53.08
PIT7_7_UNIT 2 | PIT PH 7 UNIT 2 | GEN | 1965-01-01 | 1965 | WATER | HYDRO |  | 54.6 | 54.6 | PGAE | NQC | FC | 51.36 | 49.56 | 51.76 | 51.96 | 41.76 | 51.36 | 52.32 | 53.43 | 53.38 | 52.89 | 53.18 | 42.41
PIUTE_6_GNBSR1 | Green Beanworks B | GEN | 2018-12-28 | 2018 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE | NQC | FC | 0.01 | 0.09 | 0.11 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.11
PLACVL_1_CHILIB | Chili Bar Powerhouse | GEN | 1965-01-01 | 1965 | WATER | HYDRO |  | 8.34 | 8.4 | PGAE | NQC | FC | 1.14 | 0.95 | 1.63 | 3.8 | 3.72 | 1.35 | 0.79 | 1.89 | 1.55 | 1.04 | 0.78 | 1.54
PLACVL_1_RCKCRE | Rock Creek Hydro | GEN | 2017-03-29 | 2017 | WATER | HYDRO |  | 5 | 3.6 | PGAE | NQC | FC | 0.16 | 0.04 | 0.12 | 0.19 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.04
PLAINV_6_BSOLAR | Western Antelope Blue Sky Ranch A | GEN | 2014-11-07 | 2014 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLAINV_6_DSOLAR | Western Antelope Dry Ranch | GEN | 2016-12-01 | 2016 | SUN | PHOTO VOLTAIC |  | 10 | 10 | SCE | NQC | FC | 0.04 | 0.3 | 0.35 | 0.44 | 0.64 | 1.31 | 1.44 | 1.24 | 1.11 | 0.74 | 0.57 | 0.35
PLAINV_6_NLRSR1 | North Lancaster Ranch | GEN | 2016-12-31 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLAINV_6_SOLAR3 | Sierra Solar Greenworks LLC | GEN | 2015-11-30 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLAINV_6_SOLARC | Central Antelope Dry Ranch C | GEN | 2016-05-06 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PLMSSR_6_HISIER | High Sierra Cogeneration Aggregate | GEN | 2010-04-22 | 2010 | NATURAL GAS | RECIPROCATING ENGINE |  | 6 | 6 | PGAE | NQC | FC | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
PLSNTG_7_LNCLND | Lincoln Landfill Power Plant | GEN | 1985-01-01 | 1985 | BIOGAS | RECIPROCATING ENGINE |  | 4.98 | 5 | PGAE | NQC | FC | 3.68 | 3.75 | 3.84 | 3.86 | 3.97 | 4 | 3.96 | 3.78 | 3.68 | 3.73 | 3.52 | 3.71
PMDLET_6_SOLAR1 | SEPV Palmdale East, LLC | GEN | 2015-07-31 | 2015 | SUN | PHOTO VOLTAIC |  | 10 | 10 | SCE | NQC | FC | 0.04 | 0.3 | 0.35 | 0.44 | 0.64 | 1.31 | 1.44 | 1.24 | 1.11 | 0.74 | 0.57 | 0.35
PMPJCK_1_RB2SLR | Rio Bravo Solar 2 | GEN | 2016-12-29 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
PMPJCK_1_SOLAR1 | Pumpjack Solar I | GEN | 2015-01-27 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
PMPJCK_1_SOLAR2 | Rio Bravo Solar 1 | GEN | 2016-12-21 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
PNCHEG_2_CTG1 | PANOCHE ENERGY CENTER (CTG1) | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 104.25 | 104.25 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PNCHEG_2_CTG2 | PANOCHE ENERGY CENTER (CTG2) | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 104.25 | 104.25 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PNCHEG_2_CTG3 | PANOCHE ENERGY CENTER (CTG3) | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 104.25 | 104.25 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PNCHEG_2_CTG4 | PANOCHE ENERGY CENTER (CTG4) | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 104.25 | 104.25 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PNCHEG_2_PL1X4 | PANOCHE ENERGY CENTER (Aggregated) | GEN | 2009-05-27 | 2009 | NATURAL GAS | COMBUSTION TURBINE |  | 417 | 0 | PGAE | NQC | ID | 417 | 417 | 417 | 417 | 416 | 412 | 403 | 403 | 408 | 416 | 417 | 417
PNCHPP_1_CTG1 | STARWOOD POWER - MIDWAY UNIT 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 82.3 | 82.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PNCHPP_1_CTG2 | STARWOOD POWER - MIDWAY UNIT 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 82.3 | 82.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PNCHPP_1_PL1X2 | Midway Peaking Aggregate | GEN | 2009-05-03 | 2009 | NATURAL GAS | COMBUSTION TURBINE |  | 119.91 | 0 | PGAE | NQC | FC | 119.91 | 119.91 | 119 | 117.54 | 119.91 | 119.91 | 119.91 | 119.91 | 119.91 | 119.91 | 119.91 | 119.91
PNCHVS_2_SOLAR | Panoche Valley Solar | GEN | 2018-11-26 | 2018 | SUN | PHOTO VOLTAIC |  | 140 | 0 | PGAE | NQC | FC | 0.56 | 4.2 | 4.9 | 6.16 | 8.96 | 18.34 | 20.16 | 17.36 | 15.54 | 10.36 | 7.98 | 4.9
PNCHVS_2_SOLARA | PNCHVS_2_SOLARA | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 69.5 | 69.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PNCHVS_2_SOLARB | PNCHVS_2_SOLARB | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 74.4 | 74.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PNOCHE_1_PL1X2 | Panoche Peaker | GEN | 2005-06-14 | 2005 | NATURAL GAS | COMBUSTION TURBINE |  | 49.97 | 0 | PGAE | NQC | FC | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97
PNOCHE_1_UNITA1 | CalPeak Power Panoche Unit 1 | GEN | 2001-12-27 | 2001 | NATURAL GAS | COMBUSTION TURBINE |  | 52.3 | 57 | PGAE | NQC | PD | 52.01 | 52.01 | 52.01 | 52.01 | 52.01 | 52.01 | 52.01 | 52.01 | 52.01 | 52.01 | 52.01 | 52.01
PNOCHE_7_CTG1 | Panoche Peaker Facility | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 49 | 49 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PNOCHE_7_ICE2 | Panoche Peaker Facility | GEN | 0 |  | NATURAL GAS | RECIPROCATING ENGINE |  | 0.3 | 0.3 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POEPH_7_UNIT 1 | POE HYDRO UNIT 1 | GEN | 1958-01-01 | 1958 | WATER | HYDRO |  | 68 | 68 | PGAE | NQC | FC | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 9.6 | 9.81
POEPH_7_UNIT 2 | POE HYDRO UNIT 2 | GEN | 1958-01-01 | 1958 | WATER | HYDRO |  | 68.5 | 68.5 | PGAE | NQC | FC | 20.82 | 20.82 | 20.82 | 20.82 | 20.82 | 20 | 20.82 | 20.82 | 20.82 | 20.4 | 16.34 | 15.3
POLRIS_2_ASEBT1 | Antelope Solar 2 Estrella BESS | GEN | 2023-12-29 | 2023 | LESR | OTHER |  | 28 | 28 | SCE | NQC | ID |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
POLRIS_2_ASESR1 | Antelope Solar 2 Estrella | GEN | 2023-12-29 | 2023 | SUN | PHOTO VOLTAIC |  | 56 | 56 | SCE | NQC | ID |  | 1.17 | 1.41 | 1.89 | 2.82 | 5.8 | 6.32 | 5.35 | 4.64 | 2.94 | 2.06 | 1
POLRIS_2_ASRBT1 | Antelope Solar 2 Raceway BESS | GEN | 0 |  | LESR | OTHER |  | 80 | 80 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POLRIS_2_ASRSR1 | Antelope Solar 2 Raceway | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 125 | 125 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POTTER_7_VECINO | Vecino Vineyards LLC | GEN | 1990-03-27 | 1990 | WATER | HYDRO |  | 1.25 | 1.3 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRCTVY_1_MIGBT1 | Miguel BESS | GEN | 2018-12-12 | 2018 | LESR | OTHER |  | 2 | 2 | SDGE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRIMM_2_SOLAR1 | Silver State South | GEN | 2016-08-23 | 2016 | SUN | PHOTO VOLTAIC |  | 250 | 0 | SCE | NQC | FC | 1 | 7.5 | 8.75 | 11 | 16 | 32.75 | 36 | 31 | 27.75 | 18.5 | 14.25 | 8.75
PRIMM_2_SOLRA1 | PRIMM_2_SOLRA1 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 136.5 | 136.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRIMM_2_SOLRB1 | PRIMM_2_SOLRB1 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 136.5 | 136.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PROXSR_2_PROSR1 | Proxima Solar | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 120 | 120 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PROXSR_2_PS1BT1 | Proxima Solar BESS 1A | GEN | 0 |  | LESR | OTHER |  | 40 | 40 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PROXSR_2_PS1BT2 | Proxima Solar BESS 1B | GEN | 0 |  | LESR | OTHER |  | 32 | 32 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PROXSR_2_PS1SR2 | Proxima Solar 1B | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 69.74 | 70 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PROXSR_2_PS2BT3 | Proxima Solar BESS 2 | GEN | 0 |  | LESR | OTHER |  | 90 | 90 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PSWEET_1_STCRUZ | Santa Cruz Energy LLC | GEN | 2010-02-06 | 2010 | BIOGAS | RECIPROCATING ENGINE |  | 1.6 | 1.6 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PUTHCR_1_PCNSB1 | Putah Creek Solar Farm North | GEN | 2022-10-15 | 2022 | HYBD | OTHER |  | 3 | 3 | PGAE | NQC | ID | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
PUTHCR_1_SOLAR1 | Putah Creek Solar Farm | GEN | 2014-12-19 | 2014 | SUN | PHOTO VOLTAIC |  | 1.98 | 2 | PGAE | NQC | FC | 0.01 | 0.06 | 0.07 | 0.09 | 0.13 | 0.26 | 0.29 | 0.25 | 0.22 | 0.15 | 0.11 | 0.07
PVERDE_5_SCEDYN | PVERDE_5_SCEDYN | TG | 0 |  | URANIUM | 0 |  | 635 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PWEST_1_UNIT | PACIFIC WEST 1 WIND GENERATION | GEN | 0 |  | WIND | WIND |  | 2.1 | 2.1 | SCE | NQC | FC | 0.37 | 0.39 | 0.35 | 0.33 | 0.35 | 0.32 | 0.3 | 0.23 | 0.24 | 0.22 | 0.3 | 0.36
RALSTN_7_UNIT 1 | RALSTON UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 86 | 86 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAMON_2_SCEDYN | RAMON_2_SCEDYN | TG | 0 |  | GEOTHERMAL | OTHER |  | 106.18 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RANCHO_2_SMUDSYSDYN | SMUD Regulation Market | TG | 2017-03-01 | 2017 | OTHER | OTHER |  | 124 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RATSKE_2_NROSR1 | North Rosamond Solar | GEN | 2019-06-11 | 2019 | SUN | PHOTO VOLTAIC |  | 150 | 150 | SCE | NQC | FC | 0.6 | 4.5 | 5.25 | 6.6 | 9.6 | 19.65 | 21.6 | 18.6 | 16.65 | 11.1 | 8.55 | 5.25
RATSKE_2_RBSSB1 | Rabbitbrush Solar 1 | GEN | 2022-10-18 | 2022 | HYBD | OTHER |  | 60 | 60 | SCE | NQC | ID | 7.72 | 9.16 | 9.45 | 9.99 | 11.14 | 14.95 | 15.67 | 14.51 | 13.74 | 11.62 | 10.62 | 9.34
RATSKE_2_RBSSB2 | Rabbitbrush Solar 2 | GEN | 2022-10-18 | 2022 | HYBD | OTHER |  | 40 | 40 | SCE | NQC | ID | 5.14 | 6.09 | 6.29 | 6.65 | 7.41 | 9.95 | 10.43 | 9.66 | 9.13 | 7.72 | 7.04 | 6.2
RCKCRK_7_UNIT 1 | ROCK CREEK HYDRO UNIT 1 | GEN | 1950-01-01 | 1950 | WATER | HYDRO |  | 57 | 57 | PGAE | NQC | FC | 13.9 | 13.9 | 13.9 | 13.9 | 10.72 | 13.9 | 13.9 | 13.9 | 13.9 | 0 | 5.6 | 13.43
RCKCRK_7_UNIT 2 | ROCK CREEK HYDRO UNIT 2 | GEN | 1950-01-01 | 1950 | WATER | HYDRO |  | 56.9 | 56.9 | PGAE | NQC | FC | 17.33 | 17.33 | 17.33 | 17.33 | 17.33 | 17.33 | 17.33 | 17.33 | 17.33 | 0 | 0 | 17.33
RDWAY_1_CREST | CREST Contracts | GEN | 2016-09-14 | 2016 | SUN | PHOTO VOLTAIC |  | 6.5 | 8.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RDWAY_1_SCKSR1 | Sheep Creek | GEN | 2023-07-28 | 2023 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RDWAY_1_WA2SR3 | Watts II | GEN | 2024-01-15 | 2024 | SUN | PHOTO VOLTAIC |  | 0.5 | 0.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RDWAY_1_WAISR2 | Watts I | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RECTOR_2_CREST | Rector Aggregate Solar Resources | GEN | 2016-12-23 | 2016 | SUN | PHOTO VOLTAIC |  | 10.5 | 17.3 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RECTOR_2_IVANPV | Ivanhoe Tulare PV | GEN | 2022-01-28 | 2022 | SUN | PHOTO VOLTAIC |  | 3.5 | 3.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RECTOR_2_KAWEAH | KAWEAH PH 2 & 3 PSP AGGREGATE | GEN | 1913-01-01 | 1913 | WATER | HYDRO |  | 6.55 | 6.6 | SCE | NQC | FC | 0.85 | 1.11 | 1.6 | 1.93 | 1.98 | 1.83 | 0.39 | 0.03 | 0 | 0 | 0 | 0
RECTOR_2_KAWH 1 | KAWEAH PH 1 UNIT 1 | GEN | 1929-01-01 | 1929 | WATER | HYDRO |  | 2.25 | 2.3 | SCE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.04 | 0.03 | 0 | 0 | 0 | 0
RECTOR_2_QF | Kaweah Unit 1 | GEN | 2020-05-18 | 2020 | WATER | HYDRO |  | 20.09 | 20.09 | SCE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 8.4 | 6.7 | 0 | 0 | 0 | 0 | 1.2
RECTOR_2_TFDBM1 | Two Fiets Dairy Digester | GEN | 2019-01-07 | 2019 | BIOGAS | RECIPROCATING ENGINE |  | 0.8 | 0.8 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RECTOR_2_VISSR1 | Visalia CSG | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RECTOR_7_TULARE | MM Tulare | GEN | 1998-05-08 | 1998 | BIOMASS | RECIPROCATING ENGINE |  | 1.5 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REDBLF_6_UNIT | RED BLUFF PEAKER PLANT | GEN | 2001-08-11 | 2001 | NATURAL GAS | RECIPROCATING ENGINE |  | 44 | 44 | PGAE | NQC | FC | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
REDMAN_2_SOLAR | Lancaster East Avenue F | GEN | 2017-08-25 | 2017 | SUN | PHOTO VOLTAIC |  | 3.75 | 3.8 | SCE | NQC | FC | 0.02 | 0.11 | 0.13 | 0.17 | 0.24 | 0.49 | 0.54 | 0.47 | 0.42 | 0.28 | 0.21 | 0.13
REDMAN_6_AVSSR1 | Antelope Valley Solar | GEN | 2019-02-04 | 2019 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE | NQC | FC | 0.01 | 0.09 | 0.11 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.11
REEDLY_6_SOLAR | Terzian | GEN | 2014-06-17 | 2014 | SUN | PHOTO VOLTAIC |  | 1.23 | 1.3 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RENWD_1_QF | Renwind re-powering project | GEN | 2013-01-08 | 2013 | WIND | WIND |  | 10 | 10.5 | SCE | NQC | FC | 1.77 | 1.88 | 1.65 | 1.58 | 1.68 | 1.54 | 1.43 | 1.09 | 1.12 | 1.04 | 1.41 | 1.7
RICHMN_1_CHVSR2 | Chevron 8.5 | GEN | 2017-12-21 | 2017 | SUN | PHOTO VOLTAIC |  | 8.5 | 8.5 | PGAE | NQC | ID | 0.03 | 0.26 | 0.3 | 0.37 | 0.54 | 1.11 | 1.22 | 1.05 | 0.94 | 0.63 | 0.48 | 0.3
RICHMN_1_SOLAR | Chevron 2 | GEN | 2017-12-21 | 2017 | SUN | PHOTO VOLTAIC |  | 2 | 2 | PGAE | NQC | ID | 0.01 | 0.06 | 0.07 | 0.09 | 0.13 | 0.26 | 0.29 | 0.25 | 0.22 | 0.15 | 0.11 | 0.07
RICHMN_7_BAYENV | BAY ENVIRONMENTAL (NOVE POWER) | GEN | 1985-01-01 | 1985 | BIOGAS | RECIPROCATING ENGINE |  | 2.5 | 2.5 | PGAE | NQC | FC | 0.64 | 0.63 | 0.4 | 0.38 | 0.35 | 0.37 | 0.35 | 0.37 | 0.07 | 0.25 | 0.35 | 0.18
RIOBRV_6_UNIT 1 | RIO BRAVO HYDRO | GEN | 1989-05-18 | 1989 | WATER | HYDRO |  | 14 | 14 | PGAE | NQC | FC | 0.14 | 0.19 | 0 | 1.51 | 2.42 | 4.12 | 3.39 | 1.31 | 0 | 0 | 0 | 0
RIOOSO_1_QF | SMALL QF AGGREGATION - GRASS VALLEY | GEN | 1984-01-01 | 1984 | WATER | HYDRO |  | 1.11 | 2.5 | PGAE | NQC | FC | 0.04 | 0.07 | 0.08 | 0.29 | 0.53 | 0.3 | 0.23 | 0.3 | 0.25 | 0.03 | 0.01 | 0.02
RNDMTN_2_SLSPHY1 | Silver Springs | GEN | 2017-08-10 | 2017 | WATER | HYDRO |  | 0.6 | 0.6 | PGAE | NQC | FC | 0.2 | 0.21 | 0.19 | 0.18 | 0.18 | 0.17 | 0.15 | 0.15 | 0.14 | 0.15 | 0.14 | 0.14
RNDSBG_1_HZASR1 | Hazel A | GEN | 2019-11-11 | 2019 | SUN | PHOTO VOLTAIC |  | 2.99 | 3 | SCE | NQC | FC | 0.01 | 0.09 | 0.1 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.1
ROLLIN_6_UNIT | ROLLINS HYDRO | GEN | 1980-01-01 | 1980 | WATER | HYDRO |  | 13.5 | 13.5 | PGAE | NQC | FC | 7.78 | 5.81 | 5.23 | 8.3 | 7.56 | 5.64 | 6.46 | 6.2 | 4.62 | 2.38 | 1.18 | 6.6
ROMOLA_5_MPBBT1 | Menifee Power Bank | GEN | 0 |  | LESR | OTHER |  | 230 | 230 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ROMOLA_5_MPBBT2 | Menifee Power Bank 2 | GEN | 0 |  | LESR | OTHER |  | 230 | 230 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ROMOLA_5_MPBBT3 | Menifee Power Bank 3 | GEN | 0 |  | LESR | OTHER |  | 50 | 50 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ROSMDW_2_WIND1 | Pacific Wind - Phase 1 | GEN | 2012-07-20 | 2012 | WIND | WIND |  | 140 | 141.3 | SCE | NQC | FC | 24.74 | 26.31 | 23.12 | 22.15 | 23.55 | 21.59 | 20.06 | 15.24 | 15.74 | 14.61 | 19.68 | 23.84
ROSMND_6_SOLAR | Lancaster B | GEN | 2017-04-22 | 2017 | SUN | PHOTO VOLTAIC |  | 3 | 3 | SCE | NQC | FC | 0.01 | 0.09 | 0.11 | 0.13 | 0.19 | 0.39 | 0.43 | 0.37 | 0.33 | 0.22 | 0.17 | 0.11
RSMSLR_6_SOLAR1 | Rosamond One | GEN | 2013-12-20 | 2013 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
RSMSLR_6_SOLAR2 | Rosamond Two | GEN | 2013-12-20 | 2013 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
RTEDDY_2_RWSBT1 | Rosamond West Solar Central BESS A1 | GEN | 0 |  | LESR | OTHER |  | 30 | 30 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RTEDDY_2_RWSBT2 | Rosamond West Solar Central BESS A2 | GEN | 0 |  | LESR | OTHER |  | 30 | 30 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RTEDDY_2_RWSBT3 | Rosamond West Solar Central BESS A3 | GEN | 0 |  | LESR | OTHER |  | 45 | 45 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RTEDDY_2_RWSBT4 | Rosamond West Solar Central BESS B | GEN | 0 |  | LESR | OTHER |  | 30 | 30 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RTEDDY_2_RWSBT5 | Rosamond West Solar Central BESS C | GEN | 0 |  | LESR | OTHER |  | 12 | 12 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RTEDDY_2_SC1SR3 | Rosamond West Solar Clean | GEN | 2020-12-21 | 2020 | SUN | PHOTO VOLTAIC |  | 40 | 40 | SCE | NQC | FC | 0.16 | 1.2 | 1.4 | 1.76 | 2.56 | 5.24 | 5.76 | 4.96 | 4.44 | 2.96 | 2.28 | 1.4
RTEDDY_2_SEBSR3 | Rosamond West Solar East Bay 3 | GEN | 2020-12-21 | 2020 | SUN | PHOTO VOLTAIC |  | 56 | 56 | SCE | NQC | FC | 0.22 | 1.68 | 1.96 | 2.46 | 3.58 | 7.34 | 8.06 | 6.94 | 6.22 | 4.14 | 3.19 | 1.96
RTEDDY_2_SEBSR4 | Rosamond West Solar East Bay 4 | GEN | 2020-12-21 | 2020 | SUN | PHOTO VOLTAIC |  | 56 | 56 | SCE | NQC | FC | 0.22 | 1.68 | 1.96 | 2.46 | 3.58 | 7.34 | 8.06 | 6.94 | 6.22 | 4.14 | 3.19 | 1.96
RTEDDY_2_SOLAR1 | Rosamond West Solar 1 | GEN | 2016-12-22 | 2016 | SUN | PHOTO VOLTAIC |  | 54 | 55 | SCE | NQC | FC | 0.22 | 1.62 | 1.89 | 2.38 | 3.46 | 7.07 | 7.78 | 6.7 | 5.99 | 4 | 3.08 | 1.89
RTEDDY_2_SOLAR2 | Rosamond West Solar 2 | GEN | 2016-12-22 | 2016 | SUN | PHOTO VOLTAIC |  | 54 | 55 | SCE | NQC | FC | 0.22 | 1.62 | 1.89 | 2.38 | 3.46 | 7.07 | 7.78 | 6.7 | 5.99 | 4 | 3.08 | 1.89
RTEDDY_2_SPASR4 | Rosamond West Solar Palo Alto | GEN | 2020-12-21 | 2020 | SUN | PHOTO VOLTAIC |  | 26 | 26 | SCE | NQC | FC | 10.61 | 14.53 | 16.9 | 21.67 | 23.08 | 22.52 | 22.23 | 20.53 | 18.62 | 16.04 | 10.94 | 8.13
RTEDDY_2_SRXSR4 | Rosamond West Solar Rosie X | GEN | 2020-12-21 | 2020 | SUN | PHOTO VOLTAIC |  | 13.6 | 13.6 | SCE | NQC | FC | 0.05 | 0.41 | 0.48 | 0.6 | 0.87 | 1.78 | 1.96 | 1.69 | 1.51 | 1.01 | 0.78 | 0.48
RTREE_2_WIND1 | Rising Tree 1 | GEN | 2015-01-12 | 2015 | WIND | WIND |  | 79.2 | 79.2 | SCE | NQC | FC | 13.99 | 14.88 | 13.08 | 12.53 | 13.32 | 12.21 | 11.35 | 8.62 | 8.91 | 8.26 | 11.14 | 13.49
RTREE_2_WIND2 | Rising Tree 2 | GEN | 2015-01-12 | 2015 | WIND | WIND |  | 19.8 | 19.8 | SCE | NQC | FC | 3.5 | 3.72 | 3.27 | 3.13 | 3.33 | 3.05 | 2.84 | 2.16 | 2.23 | 2.07 | 2.78 | 3.37
RTREE_2_WIND3 | Rising Tree 3 | GEN | 2015-06-25 | 2015 | WIND | WIND |  | 99 | 99 | SCE | NQC | FC | 17.49 | 18.61 | 16.35 | 15.66 | 16.65 | 15.27 | 14.18 | 10.78 | 11.13 | 10.33 | 13.92 | 16.86
RUSCTY_2_CTG1 | Russell City | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 180 | 180 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RUSCTY_2_CTG2 | Russell City | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 180 | 180 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RUSCTY_2_STG | Russell City | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 254 | 254 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RUSCTY_2_UNITS | Russell City Energy Center | GEN | 2013-08-08 | 2013 | NATURAL GAS | COMBINED CYCLE |  | 615.18 | 0 | PGAE | NQC | FC | 615.18 | 615.18 | 615.18 | 612.7 | 607.7 | 601 | 597.4 | 597.4 | 600.9 | 606.1 | 615.18 | 615.18
RUSSELL_2_SOLANO1 | Solano Renewables 1 | GEN | 2024-02-06 | 2024 | WIND | WIND |  | 229.98 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RUSSLL_2_SMUD | SOLANO WIND FARM | GEN | 0 |  | WIND | WIND |  | 102 | 102 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RUSSLL_2_SMUD2 | Solano Wind Project Phase 3 | GEN | 0 |  | WIND | WIND |  | 218.78 | 218.78 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RVRVEW_1_UNITA1 | Riverview Energy Center (GP Antioch) | GEN | 2003-05-02 | 2003 | NATURAL GAS | COMBUSTION TURBINE |  | 48.7 | 50 | PGAE | NQC | FC | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6
RVSIDE_2_RERCU3 | Riverside Energy Res. Ctr Unit 3 | GEN | 2011-04-01 | 2011 | NATURAL GAS | COMBUSTION TURBINE |  | 49 | 71 | SCE | NQC | FC | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
RVSIDE_2_RERCU4 | Riverside Energy Res. Ctr Unit 4 | GEN | 2011-04-01 | 2011 | NATURAL GAS | COMBUSTION TURBINE |  | 49 | 71.2 | SCE | NQC | FC | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
RVSIDE_6_RERCU1 | Riverside Energy Res. Ctr Unit 1 | GEN | 2006-06-01 | 2006 | NATURAL GAS | COMBUSTION TURBINE |  | 48.35 | 48.5 | SCE | NQC | FC | 48.35 | 48.35 | 48.35 | 48.35 | 48.35 | 48.35 | 48.35 | 48.35 | 48.35 | 48.35 | 48.35 | 48.35
RVSIDE_6_RERCU2 | Riverside Energy Res. Ctr Unit 2 | GEN | 2006-06-01 | 2006 | NATURAL GAS | COMBUSTION TURBINE |  | 48.5 | 48.5 | SCE | NQC | FC | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5
RVSIDE_6_SOLAR1 | Tequesquite Landfill Solar Project | GEN | 2015-09-09 | 2015 | SUN | PHOTO VOLTAIC |  | 7.5 | 7.5 | SCE | NQC | FC | 0.03 | 0.23 | 0.26 | 0.33 | 0.48 | 0.98 | 1.08 | 0.93 | 0.83 | 0.56 | 0.43 | 0.26
RVSIDE_6_SPRING | SPRINGS GENERATION PROJECT AGGREGATE | GEN | 2002-06-13 | 2002 | NATURAL GAS | FTUR |  | 36 | 0 | SCE | NQC | FC | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
RVSIDE_7_SPRGU1 | RVSIDE_7_SPRGU1 | GEN | 0 |  | 0 | 0 |  | 11 | 11 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RVSIDE_7_SPRGU2 | RVSIDE_7_SPRGU2 | GEN | 0 |  | 0 | 0 |  | 11 | 11 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RVSIDE_7_SPRGU3 | RVSIDE_7_SPRGU3 | GEN | 0 |  | 0 | 0 |  | 11 | 11 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RVSIDE_7_SPRGU4 | RVSIDE_7_SPRGU4 | GEN | 0 |  | 0 | 0 |  | 11 | 11 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S_RITA_6_SOLAR1 | Sun Harvest Solar | GEN | 2015-05-28 | 2015 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SALIRV_2_UNIT | Salinas River Cogeneration | GEN | 1991-10-11 | 1991 | NATURAL GAS | FTUR |  | 39 | 57 | PGAE | NQC | FC | 23.11 | 22 | 23.11 | 21.52 | 17.17 | 19.17 | 17.55 | 19.23 | 19.61 | 19.48 | 21.65 | 23.33
SALTSP_7_UNIT 1 | Salt Springs Unit 1 | GEN | 0 |  | WATER | HYDRO |  | 12 | 12 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SALTSP_7_UNIT 2 | Salt Springs Unit 2 | GEN | 0 |  | WATER | HYDRO |  | 34 | 34 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SALTSP_7_UNITS | SALT SPRINGS HYDRO AGGREGATE | GEN | 1931-01-01 | 1931 | WATER | HYDRO |  | 46 | 0 | PGAE | NQC | FC | 1.6 | 4.72 | 12.8 | 0.4 | 17.46 | 16.93 | 18.56 | 24.1 | 6.32 | 4.24 | 2.8 | 20.7
SAMPSN_6_KELCO1 | KELCO QUALIFYING FACILITY | GEN | 2014-03-05 | 2014 | OTHER | COMBUSTION TURBINE |  | 25 | 28 | SDGE | NQC | FC | 1.03 | 1.05 | 2.18 | 2.77 | 3.33 | 3.81 | 2.44 | 1.59 | 3.62 | 1.85 | 1.24 | 2.21
SANBRN_2_EESSB2 | Edsan 2 Edwards Sanborn E1B | GEN | 2023-11-09 | 2023 | HYBD | OTHER |  | 166 | 166 | SCE | NQC | ID | 85.25 | 87.36 | 87.88 | 88.98 | 91.01 | 97.37 | 98.43 | 96.29 | 94.63 | 90.95 | 88.96 | 86.62
SANBRN_2_ES1BT3 | EdSan 1 Edwards 1 | GEN | 2022-04-13 | 2022 | HYBD | OTHER |  | 50.43 | 51 | SCE | NQC | ID | 22.09 | 22.8 | 22.97 | 23.31 | 23.96 | 26.03 | 26.39 | 25.71 | 25.2 | 24.01 | 23.39 | 22.64
SANBRN_2_ES2SB3 | EdSan 2 Sanborn 3 | GEN | 2022-04-13 | 2022 | HYBD | OTHER |  | 42 | 42 | SCE | NQC | ID | 18.07 | 18.66 | 18.8 | 19.08 | 19.62 | 21.34 | 21.63 | 21.07 | 20.65 | 19.67 | 19.15 | 18.53
SANBRN_2_ESABT1 | EdSan 1A | GEN | 2021-11-19 | 2021 | LESR | OTHER |  | 100 | 100 | SCE | NQC | ID | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SANBRN_2_ESBBT1 | EdSan 1B | GEN | 2021-11-01 | 2021 | LESR | OTHER |  | 100 | 100 | SCE | NQC | ID | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SANBRN_2_SS2BT3 | Sanborn Solar 2 SBESS 3 | GEN | 2023-10-11 | 2023 | LESR | OTHER |  | 169 | 169 | SCE | NQC | ID | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
SANBRN_2_SS2BT4 | Sanborn Solar 2 SBESS 4 | GEN | 2023-11-16 | 2023 | LESR | OTHER |  | 47 | 47 | SCE | NQC | ID | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANBRN_2_SS2SB4 | Sanborn Solar 2 Edwards Sanborn S4 | GEN | 2023-07-11 | 2023 | HYBD | OTHER |  | 36 | 36 | SCE | NQC | ID | 18.09 | 18.75 | 18.91 | 19.21 | 19.81 | 21.73 | 22.06 | 21.44 | 20.98 | 19.89 | 19.32 | 18.64
SANDLT_2_STGA | SANDLT_2_STGA | GEN | 0 |  | SUN | STEAM |  | 137.5 | 137.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANDLT_2_STGB | SANDLT_2_STGB | GEN | 0 |  | SUN | STEAM |  | 137.5 | 137.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANDLT_2_SUNITS | Mojave Solar | GEN | 2014-12-04 | 2014 | SUN | STEAM |  | 275 | 0 | SCE | NQC | FC | 1.1 | 8.25 | 9.63 | 12.1 | 17.6 | 36.03 | 39.6 | 34.1 | 30.53 | 20.35 | 15.68 | 9.63
SANDRN_2_SS1SR1 | Sandrini Sol 1 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 100 | 100 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANITR_6_CTG1 | LACSD CARSON WATER POLLUTION CTG1 | GEN | 0 |  | BIOGAS | COMBUSTION TURBINE |  | 10 | 10 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANITR_6_CTG2 | LACSD CARSON WATER POLLUTION CTG2 | GEN | 0 |  | BIOGAS | COMBUSTION TURBINE |  | 10 | 10 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANITR_6_CTG3 | LACSD CARSON WATER POLLUTION CTG3 | GEN | 0 |  | BIOGAS | COMBUSTION TURBINE |  | 10 | 10 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANITR_6_STG4 | LACSD CARSON WATER POLLUTION STG4 | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 5.5 | 5.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANITR_6_UNITS | LACSD CARSON WATER POLLUTION AGGREGATE | GEN | 0 |  | NATURAL GAS | COMBINED CYCLE |  | 8 | 0 | SCE | NQC | FC | 1.05 | 1.1 | 0.2 | 0.18 | 0.66 | 0.65 | 0.84 | 1.11 | 1.09 | 0.78 | 0.66 | 0.52
SANLOB_1_LNDFIL | Cold Canyon | GEN | 2013-07-18 | 2013 | BIOGAS | RECIPROCATING ENGINE |  | 1.5 | 5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANLOB_1_OSFBM1 | Old Santa Fe Road | GEN | 2019-07-11 | 2019 | BIOGAS | RECIPROCATING ENGINE |  | 0.85 | 0 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANTFG_7_UNIT 1 | SANTFG_7_UNIT 1 | GEN | 0 |  | 0 | 0 |  | 46 | 46 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANTFG_7_UNIT 2 | SANTFG_7_UNIT 2 | GEN | 0 |  | 0 | 0 |  | 46 | 46 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SANTFG_7_UNITS | GEYSERS CALISTOGA AGGREGATE | GEN | 1984-03-14 | 1984 | GEOTHERMAL | STEAM |  | 72 | 0 | PGAE | NQC | FC | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
SANTGO_2_LNDFL1 | Bowerman Power | GEN | 2016-04-12 | 2016 | BIOGAS | RECIPROCATING ENGINE |  | 19.6 | 20 | SCE | NQC | FC | 18.54 | 18.97 | 17.9 | 18.82 | 18.12 | 19.53 | 18.66 | 18.64 | 18.5 | 17.79 | 18.48 | 19.6
SANTGO_2_MABBT1 | Millikan Avenue BESS | GEN | 2017-01-14 | 2017 | LESR | OTHER |  | 2 | 2 | SCE | NQC | FC | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
SANWD_1_QF | San Gorgonio Farms Wind Farm | GEN | 1983-03-01 | 1983 | WIND | WIND |  | 31 | 32 | SCE | NQC | FC | 5.48 | 5.83 | 5.12 | 4.9 | 5.22 | 4.78 | 4.44 | 3.37 | 3.49 | 3.23 | 4.36 | 5.28
SAUGUS_2_SPESBT1 | Santa Paula Energy Storage | GEN | 0 |  | LESR | OTHER |  | 30 | 30 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SAUGUS_6_CREST | East Portal Hydro | GEN | 2017-10-11 | 2017 | WATER | HYDRO |  | 1 | 1 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SAUGUS_6_MWDFTH | Foothill Hydroelectric Recovery Plant | GEN | 1981-01-01 | 1981 | WATER | HYDRO |  | 9.1 | 9.1 | SCE | NQC | FC | 2.4 | 2.4 | 1.6 | 3.2 | 4.8 | 4 | 4.8 | 4 | 4 | 4.8 | 4 | 2.4
SAUGUS_6_QF | SAUGUS QFS | GEN | 1987-01-01 | 1987 | OTHER | OTHER |  | 2.19 | 8.9 | SCE | NQC | FC | 0.07 | 0.2 | 0.14 | 0.4 | 0.23 | 0.19 | 0.27 | 0.59 | 1 | 1 | 1 | 0.97
SAUGUS_7_CHIQCN | Chiquita Canyon Landfill Fac | GEN | 2010-11-23 | 2010 | BIOGAS | COMBUSTION TURBINE |  | 8 | 9.2 | SCE | NQC | FC | 6.23 | 6 | 6.05 | 5.95 | 5.85 | 5.57 | 5.34 | 5.35 | 5.14 | 5.38 | 5.5 | 5.5
SBERDO_2_PSP3 | Mountainview Gen Sta. Unit 3 | GEN | 2005-12-10 | 2005 | NATURAL GAS | COMBINED CYCLE |  | 555 | 0 | SCE | NQC | FC | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555
SBERDO_2_PSP4 | Mountainview Gen Sta. Unit 4 | GEN | 2006-01-19 | 2006 | NATURAL GAS | COMBINED CYCLE |  | 555 | 0 | SCE | NQC | FC | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555
SBERDO_2_SNTANA | SANTA ANA PSP | GEN | 0 |  | WATER | HYDRO |  | 6.95 | 7 | SCE | NQC | FC | 0.46 | 0.53 | 0.52 | 0.34 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SBERDO_6_MILLCK | MILL CREEK PSP | GEN | 0 |  | WATER | HYDRO |  | 3.93 | 4 | SCE | NQC | FC | 1.33 | 1.4 | 1.46 | 1.61 | 1.04 | 0.95 | 0.87 | 0.57 | 0.62 | 0.54 | 0.78 | 0.89
SBERDO_7_CT3A | SBERDO_7_CT3A | GEN | 0 |  | 0 | 0 |  | 182 | 182 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SBERDO_7_CT3B | SBERDO_7_CT3B | GEN | 0 |  | 0 | 0 |  | 182 | 182 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SBERDO_7_CT4A | SBERDO_7_CT4A | GEN | 0 |  | 0 | 0 |  | 182 | 182 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SBERDO_7_CT4B | SBERDO_7_CT4B | GEN | 0 |  | 0 | 0 |  | 182 | 182 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SBERDO_7_STG3 | SBERDO_7_STG3 | GEN | 0 |  | 0 | 0 |  | 202 | 202 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SBERDO_7_STG4 | SBERDO_7_STG4 | GEN | 0 |  | 0 | 0 |  | 202 | 202 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCARLT_2_SSABT1 | Scarlet Solar CA 1A | GEN | 0 |  | LESR | OTHER |  | 10 | 10 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCARLT_2_SSASR1 | Scarlet Solar CA 1A PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 100 | 100 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCARLT_2_SSBBT1 | Scarlet Solar CA 1B | GEN | 0 |  | LESR | OTHER |  | 30 | 30 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCARLT_2_SSBSR1 | Scarlet Solar CA 1B PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 100 | 100 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_DERP01 | ESS CSG Aggregated Resources | GEN | 0 |  | OTHER | OTHER |  | 0.72 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP100 | SCEC_1_PDRP100 | GEN | 0 |  | OTHER | OTHER |  | 2 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP101 | SCEC_1_PDRP101 | GEN | 0 |  | OTHER | OTHER |  | 2 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP102 | SCEC_1_PDRP102 | GEN | 0 |  | OTHER | OTHER |  | 2 | 0 | SCE | NQC | FC | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP103 | SCEC_1_PDRP103 | GEN | 0 |  | OTHER | OTHER |  | 2 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP104 | SCEC_1_PDRP104 | GEN | 0 |  | OTHER | OTHER |  | 2.24 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP105 | SCEC_1_PDRP105 | GEN | 0 |  | OTHER | OTHER |  | 2.24 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP106 | SCEC_1_PDRP106 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP107 | SCEC_1_PDRP107 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP108 | SCEC_1_PDRP108 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP109 | SCEC_1_PDRP109 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 0.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP110 | SCEC_1_PDRP110 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 0.12 | 4.95 | 3.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP111 | SCEC_1_PDRP111 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP113 | SCEC_1_PDRP113 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.62 | 0.79 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP114 | SCEC_1_PDRP114 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP115 | SCEC_1_PDRP115 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.63 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP116 | SCEC_1_PDRP116 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC |  | 0.99 | 0.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP117 | SCEC_1_PDRP117 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP118 | SCEC_1_PDRP118 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.21 | 0.99 | 0.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP119 | SCEC_1_PDRP119 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP120 | SCEC_1_PDRP120 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP121 | SCEC_1_PDRP121 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP122 | SCEC_1_PDRP122 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP124 | LCR AMS Hybrid West LA 1-C-LCRLL | GEN | 0 |  | OTHER | OTHER |  | 2.13 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP125 | SCEC_1_PDRP125 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP126 | SCEC_1_PDRP126 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.84 | 0.99 | 0.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP127 | SCEC_1_PDRP127 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.44 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP128 | SCEC_1_PDRP128 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP129 | SCEC_1_PDRP129 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP130 | SCEC_1_PDRP130 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP131 | SCEC_1_PDRP131 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP132 | SCEC_1_PDRP132 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.8 | 0.99 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP133 | SCEC_1_PDRP133 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP134 | SCEC_1_PDRP134 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP135 | SCEC_1_PDRP135 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.39 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP136 | SCEC_1_PDRP136 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP137 | SCEC_1_PDRP137 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP138 | SCEC_1_PDRP138 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP139 | SCEC_1_PDRP139 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.65 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP140 | SCEC_1_PDRP140 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP141 | SCEC_1_PDRP141 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP142 | SCEC_1_PDRP142 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.59 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP143 | SCEC_1_PDRP143 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP144 | SCEC_1_PDRP144 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP145 | SCEC_1_PDRP145 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP146 | SCEC_1_PDRP146 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP147 | SCEC_1_PDRP147 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP148 | SCEC_1_PDRP148 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP149 | SCEC_1_PDRP149 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP150 | SCEC_1_PDRP150 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP151 | SCEC_1_PDRP151 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP152 | SCEC_1_PDRP152 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.35 | 0.99 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP153 | SCEC_1_PDRP153 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP154 | SCEC_1_PDRP154 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC |  | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP155 | SCEC_1_PDRP155 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP156 | SCEC_1_PDRP156 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.45 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP157 | SCEC_1_PDRP157 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.39 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP158 | SCEC_1_PDRP158 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP159 | SCEC_1_PDRP159 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP160 | SCEC_1_PDRP160 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 3.65 | 4.65 | 6.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP161 | SCEC_1_PDRP161 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP162 | SCEC_1_PDRP162 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP163 | SCEC_1_PDRP163 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP171 | IEUA Battery Energy Storage System | GEN | 0 |  | OTHER | OTHER |  | 1 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP173 | LCR AMS Hybrid West LA 2-C-LSCE | GEN | 0 |  | OTHER | OTHER |  | 2.46 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP175 | VLTS_PDR_SCEC_01 | GEN | 0 |  | OTHER | OTHER |  | 9.95 | 0 | SCE | NQC | FC | 0.11 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP176 | VLTS_PDR_SCEC_02 | GEN | 0 |  | OTHER | OTHER |  | 9.95 | 0 | SCE | NQC | FC | 1.68 | 1.68 | 1.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP178 | SCEC_1_PDRP178 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP179 | SCEC_1_PDRP179 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP181 | SCEC_1_PDRP181 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC |  |  | 0.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP185 | VLTS_PDR_SCEC_03 | GEN | 0 |  | OTHER | OTHER |  | 7.5 | 0 | SCE | NQC | FC | 0.11 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP187 | ESPN_SCEC_1_PDRP187 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 9.94 | 9.98 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP188 | ESPN_SCEC_1_PDRP188 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 9.94 | 9.98 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP189 | ESPN_SCEC_1_PDRP189 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 9.94 | 9.98 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP190 | ESPN SCEC_1_PDRP190 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP191 | ESPN_SCEC_1_PDRP191 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP192 | ESPN_SCEC_1_PDRP192 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 5.26 | 5.26 | 5.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEC_1_PDRP196 | SCEC | GEN | 0 |  | OTHER | OTHER |  | 9.9 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEN_6_PDRP101 | SCEN_6_PDRP101 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEN_6_PDRP103 | ESPN_SCEN_6_PDRP103 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 7.05 | 7.04 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEN_6_PDRP104 | ESPN_SCEN_6_PDRP104 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEN_6_PDRP105 | SCEN_6_PDRP105 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEN_6_PDRP106 | SCEN_6_PDRP106 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEN_6_PDRP111 | SCEN | GEN | 0 |  | OTHER | OTHER |  | 9.9 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP100 | SCEW_2_PDRP100 | GEN | 0 |  | OTHER | OTHER |  | 2 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP101 | SCEW_2_PDRP101 | GEN | 0 |  | OTHER | OTHER |  | 2 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP102 | SCEW_2_PDRP102 | GEN | 0 |  | OTHER | OTHER |  | 2 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP103 | SCEW_2_PDRP103 | GEN | 0 |  | OTHER | OTHER |  | 2 | 0 | SCE | NQC | FC | 0.48 | 0.48 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP104 | SCEW_2_PDRP104 | GEN | 0 |  | OTHER | OTHER |  | 2 | 0 | SCE | NQC | FC | 0.4 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP105 | SCEW_2_PDRP105 | GEN | 0 |  | OTHER | OTHER |  | 2 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP106 | SCEW_2_PDRP106 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP107 | SCEW_2_PDRP107 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.1 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP108 | SCEW_2_PDRP108 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.28 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP109 | SCEW_2_PDRP109 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP110 | SCEW_2_PDRP110 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.38 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP111 | SCEW_2_PDRP111 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP112 | SCEW_2_PDRP112 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC |  | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP114 | LCR AMS Hybrid West LA 1-W-SCE | GEN | 0 |  | OTHER | OTHER |  | 5.8 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP116 | SCEW_2_PDRP116 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.53 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP117 | SCEW_2_PDRP117 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC |  | 0.99 | 0.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP118 | SCEW_2_PDRP118 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.61 | 0.99 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP119 | SCEW_2_PDRP119 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP120 | SCEW_2_PDRP120 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.28 | 0.99 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP121 | SCEW_2_PDRP121 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.74 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP122 | SCEW_2_PDRP122 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC |  | 4.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP123 | SCEW_2_PDRP123 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP124 | SCEW_2_PDRP124 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP125 | SCEW_2_PDRP125 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.39 | 0.99 | 0.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP130 | SCEW_2_PDRP130 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC |  | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP131 | SCEW_2_PDRP131 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC |  | 0.99 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP133 | SCEW_2_PDRP133 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.23 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP141 | SCEW_2_PDRP141 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP159 | LCR AMS Hybrid West LA 1-W-LNEI1 | GEN | 0 |  | OTHER | OTHER |  | 8.14 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP160 | LCR AMS Hybrid West LA 2-W-LSCE | GEN | 0 |  | OTHER | OTHER |  | 5.26 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP163 | LCR AMS Hybrid West LA 2-W-LPIPO | GEN | 0 |  | OTHER | OTHER |  | 8.08 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP167 | LCR AMS Hybrid West LA 1-W-2-SCE | GEN | 0 |  | OTHER | OTHER |  | 10.36 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP168 | VLTS_PDR_SCEW_01 | GEN | 0 |  | OTHER | OTHER |  | 6.5 | 0 | SCE | NQC | FC | 0.42 | 0.42 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP171 | SCEW_2_PDRP171 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP172 | SCEW_2_PDRP172 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE | NQC | FC | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP173 | SCEW_2_PDRP173 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP174 | SCEW_2_PDRP174 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP175 | SCEW_2_PDRP175 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP177 | VLTS_PDR_SCEW_02 | GEN | 0 |  | OTHER | OTHER |  | 9.9 | 0 | SCE | NQC | FC | 0.84 | 0.84 | 0.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP180 | VLTS_PDR_SCEW_03 | GEN | 0 |  | OTHER | OTHER |  | 9.95 | 0 | SCE | NQC | FC | 0.11 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP182 | ESPN_SCEW_2_PDRP182 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE | NQC | FC | 8.01 | 7.99 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP183 | ESPN_SCEW_2_PDRP183 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP185 | ESPN_SCEW_2_PDRP185 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCEW_2_PDRP187 | SCEW | GEN | 0 |  | OTHER | OTHER |  | 9.9 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCHLTE_1_PL1X3 | Tracy Combined Cycle Power Plant | GEN | 2012-10-31 | 2012 | NATURAL GAS | COMBINED CYCLE |  | 336.04 | 0 | PGAE | NQC | FC | 336.04 | 336.04 | 336.04 | 336.04 | 336.04 | 336.04 | 336.04 | 336.04 | 336.04 | 336.04 | 336.04 | 336.04
SCHLTE_1_UNITA1 | Tracy Unit 1 Peaking Project | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 87 | 87 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCHLTE_1_UNITA2 | Tracy Unit 2 Peaking Project | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 87 | 87 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCHLTE_1_UNITA3 | Tracy Combined Cycle Plant | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 165 | 165 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCHNDR_1_FIVPTS | Five Points Solar Station | GEN | 2011-10-07 | 2011 | SUN | PHOTO VOLTAIC |  | 15 | 15 | PGAE | NQC | FC | 0.06 | 0.45 | 0.53 | 0.66 | 0.96 | 1.97 | 2.16 | 1.86 | 1.67 | 1.11 | 0.86 | 0.53
SCHNDR_1_WSTSDE | Westside Solar Station | GEN | 2011-09-13 | 2011 | SUN | PHOTO VOLTAIC |  | 15 | 15 | PGAE | NQC | FC | 0.06 | 0.45 | 0.53 | 0.66 | 0.96 | 1.97 | 2.16 | 1.86 | 1.67 | 1.11 | 0.86 | 0.53
SDG1_1_PDRP100 | SDG1_1_PDRP100 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC | 0.56 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP101 | SDG1_1_PDRP101 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC | 0.61 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP102 | SDG1_1_PDRP102 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC | 0.32 | 0.78 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP103 | SDG1_1_PDRP103 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC | 0.13 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP104 | SDG1_1_PDRP104 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SDGE | NQC | FC | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP105 | SDG1_1_PDRP105 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC | 0.34 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP106 | SDG1_1_PDRP106 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP111 | SDG1_1_PDRP111 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC | 0.26 | 0.99 | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP113 | SDG1_1_PDRP113 | GEN | 0 |  | OTHER | OTHER |  | 9.99 | 0 | SDGE | NQC | FC | 0.16 | 0.17 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP114 | SDG1_1_PDRP114 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC |  |  | 0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP117 | SDG1_1_PDRP117 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP118 | SDG1_1_PDRP118 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC | 0.1 | 0.24 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP119 | SDG1_1_PDRP119 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP120 | SDG1_1_PDRP120 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP121 | SDG1_1_PDRP121 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE | NQC | FC |  |  | 0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP122 | SDG1_1_PDRP122 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDG1_1_PDRP123 | SDG1_1_PDRP123 | GEN | 0 |  | OTHER | OTHER |  | 0.99 | 0 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEARLS_1_TS3SR1 | Trona Solar III | GEN | 2023-04-13 | 2023 | SUN | PHOTO VOLTAIC |  | 2 | 2 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEARLS_7_ARGUS | Argus Cogeneration | GEN | 2013-11-15 | 2013 | OTHER | 0 |  | 19 | 62.5 | SCE | NQC | FC | 4.75 | 5.75 | 4.49 | 4.47 | 3.15 | 2.06 | 1.14 | 1.48 | 3.39 | 4.18 | 3.73 | 4.61
SEAWND_2_AMWWD1 | Alta Mesa Wind | GEN | 0 |  | WIND | WIND |  | 27 | 27 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SEGS_1_SR2SL2 | Sunray 2 | GEN | 2017-06-02 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
SENTNL_2_CTG1 | Sentinel Unit 1 | GEN | 2013-05-06 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 107.68 | 131.8 | SCE | NQC | FC | 107.68 | 107.68 | 107.68 | 107.68 | 107.68 | 107.68 | 107.68 | 107.68 | 107.68 | 107.68 | 107.68 | 107.68
SENTNL_2_CTG2 | Sentinel Unit 2 | GEN | 2013-05-06 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 104.19 | 131.8 | SCE | NQC | FC | 103.98 | 103.98 | 103.98 | 103.98 | 103.98 | 103.98 | 103.98 | 103.98 | 103.98 | 103.98 | 103.98 | 103.98
SENTNL_2_CTG3 | Sentinel Unit 3 | GEN | 2013-05-06 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 105.69 | 131.8 | SCE | NQC | FC | 105.69 | 105.69 | 105.69 | 105.69 | 105.69 | 105.69 | 105.69 | 105.69 | 105.69 | 105.69 | 105.69 | 105.69
SENTNL_2_CTG4 | Sentinel Unit 4 | GEN | 2013-05-06 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 106.55 | 131.8 | SCE | NQC | FC | 106.55 | 106.55 | 106.55 | 106.55 | 106.55 | 106.55 | 106.55 | 106.55 | 106.55 | 106.55 | 106.55 | 106.55
SENTNL_2_CTG5 | Sentinel Unit 5 | GEN | 2013-05-06 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 107.52 | 131.8 | SCE | NQC | FC | 107.52 | 107.52 | 107.52 | 107.52 | 107.52 | 107.52 | 107.52 | 107.52 | 107.52 | 107.52 | 107.52 | 107.52
SENTNL_2_CTG6 | Sentinel Unit 6 | GEN | 2013-05-06 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 105 | 131.8 | SCE | NQC | FC | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
SENTNL_2_CTG7 | Sentinel Unit 7 | GEN | 2013-05-06 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 106.73 | 131.8 | SCE | NQC | FC | 106.73 | 106.73 | 106.73 | 106.73 | 106.73 | 106.73 | 106.73 | 106.73 | 106.73 | 106.73 | 106.73 | 106.73
SENTNL_2_CTG8 | Sentinel Unit 8 | GEN | 2013-05-06 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 106.85 | 131.8 | SCE | NQC | FC | 106.85 | 106.85 | 106.85 | 106.85 | 106.85 | 106.85 | 106.85 | 106.85 | 106.85 | 106.85 | 106.85 | 106.85
SGREGY_6_SANGER | Algonquin Power Sanger 2 | GEN | 2017-06-01 | 2017 | NATURAL GAS | COMBINED CYCLE |  | 48.3 | 48.3 | PGAE | NQC | FC | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08 | 48.08
SHANDN_2_SBBBM1 | San Bernardino Biogas | GEN | 2023-06-30 | 2023 | BIOMASS | RECIPROCATING ENGINE |  | 2.6 | 2.6 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHELRF_1_UNITS | SHELL OIL REFINERY AGGREGATE | GEN | 1995-01-01 | 1995 | NATURAL GAS | COMBINED CYCLE |  | 100 | 0 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.33 | 0 | 0
SHELRF_7_UNIT 1 | Shell Oil Refinery Unit 1 | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 20 | 20 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHELRF_7_UNIT 2 | Shell Oil Refinery Unit 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 40 | 40 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHELRF_7_UNIT 3 | Shell Oil Refinery Unit 3 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 40 | 40 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHUTLE_6_CREST | CREST Contracts | GEN | 2016-03-25 | 2016 | SUN | PHOTO VOLTAIC |  | 4 | 5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHUTLE_6_RUISR1 | Rutan 1 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHUTLE_6_RUISR2 | Rutan 2 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHUTLE_6_RUISR3 | Rutan 3 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1 | 1 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SIERRA_1_UNITS | HIGH SIERRA LIMITED | GEN | 1989-02-24 | 1989 | NATURAL GAS | COMBUSTION TURBINE |  | 52.43 | 60.3 | PGAE | NQC | FC | 52.43 | 52.43 | 52.43 | 52.43 | 52.43 | 52.43 | 52.43 | 52.43 | 52.43 | 52.43 | 52.43 | 52.43
SIGHEB_6_HE2SCEDYN | Heber 2 | TG | 2022-12-20 | 2022 | GEOTHERMAL | COMBUSTION TURBINE |  | 28 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SIGHEB_6_MIRDYN | Heber South | TG | 2021-12-29 | 2021 | GEOTHERMAL | COMBUSTION TURBINE |  | 17 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SISPRG_2_DS3BT1 | Daggett Solar 3 a BESS | GEN | 2023-11-15 | 2023 | LESR | OTHER |  | 61.16 | 61.5 | SCE | NQC | ID | 61.5 | 61.5 | 61.5 | 61.5 | 61.5 | 61.5 | 61.5 | 61.5 | 61.5 | 61.5 | 61.5 | 61.5
SISPRG_2_DS3BT2 | Daggett Solar 3 b BESS | GEN | 2023-08-24 | 2023 | LESR | OTHER |  | 59.43 | 60 | SCE | NQC | ID | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SISPRG_2_DS3BT3 | Daggett Solar 3 cd BESS | GEN | 2023-09-05 | 2023 | LESR | OTHER |  | 12.5 | 12.5 | SCE | NQC | ID | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
SISPRG_2_DS3BT4 | Daggett Solar 3 e BESS | GEN | 2023-08-24 | 2023 | LESR | OTHER |  | 15 | 15 | SCE | NQC | ID | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
SISPRG_2_DS3SR1 | Daggett Solar 3 a PV | GEN | 2023-10-24 | 2023 | SUN | PHOTO VOLTAIC |  | 123 | 123 | SCE | NQC | ID | 0.29 | 2.58 | 3.1 | 4.15 | 6.2 | 12.74 | 13.89 | 11.76 | 10.18 | 6.45 | 4.52 | 2.19
SISPRG_2_DS3SR2 | Daggett Solar 3 b PV | GEN | 2023-08-24 | 2023 | SUN | PHOTO VOLTAIC |  | 110 | 110 | SCE | NQC | ID | 0.25 | 2.22 | 2.67 | 3.61 | 5.41 | 11.12 | 12.11 | 10.23 | 8.82 | 5.55 | 3.84 | 1.78
SISPRG_2_DS3SR3 | Daggett Solar 3 cd PV | GEN | 2023-09-05 | 2023 | SUN | PHOTO VOLTAIC |  | 50 | 50 | SCE | NQC | ID | 0.16 | 1.27 | 1.5 | 1.94 | 2.86 | 5.86 | 6.42 | 5.49 | 4.84 | 3.16 | 2.34 | 1.32
SISPRG_2_DS3SR4 | Daggett Solar 3 e PV | GEN | 2023-07-14 | 2023 | SUN | PHOTO VOLTAIC |  | 17 | 17 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SISQUC_1_SMARIA | Santa Maria II LFG Power Plant | GEN | 2010-09-27 | 2010 | BIOGAS | RECIPROCATING ENGINE |  | 1.42 | 1.5 | PGAE | NQC | FC | 0.99 | 1.01 | 1 | 1.01 | 1.01 | 1.03 | 1.02 | 1.03 | 0.69 | 0.69 | 1.02 | 1.03
SKERN_6_SOLAR1 | South Kern Solar PV Plant | GEN | 2015-04-07 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
SKERN_6_SOLAR2 | SKIC Solar | GEN | 2017-01-05 | 2017 | SUN | PHOTO VOLTAIC |  | 10 | 10 | PGAE | NQC | FC | 0.04 | 0.3 | 0.35 | 0.44 | 0.64 | 1.31 | 1.44 | 1.24 | 1.11 | 0.74 | 0.57 | 0.35
SLATE_2_SLASR1 | Slate | GEN | 2021-11-12 | 2021 | SUN | PHOTO VOLTAIC |  | 50.5 | 50.5 | PGAE | NQC | ID | 21.36 | 29.58 | 31.34 | 38.94 | 42 | 44.85 | 44.35 | 40.29 | 38.51 | 27.35 | 20.11 | 12.54
SLATE_2_SLASR2 | SLATE_2 | GEN | 2022-03-15 | 2022 | HYBD | OTHER |  | 93 | 93 | PGAE | NQC | ID | 46.72 | 48.45 | 48.84 | 49.64 | 51.19 | 56.13 | 57 | 55.39 | 54.2 | 51.38 | 49.91 | 48.15
SLATE_2_SLASR3 | SLATE_3 | GEN | 2022-03-15 | 2022 | HYBD | OTHER |  | 67.5 | 67.5 | PGAE | NQC | ID | 33.91 | 35.17 | 35.45 | 36.03 | 37.15 | 40.74 | 41.37 | 40.2 | 39.34 | 37.29 | 36.23 | 34.95
SLATE_2_SLASR4 | SLATE_4 | GEN | 2022-03-15 | 2022 | HYBD | OTHER |  | 63 | 63 | PGAE | NQC | ID | 50.09 | 50.99 | 51.22 | 51.75 | 52.67 | 55.51 | 55.96 | 54.97 | 54.17 | 52.5 | 51.56 | 50.48
SLATE_2_SLASR5 | Slate 5 | GEN | 2022-03-15 | 2022 | HYBD | OTHER |  | 26 | 26 | PGAE | NQC | ID | 10.07 | 10.6 | 10.71 | 10.94 | 11.39 | 12.86 | 13.12 | 12.66 | 12.32 | 11.49 | 11.08 | 10.57
SLRMS3_2_SRMSR1 | SILVER RIDGE MOUNT SIGNAL 3 | GEN | 2019-12-06 | 2019 | SUN | PHOTO VOLTAIC |  | 250 | 250 | SDGE | NQC | FC | 1 | 7.5 | 8.75 | 11 | 16 | 32.75 | 36 | 31 | 27.75 | 18.5 | 14.25 | 8.75
SLST13_2_SOLAR1 | Quinto Solar PV Project | GEN | 2015-11-30 | 2015 | SUN | PHOTO VOLTAIC |  | 107.6 | 107.6 | PGAE | NQC | FC | 0.43 | 3.23 | 3.77 | 4.73 | 6.89 | 14.1 | 15.49 | 13.34 | 11.94 | 7.96 | 6.13 | 3.77
SLSTR1_2_SOLAR1 | Solar Star 1 | GEN | 2014-10-22 | 2014 | SUN | PHOTO VOLTAIC |  | 310 | 0 | SCE | NQC | FC | 1.24 | 9.3 | 10.85 | 13.64 | 19.84 | 40.61 | 44.64 | 38.44 | 34.41 | 22.94 | 17.67 | 10.85
SLSTR1_2_SOLR1A | Solar Star 1 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 151.5 | 151.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLSTR1_2_SOLR1B | Solar Star 1 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 166.5 | 166.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLSTR2_2_SOLAR2 | Solar Star 2 | GEN | 2014-07-31 | 2014 | SUN | PHOTO VOLTAIC |  | 276 | 0 | SCE | NQC | FC | 1.1 | 8.28 | 9.66 | 12.14 | 17.66 | 36.16 | 39.74 | 34.22 | 30.64 | 20.42 | 15.73 | 9.66
SLSTR2_2_SOLR2A | Solar Star 2 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 219 | 219 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLSTR2_2_SOLR2B | Solar Star 2 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 57 | 57 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLUISP_2_UNIT 1 | San Luis P-G Unit 1 | GEN | 0 |  | WATER | PUMPED STORAGE |  | 53 | 53 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLUISP_2_UNIT 2 | San Luis P-G Unit 2 | GEN | 0 |  | WATER | PUMPED STORAGE |  | 53 | 53 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLUISP_2_UNIT 3 | San Luis P-G Unit 3 | GEN | 0 |  | WATER | PUMPED STORAGE |  | 53 | 53 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLUISP_2_UNIT 4 | San Luis P-G Unit 4 | GEN | 0 |  | WATER | PUMPED STORAGE |  | 53 | 53 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLUISP_2_UNIT 5 | San Luis P-G Unit 5 | GEN | 0 |  | WATER | PUMPED STORAGE |  | 53 | 53 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLUISP_2_UNIT 6 | San Luis P-G Unit 6 | GEN | 0 |  | WATER | PUMPED STORAGE |  | 53 | 53 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLUISP_2_UNIT 7 | San Luis P-G Unit 7 | GEN | 0 |  | WATER | PUMPED STORAGE |  | 53 | 53 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLUISP_2_UNIT 8 | San Luis P-G Unit 8 | GEN | 0 |  | WATER | PUMPED STORAGE |  | 53 | 53 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SLUISP_2_UNITS | SAN LUIS (GIANELLI) PUMP-GEN (AGGREGATE) | GEN | 1967-01-01 | 1967 | WATER | PUMPED STORAGE |  | 374.43 | 0 | PGAE | NQC | FC | 0 | 46.13 | 42.68 | 99.91 | 83.47 | 66.46 | 0 | 0 | 0 | 0 | 0 | 0
SLYCRK_1_UNIT 1 | SLY CREEK HYDRO | GEN | 1983-01-01 | 1983 | WATER | HYDRO |  | 13 | 13 | PGAE | NQC | FC | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SMPRIP_1_SMPSON | Ripon Cogeneration Unit 1 | GEN | 1988-04-19 | 1988 | NATURAL GAS | COMBUSTION TURBINE |  | 46.05 | 56.9 | PGAE | NQC | FC | 46.05 | 46.05 | 46.05 | 46.05 | 46.05 | 46.05 | 46.05 | 46.05 | 46.05 | 46.05 | 46.05 | 46.05
SMRCOS_6_LNDFIL | San Marcos Energy | GEN | 2011-05-20 | 2011 | BIOGAS | RECIPROCATING ENGINE |  | 1.5 | 2 | SDGE | NQC | FC | 1.5 | 1.5 | 1.5 | 1.5 | 1.49 | 1.48 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
SMUDGO_7_UNIT 1 | SONOMA POWER PLANT | GEN | 1983-01-01 | 1983 | GEOTHERMAL | STEAM |  | 64.8 | 78 | PGAE | NQC | FC | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SMYRNA_1_DL1SR1 | Delano Land 1 | GEN | 2017-12-28 | 2017 | SUN | PHOTO VOLTAIC |  | 1 | 1 | PGAE | NQC | FC | 0 | 0.03 | 0.04 | 0.04 | 0.06 | 0.13 | 0.14 | 0.12 | 0.11 | 0.07 | 0.06 | 0.04
SNCLRA_2_HOWLNG | Houwelings Nurseries Oxnard, Inc | GEN | 2013-06-14 | 2013 | NATURAL GAS | RECIPROCATING ENGINE |  | 12.71 | 13.2 | SCE | NQC | FC | 6.1 | 6.85 | 6.43 | 5.62 | 4.44 | 6.64 | 5.02 | 5.03 | 5.48 | 2.97 | 3.65 | 2.82
SNCLRA_2_SILBT1 | Silverstrand BESS | GEN | 2021-04-01 | 2021 | LESR | OTHER |  | 11 | 11 | SCE | NQC | FC | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
SNCLRA_2_SPRHYD | Springville Hydroelectric Generator | GEN | 2016-04-19 | 2016 | WATER | HYDRO |  | 1 | 1 | SCE | NQC | FC | 0.05 | 0.03 | 0.11 | 0.06 | 0.06 | 0.13 | 0.15 | 0.16 | 0.1 | 0.04 | 0.03 | 0.03
SNCLRA_2_UNIT | Channel Islands Power | GEN | 2018-04-26 | 2018 | NATURAL GAS | COMBINED CYCLE | Yes | 27.5 | 28 | SCE | NQC | FC | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5
SNCLRA_2_UNIT1 | New Indy Oxnard | GEN | 2016-04-15 | 2016 | NATURAL GAS | FTUR |  | 27.8 | 29 | SCE | NQC | FC | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8
SNCLRA_2_VESBT1 | Ventura Energy Storage | GEN | 2021-04-20 | 2021 | LESR | OTHER |  | 100 | 100 | SCE | NQC | FC | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SNCLRA_6_OXGEN | OXGEN | GEN | 2020-06-01 | 2020 | NATURAL GAS | COMBUSTION TURBINE |  | 47.7 | 47.7 | SCE | NQC | FC | 47.7 | 47.7 | 47.7 | 47.7 | 47.7 | 47.7 | 47.7 | 47.7 | 47.7 | 47.7 | 47.7 | 47.7
SNCLRA_6_PROCGN | Procter and Gamble Oxnard 2 | GEN | 1998-11-17 | 1998 | NATURAL GAS | FTUR |  | 47.9 | 49.5 | SCE | NQC | FC | 28.35 | 22.46 | 28.38 | 28.33 | 28.21 | 28.06 | 27.46 | 19.41 | 19.22 | 19.2 | 19.24 | 19.44
SNCLRA_6_QF | SANTA CLARA QFS | GEN | 1987-01-01 | 1987 | OTHER | OTHER |  | 1.65 | 15 | SCE | NQC | FC | 0.22 | 0.22 | 0.18 | 0.24 | 0.23 | 0.25 | 0.24 | 0.31 | 0.3 | 0.26 | 0.34 | 0.46
SNDBAR_7_UNIT 1 | SANDBAR | GEN | 2017-01-01 | 2017 | WATER | HYDRO |  | 16.2 | 18.6 | PGAE | NQC | FC | 8.92 | 4.25 | 0.68 | 6.47 | 6.64 | 6.6 | 5.42 | 3.57 | 3.19 | 0.7 | 5.81 | 12.69
SNMALF_6_UNITS | Sonoma County Landfill | GEN | 1993-04-30 | 1993 | BIOGAS | RECIPROCATING ENGINE |  | 5 | 8 | PGAE | NQC | FC | 3.07 | 2.54 | 3.24 | 3.21 | 2.87 | 2.61 | 3.15 | 3.05 | 3.02 | 3.02 | 3.13 | 2.87
SNORA_2_SNRSLR | SG Sorrento | TG | 2015-08-29 | 2015 | SUN | PHOTO VOLTAIC |  | 50 | 0 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOLBLU_2_WSBBT1 | Westlands Solar Blue BESS | GEN | 0 |  | LESR | OTHER |  | 112.5 | 112.5 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOLBLU_2_WSBBT2 | Westlands Solar Blue BESS | GEN | 0 |  | LESR | OTHER |  | 112.5 | 112.5 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOLBLU_2_WSBBX2 | Westlands Solar Blue BESS | GEN | 2023-12-13 | 2023 | LESR | OTHER |  | 225 | 0 | PGAE | NQC | ID | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225
SOLBLU_2_WSBSR1 | Westlands Solar Blue | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 125 | 125 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOLBLU_2_WSBSR2 | Westlands Solar Blue | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 125 | 125 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOLBLU_2_WSBSX2 | Westlands Solar Blue | GEN | 2023-12-13 | 2023 | SUN | PHOTO VOLTAIC |  | 250 | 0 | PGAE | NQC | ID | 0.27 | 3.44 | 4.34 | 6.39 | 9.87 | 20.4 | 22 | 18.21 | 15.05 | 8.79 | 5.12 | 1
SOUTH_2_UNIT | SOUTH HYDRO | GEN | 1979-01-01 | 1979 | WATER | HYDRO |  | 7.1 | 7.1 | PGAE | NQC | FC | 2.73 | 3.12 | 2.46 | 1.15 | 2.32 | 1.45 | 1.26 | 1.07 | 1.04 | 1.11 | 1.36 | 1.35
SPAULD_6_UNIT 1 | SPAULDING HYDRO PH 1 UNIT | GEN | 0 |  | WATER | HYDRO |  | 7 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPAULD_6_UNIT 2 | SPAULDING HYDRO PH 2 UNIT | GEN | 0 |  | WATER | HYDRO |  | 4.4 | 4.4 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPAULD_6_UNIT 3 | SPAULDING HYDRO PH 3 UNIT | GEN | 1928-01-01 | 1928 | WATER | HYDRO |  | 6.5 | 6.5 | PGAE | NQC | FC | 0.8 | 0.79 | 0.79 | 1.09 | 3.42 | 0.73 | 1.68 | 3.53 | 2.96 | 1.93 | 0.62 | 0.82
SPAULD_6_UNIT12 | SPAULDING HYDRO PH 1 & 2 AGGREGATE | GEN | 1929-01-01 | 1929 | WATER | HYDRO |  | 11.4 | 0 | PGAE | NQC | FC | 2.98 | 1.65 | 1.8 | 1.92 | 4.44 | 4.4 | 3.41 | 3.62 | 1.2 | 1.2 | 1.6 | 2.58
SPBURN_2_UNIT 1 | Burney Biomass | GEN | 1986-01-01 | 1986 | BIOMASS | STEAM |  | 22 | 22 | PGAE | NQC | FC | 9.91 | 10.64 | 10.78 | 10.62 | 10.63 | 12.14 | 12.75 | 12.66 | 12.76 | 11.94 | 10.89 | 9.33
SPBURN_7_SNOWMT | Burney Creek Hydro | GEN | 1990-03-28 | 1990 | WATER | HYDRO |  | 3 | 3 | PGAE | NQC | FC | 0.2 | 0.02 | 0.19 | 0.92 | 0.44 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.06
SPI LI_2_UNIT 1 | Lincoln Biomass | GEN | 1986-06-03 | 1986 | BIOMASS | STEAM |  | 17.2 | 19.2 | PGAE | NQC | FC | 7.56 | 6.64 | 6.38 | 6.26 | 8.39 | 9.34 | 9.43 | 9.55 | 9.43 | 8.52 | 6.71 | 7.03
SPIAND_1_ANDSN2 | SPI Anderson 2 | GEN | 2015-09-09 | 2015 | BIOMASS | STEAM |  | 27.15 | 30.1 | PGAE | NQC | FC | 12.23 | 13.3 | 14.75 | 14.47 | 16.25 | 17.9 | 17.77 | 18.42 | 18.34 | 15.65 | 14.85 | 14.87
SPICER_1_UNIT 1 | SPICER HYDRO UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 2.8 | 2.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPICER_1_UNIT 2 | SPICER HYDRO UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 2.8 | 2.8 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPICER_1_UNIT 3 | SPICER HYDRO UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 0.5 | 0.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPICER_1_UNITS | SPICER HYDRO UNITS 1-3 AGGREGATE | GEN | 1990-01-01 | 1990 | WATER | HYDRO |  | 6 | 0 | PGAE | NQC | FC | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
SPIFBD_1_PL1X2 | SIERRA PACIFIC IND. (SONORA) | GEN | 2018-04-12 | 2018 | BIOMASS | STEAM |  | 7.5 | 7.5 | PGAE | NQC | FC | 2.62 | 2.61 | 2.72 | 2.58 | 3.03 | 3.29 | 3.55 | 3.78 | 3.72 | 3.12 | 2.78 | 2.54
SPQUIN_6_SRPCQU | Quincy Biomass | GEN | 2018-05-17 | 2018 | BIOMASS | STEAM |  | 24 | 24 | PGAE | NQC | FC | 18.25 | 16.86 | 16.76 | 14.42 | 19.08 | 21.09 | 19.62 | 14.76 | 13.92 | 10.5 | 9.59 | 15.22
SPRGAP_1_UNIT 1 | SPRING GAP HYDRO | GEN | 1921-01-01 | 1921 | WATER | HYDRO |  | 7 | 7 | PGAE | NQC | FC | 2.19 | 1.89 | 3.03 | 4.89 | 4.9 | 1.63 | 0 | 0 | 3.1 | 3.9 | 2.53 | 3.22
SPRGVL_2_CREST | Springerville Aggregate Solar Resources | GEN | 2017-01-05 | 2017 | SUN | PHOTO VOLTAIC |  | 3 | 18.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPRGVL_2_EXETPV | Exeter Tulare PV | GEN | 2022-01-28 | 2022 | SUN | PHOTO VOLTAIC |  | 3.5 | 3.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPRGVL_2_LINDPV | Lindsay Tulare PV | GEN | 2022-01-28 | 2022 | SUN | PHOTO VOLTAIC |  | 4 | 4 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPRGVL_2_PORTPV | Porterville Tulare PV | GEN | 2022-02-03 | 2022 | SUN | PHOTO VOLTAIC |  | 3.5 | 3.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPRGVL_2_TULESC | TULE RIVER HYDRO PLANT (SCE) | GEN | 1909-01-01 | 1909 | WATER | HYDRO |  | 2.5 | 2.5 | SCE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SRINTL_6_UNIT | SRI INTERNATIONAL | GEN | 1987-03-10 | 1987 | NATURAL GAS | COMBUSTION TURBINE |  | 6.9 | 6.9 | PGAE | NQC | FC | 1.32 | 1.24 | 1.36 | 1.39 | 1.32 | 1.09 | 1 | 0.96 | 0.9 | 0.98 | 1.23 | 1.27
STANIS_7_UNIT 1 | STANISLAUS HYDRO | GEN | 1963-01-01 | 1963 | WATER | HYDRO |  | 91 | 95 | PGAE | NQC | FC | 66.66 | 56.75 | 54.07 | 40 | 28 | 59 | 61.99 | 70.02 | 56.65 | 20.88 | 0 | 65.85
STANTN_2_SBEBT3 | Stanton Battery Energy Storage | GEN | 0 |  | LESR | OTHER |  | 34.4 | 34.4 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STANTN_2_SBEBT4 | Stanton Battery Energy Storage | GEN | 0 |  | LESR | OTHER |  | 34.4 | 34.4 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STANTN_2_SBEBX2 | Stanton Battery Energy Storage | GEN | 2023-07-19 | 2023 | LESR | OTHER |  | 68.8 | 0 | SCE | NQC | FC | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8
STANTN_2_STAGT1 | Stanton 1 | GEN | 2020-05-20 | 2020 | NATURAL GAS | OTHER |  | 49.65 | 50 | SCE | NQC | FC | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65
STANTN_2_STAGT2 | Stanton 2 | GEN | 2020-05-20 | 2020 | NATURAL GAS | OTHER |  | 49.65 | 50 | SCE | NQC | FC | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65 | 49.65
STIGCT_2_LODI | LODI STIG UNIT | GEN | 1996-01-01 | 1996 | NATURAL GAS | COMBUSTION TURBINE |  | 49.9 | 51.2 | PGAE | NQC | FC | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
STNRES_1_UNIT | Covanta Stanislaus | GEN | 1988-09-06 | 1988 | WASTE TO POWER | STEAM |  | 19.9 | 22.3 | PGAE | NQC | FC | 15.91 | 19.31 | 19.02 | 15.14 | 13.88 | 17.58 | 19.43 | 19.79 | 19.32 | 18.87 | 19.39 | 18.17
STOILS_1_UNIT 1 | STOILS_1_UNIT 1 | GEN | 0 |  | 0 | 0 |  | 62.5 | 62.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STOILS_1_UNIT 2 | STOILS_1_UNIT 2 | GEN | 0 |  | 0 | 0 |  | 62.5 | 62.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STOILS_1_UNITS | Chevron Richmond Refinery | GEN | 1992-08-31 | 1992 | NATURAL GAS | COMBINED CYCLE |  | 56.2 | 0 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 5.33 | 9.44 | 0 | 11.34 | 16.56 | 0
STOREY_2_MDRCH2 | Madera Chowchilla 2 | GEN | 2016-08-01 | 2016 | WATER | HYDRO |  | 0.56 | 0.6 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0.04 | 0.19 | 0.32 | 0.04 | 0 | 0 | 0 | 0
STOREY_2_MDRCH3 | Madera Chowchilla 3 | GEN | 2016-08-01 | 2016 | WATER | HYDRO |  | 0.42 | 0.5 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0.01 | 0.11 | 0.22 | 0.02 | 0 | 0 | 0 | 0
STOREY_2_MDRCH4 | Madera Chowchilla 4 | GEN | 2016-07-19 | 2016 | WATER | HYDRO |  | 0.92 | 1 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0.01 | 0.1 | 0.31 | 0.01 | 0 | 0 | 0 | 0
STOREY_7_MDRCHW | Madera Canal Site 980 | GEN | 1985-02-02 | 1985 | WATER | HYDRO |  | 1.84 | 3.8 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0.45 | 0.82 | 0.06 | 0 | 0 | 0 | 0
STRAUS_1_STRWD1 | Strauss Wind, LLC | GEN | 2023-12-20 | 2023 | WIND | WIND |  | 95.25 | 99 | PGAE | NQC | FC | 28.9 | 33.56 | 29.93 | 31.62 | 32.71 | 24.13 | 21.46 | 20.16 | 20.69 | 17.34 | 21.91 | 28
STROUD_6_SOLAR | Stroud Solar Station | GEN | 2011-10-04 | 2011 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
STROUD_6_WWHSR1 | Winter Wheat Solar Farm | GEN | 2019-05-11 | 2019 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUMWHT_6_SWSSR1 | Summer Wheat Solar Farm | GEN | 2018-10-11 | 2018 | SUN | PHOTO VOLTAIC |  | 18.5 | 18.5 | PGAE | NQC | FC | 0.07 | 0.56 | 0.65 | 0.81 | 1.18 | 2.42 | 2.66 | 2.29 | 2.05 | 1.37 | 1.05 | 0.65
SUNCAT_2_A1ABT1 | Arlington Solar Unit 1A BESS | GEN | 2022-08-01 | 2022 | LESR | OTHER |  | 47 | 47 | SCE | NQC | ID | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SUNCAT_2_A1BBT1 | Arlington Solar Unit 1B BESS | GEN | 2022-08-01 | 2022 | LESR | OTHER |  | 63 | 63 | SCE | NQC | ID | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
SUNCAT_2_A2ABT2 | Arlington Solar Unit 2A BESS | GEN | 2022-08-16 | 2022 | LESR | OTHER |  | 132 | 132 | SCE | NQC | ID | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
SUNCAT_2_A2BSR2 | Arlington Solar Unit 2B | GEN | 2023-10-20 | 2023 | SUN | PHOTO VOLTAIC |  | 133 | 133 | SCE | NQC | ID | 0.28 | 2.16 | 2.52 | 3.17 | 4.61 | 9.44 | 10.37 | 8.93 | 8 | 5.33 | 4.11 | 1.96
SUNRIS_2_PL1X3 | Sunrise Power Project AGGREGATE II | GEN | 2001-06-07 | 2001 | NATURAL GAS | COMBINED CYCLE |  | 586.02 | 0 | PGAE | NQC | FC | 586.02 | 586.02 | 586.02 | 586.02 | 586.02 | 586.02 | 586.02 | 586.02 | 586.02 | 586.02 | 586.02 | 586.02
SUNRIS_2_UNIT 1 | Sunrise Power Project Unit 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 164 | 164 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUNRIS_2_UNIT 2 | Sunrise Power Project Unit 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 164 | 164 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUNRIS_2_UNIT 3 | Sunrise Power Project Unit 3 | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 272 | 272 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUNSET_2_UNITS | MIDWAY SUNSET COGENERATION PLANT | GEN | 1989-12-18 | 1989 | NATURAL GAS | FTUR |  | 248 | 291 | PGAE | NQC | FC | 248 | 248 | 248 | 245 | 240 | 234 | 229 | 229 | 231 | 243 | 246 | 248
SUNSHN_2_LNDFL | Sunshine Gas Producers | GEN | 2014-09-01 | 2014 | BIOGAS | COMBUSTION TURBINE |  | 20 | 0 | SCE | NQC | FC | 17.49 | 16.89 | 17.35 | 16.58 | 17.14 | 16.97 | 16.4 | 15.75 | 15.88 | 15.59 | 16.8 | 15.43
SUNSHN_2_LNDFL1 | SUNSHN_2_LNDFL1 | GEN | 0 |  | BIOGAS | COMBUSTION TURBINE |  | 4.6 | 4.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUNSHN_2_LNDFL2 | SUNSHN_2_LNDFL2 | GEN | 0 |  | BIOGAS | COMBUSTION TURBINE |  | 4.6 | 4.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUNSHN_2_LNDFL3 | SUNSHN_2_LNDFL3 | GEN | 0 |  | BIOGAS | COMBUSTION TURBINE |  | 4.6 | 4.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUNSHN_2_LNDFL4 | SUNSHN_2_LNDFL4 | GEN | 0 |  | BIOGAS | COMBUSTION TURBINE |  | 4.6 | 4.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUNSHN_2_LNDFL5 | SUNSHN_2_LNDFL5 | GEN | 0 |  | BIOGAS | COMBUSTION TURBINE |  | 4.6 | 4.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUNSLR_1_SSVSR1 | Sunshine Valley Solar 1 | GEN | 2019-12-18 | 2019 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE | NQC | FC | 0.4 | 3 | 3.5 | 4.4 | 6.4 | 13.1 | 14.4 | 12.4 | 11.1 | 7.4 | 5.7 | 3.5
SUNSPT_2_WNASR1 | Windhub Solar A | GEN | 2019-12-18 | 2019 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
SUNST2_5_SS2SR1 | Sun Streams Solar 2 | GEN | 2021-06-25 | 2021 | SUN | PHOTO VOLTAIC |  | 150 | 150 | SDGE | NQC | FC | 0.6 | 4.5 | 5.25 | 6.6 | 9.6 | 19.65 | 21.6 | 18.6 | 16.65 | 11.1 | 8.55 | 5.25
SUNSTR_5_SS1SCEDYN | Sunstream Solar 1 | TG | 2019-11-19 | 2019 | SUN | PHOTO VOLTAIC |  | 150 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUTTER_2_CISO | Sutter Power Plant Pseudo-CISO | TG | 2020-07-10 | 2020 | NATURAL GAS | COMBINED CYCLE |  | 275 | 280 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SYCAMR_2_UNIT 1 | Sycamore Cogeneration Unit 1 | GEN | 1987-01-01 | 1987 | NATURAL GAS | FTUR |  | 74 | 90 | SCE | NQC | FC | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
SYCAMR_2_UNIT 2 | Sycamore Cogeneration Unit 2 | GEN | 1987-01-01 | 1987 | NATURAL GAS | FTUR |  | 76 | 90 | SCE | NQC | FC | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
SYCAMR_2_UNIT 3 | Sycamore Cogeneration Unit 3 | GEN | 1987-01-01 | 1987 | NATURAL GAS | FTUR |  | 74 | 90 | SCE | NQC | FC | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
SYCAMR_2_UNIT 4 | Sycamore Cogeneration Unit 4 | GEN | 1987-01-01 | 1987 | NATURAL GAS | FTUR |  | 76 | 90 | SCE | NQC | FC | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
TANHIL_6_SOLART | Berry Cogen 18 | GEN | 1986-01-01 | 1986 | NATURAL GAS | FTUR |  | 17 | 17 | PGAE | NQC | FC | 12.04 | 12.08 | 11.77 | 12.17 | 12.38 | 11.78 | 11.36 | 11.05 | 11.1 | 12.04 | 11.36 | 11.07
TBLMTN_6_QF | SMALL QF AGGREGATION - PARADISE | GEN | 1983-01-01 | 1983 | WATER | HYDRO |  | 1.7 | 5.8 | PGAE | NQC | FC | 0.19 | 0.24 | 0.22 | 0.21 | 0.22 | 0.18 | 0.2 | 0.19 | 0.19 | 0.16 | 0.16 | 0.18
TECOLOTE_3_WBDYN | TECOLOTE WIND | TG | 2021-12-01 | 2021 | WIND | WIND |  | 271.68 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEHAPI_2_PW1WD1 | Point Wind 1 | GEN | 2021-03-30 | 2021 | WIND | WIND |  | 47.49 | 47.5 | SCE | NQC | FC | 8.39 | 8.92 | 7.84 | 7.51 | 7.99 | 7.32 | 6.8 | 5.17 | 5.34 | 4.95 | 6.68 | 8.09
TEHAPI_2_PW2WD2 | Point Wind 2 | GEN | 2021-04-20 | 2021 | WIND | WIND |  | 14.4 | 14.4 | SCE | NQC | FC | 2.54 | 2.71 | 2.38 | 2.28 | 2.42 | 2.22 | 2.06 | 1.57 | 1.62 | 1.5 | 2.02 | 2.45
TEHAPI_2_WIND1 | Wind Wall Monolith 1 | GEN | 2021-03-30 | 2021 | WIND | WIND |  | 19.85 | 19.85 | SCE | NQC | FC | 3.51 | 3.73 | 3.28 | 3.14 | 3.34 | 3.06 | 2.84 | 2.16 | 2.23 | 2.07 | 2.79 | 3.38
TEHAPI_2_WIND2 | Wind Wall Monolith 2 | GEN | 2021-03-30 | 2021 | WIND | WIND |  | 23.66 | 22.5 | SCE | NQC | FC | 4.18 | 4.45 | 3.91 | 3.74 | 3.98 | 3.65 | 3.39 | 2.58 | 2.66 | 2.47 | 3.33 | 4.03
TENGEN_2_PL1X2 | Placerita Canyon Cogen | GEN | 1990-03-06 | 1990 | NATURAL GAS | COMBUSTION TURBINE |  | 37.7 | 0 | SCE | NQC | FC | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7
TENGEN_6_UNIT 1 | Berry Petroleum Placerita, Unit 1 | GEN | 0 |  | OTHER | COMBUSTION TURBINE |  | 22.7 | 22.7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TENGEN_6_UNIT 2 | Berry Petroleum Placerita, Unit 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 22.7 | 22.7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TERMEX_2_GTG1 | TERMEX_2_GTG1 | GEN | 0 |  | 0 | 0 |  | 180 | 180 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TERMEX_2_GTG2 | TERMEX_2_GTG2 | GEN | 0 |  | 0 | 0 |  | 180 | 180 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TERMEX_2_PL1X3 | TDM | GEN | 2003-07-30 | 2003 | NATURAL GAS | COMBINED CYCLE |  | 625 | 0 | SDGE | NQC | FC | 605 | 605 | 605 | 605 | 601 | 593 | 591 | 593 | 596 | 605 | 605 | 605
TERMEX_2_STG | Termoelectrica De Mexicali STG 3 | GEN | 0 |  | HEAT RECOVERY | STEAM |  | 308 | 308 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TESLA_1_QF | SMALL QF AGGREGATION - STOCKTON | GEN | 1982-01-01 | 1982 | OTHER | OTHER |  | 2 | 5 | PGAE | NQC | FC | 0.09 | 0.07 | 0.1 | 0.13 | 0.17 | 0.32 | 0.23 | 0.2 | 0.17 | 0.07 | 0.04 | 0.07
THERMA_2_UNIT 1 | Thermalito Gen Unit 1 | GEN | 0 |  | WATER | HYDRO |  | 36 | 36 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
THERMA_2_UNIT 2 | Thermalito P-G Unit 2 | GEN | 0 |  | WATER | HYDRO |  | 28 | 28 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
THERMA_2_UNIT 3 | Thermalito P-G Unit 3 | GEN | 0 |  | WATER | HYDRO |  | 28 | 28 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
THERMA_2_UNIT 4 | Thermalito P-G Unit 4 | GEN | 0 |  | WATER | HYDRO |  | 28 | 28 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIDWTR_2_UNITS | MARTINEZ COGEN LIMITED PARTNERSHIP | GEN | 1987-02-23 | 1987 | NATURAL GAS | FTUR |  | 114.8 | 114.8 | PGAE | NQC | FC | 33.06 | 37.66 | 30.76 | 37.11 | 52.09 | 49.61 | 52.59 | 81.9 | 88.36 | 88.04 | 43.35 | 40.43
TIFFNY_1_DILLON | TIFFNY_1_DILLON | GEN | 2008-04-18 | 2008 | WIND | WIND |  | 45 | 45 | SCE | NQC | FC | 7.95 | 8.46 | 7.43 | 7.12 | 7.57 | 6.94 | 6.45 | 4.9 | 5.06 | 4.69 | 6.33 | 7.66
TIGRCK_7_UNIT 1 | Tiger Creek Unit 1 | GEN | 0 |  | WATER | HYDRO |  | 31 | 31 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIGRCK_7_UNIT 2 | Tiger Creek Unit 2 | GEN | 0 |  | WATER | HYDRO |  | 31 | 31 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIGRCK_7_UNITS | TIGER CREEK HYDRO AGGREGATE | GEN | 1931-01-01 | 1931 | WATER | HYDRO |  | 62 | 0 | PGAE | NQC | FC | 26 | 16.8 | 14.17 | 0 | 16.66 | 36.8 | 33.91 | 40.4 | 36.08 | 30.37 | 30.43 | 28.38
TITANS_2_TTSSR1 | Titan Solar 1 Pseudo | TG | 2020-12-17 | 2020 | SUN | PHOTO VOLTAIC |  | 70 | 70 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TKOPWR_6_HYDRO | Bear Creek Hydroelectric Project | GEN | 2016-04-27 | 2016 | WATER | HYDRO |  | 2.83 | 3.2 | PGAE | NQC | FC | 0.35 | 0.27 | 0 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.12
TMPLTN_2_SOLAR | Vintner Solar | GEN | 2014-03-05 | 2014 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | FC | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
TOADTW_6_UNIT | TOAD TOWN | GEN | 1986-01-01 | 1986 | WATER | HYDRO |  | 1.5 | 1.5 | PGAE | NQC | FC | 0.38 | 0.59 | 0.37 | 0.26 | 0.39 | 0.28 | 0.2 | 0.18 | 0.03 | 0.03 | 0.11 | 0.06
TOPAZ_2_SOLAR | Topaz Solar Farms | GEN | 2014-10-27 | 2014 | SUN | PHOTO VOLTAIC |  | 550 | 550 | PGAE | NQC | FC | 2.2 | 16.5 | 19.25 | 24.2 | 35.2 | 72.05 | 79.2 | 68.2 | 61.05 | 40.7 | 31.35 | 19.25
TORTLA_1_SOLAR | Longboat Solar | GEN | 2016-12-16 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
TOWNSITE_2_MEADDYN | Townsite Solar BESS | TG | 2021-12-17 | 2021 | HYBD | OTHER |  | 180 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRNQL8_2_AMASR1 | Tranquillity 8 Amarillo | GEN | 2017-12-26 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | ID | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
TRNQL8_2_AZUSR1 | Tranquillity 8 Azul | GEN | 2017-12-26 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | ID | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
TRNQL8_2_ROJSR1 | Tranquillity 8 Rojo | GEN | 2018-04-14 | 2018 | SUN | PHOTO VOLTAIC |  | 100 | 100 | PGAE | NQC | ID | 0.4 | 3 | 3.5 | 4.4 | 6.4 | 13.1 | 14.4 | 12.4 | 11.1 | 7.4 | 5.7 | 3.5
TRNQL8_2_VERSR1 | Tranquillity 8 Verde | GEN | 2018-04-17 | 2018 | SUN | PHOTO VOLTAIC |  | 60 | 60 | PGAE | NQC | ID | 0.24 | 1.8 | 2.1 | 2.64 | 3.84 | 7.86 | 8.64 | 7.44 | 6.66 | 4.44 | 3.42 | 2.1
TRNQLT_2_RETBT1 | RE Tranquillity BESS | GEN | 2022-03-16 | 2022 | LESR | OTHER |  | 72 | 0 | PGAE | NQC | FC | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
TRNQLT_2_SOLAR | Tranquillity | GEN | 2016-07-28 | 2016 | SUN | PHOTO VOLTAIC |  | 200 | 200 | PGAE | NQC | FC | 0.45 | 4.38 | 5.05 | 6.75 | 10.11 | 21.9 | 24.39 | 20.42 | 17.51 | 9.86 | 7.04 | 2.91
TRNSWD_1_QF | FPL Energy C Wind | GEN | 2014-12-22 | 2014 | WIND | WIND |  | 38.97 | 40 | SCE | NQC | FC | 6.89 | 7.32 | 6.44 | 6.17 | 6.56 | 6.01 | 5.58 | 4.24 | 4.38 | 4.07 | 5.48 | 6.64
TULARE_2_TFCBM1 | LB Trigen Fuel Cell 1 | GEN | 2023-10-27 | 2023 | BIOGAS | OTHER |  | 2.8 | 2.8 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TULARE_2_TULBM1 | Tulare BioMAT Fuel Cell | GEN | 2019-12-20 | 2019 | BIOGAS | OTHER |  | 2.8 | 2.8 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TULEWD_1_TULWD1 | Tule Wind | GEN | 2018-01-05 | 2018 | WIND | WIND |  | 130.5 | 131.1 | SDGE | NQC | FC | 23.06 | 24.53 | 21.55 | 20.65 | 21.95 | 20.12 | 18.7 | 14.21 | 14.68 | 13.61 | 18.35 | 22.22
TULLCK_7_UNIT 1 | TULLOCH Unit 1 | GEN | 0 |  | 0 | 0 |  | 9.9 | 9.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TULLCK_7_UNIT 2 | TULLOCH Unit 2 | GEN | 0 |  | 0 | 0 |  | 9.9 | 9.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TULLCK_7_UNIT 3 | TULLOCH HYDRO AGGREGATE | GEN | 0 |  | WATER | 0 |  | 7.2 | 7.2 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TULLCK_7_UNITS | Tullock Hydro | GEN | 1958-01-01 | 1958 | WATER | 0 |  | 25.9 | 0 | PGAE | NQC | FC | 3.87 | 7.97 | 12.42 | 16.58 | 20.51 | 23.23 | 20.55 | 18.15 | 12.68 | 8.82 | 1.58 | 2.47
TUPMAN_1_BIOGAS | ABEC Bidart-Stockale #1 | GEN | 2013-03-20 | 2013 | BIOGAS | RECIPROCATING ENGINE |  | 0.6 | 0.6 | PGAE | NQC | FC | 0.32 | 0.32 | 0.32 | 0.33 | 0.33 | 0.35 | 0.34 | 0.33 | 0.35 | 0.32 | 0.3 | 0.3
TVYVLY_6_KRSHY1 | Kings River Syphon | GEN | 2021-09-15 | 2021 | WATER | HYDRO |  | 1.3 | 1.3 | PGAE | NQC | FC | 0.25 | 0.36 | 0 | 0 | 0 | 0.2 | 0.25 | 0.32 | 0.25 | 0.19 | 0 | 0.32
TWISSL_6_SOLAR | Nickel 1 ("NLH1") | GEN | 2012-11-27 | 2012 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | FC | 0.01 | 0.05 | 0.05 | 0.07 | 0.1 | 0.2 | 0.22 | 0.19 | 0.17 | 0.11 | 0.09 | 0.05
TWISSL_6_SOLAR1 | Coronal Lost Hills | GEN | 2015-05-15 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
TX-ELK_6_ECKSR2 | Eagle Creek | GEN | 2019-12-21 | 2019 | SUN | PHOTO VOLTAIC |  | 3 | 3 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TX-ELK_6_SOLAR1 | Castor | GEN | 2016-04-02 | 2016 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TXMCKT_6_UNIT | McKittrick Cogen | GEN | 1994-10-01 | 1994 | NATURAL GAS | FTUR |  | 11.2 | 11.2 | PGAE | NQC | FC | 4.14 | 3.98 | 3.48 | 4.26 | 3.99 | 4.06 | 3.85 | 3.93 | 3.96 | 3.82 | 3.83 | 4.1
UKIAH_7_LAKEMN | UKIAH LAKE MENDOCINO HYDRO | GEN | 2007-07-02 | 2007 | WATER | HYDRO |  | 3.5 | 3.5 | PGAE | NQC | FC | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7
ULTPCH_1_UCSBT1 | Ultrapower Chinese Station BESS | GEN | 0 |  | LESR | OTHER |  | 10 | 10 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ULTPCH_1_UNIT 1 | Pacific Ultrapower Chinese Station | GEN | 2017-03-01 | 2017 | BIOMASS | STEAM |  | 18 | 25.3 | PGAE | NQC | FC | 17.99 | 17.36 | 15.48 | 15.96 | 17.81 | 11.8 | 17.37 | 17.81 | 17 | 16.51 | 14.92 | 17.62
ULTPFR_1_UNIT 1 | Rio Bravo Fresno | GEN | 2017-09-07 | 2017 | BIOMASS | STEAM |  | 24.3 | 30.5 | PGAE | NQC | FC | 22.81 | 23.17 | 23.93 | 18.63 | 23.2 | 22.81 | 22.94 | 16.1 | 14.8 | 14.6 | 18.88 | 21.77
ULTRCK_2_UNIT | Rio Bravo Rocklin | GEN | 2017-09-07 | 2017 | BIOMASS | STEAM |  | 24.4 | 28.8 | PGAE | NQC | FC | 15.73 | 20.84 | 23.09 | 21.71 | 21.8 | 23.36 | 21.68 | 23.38 | 19.51 | 22.69 | 23.36 | 22.6
UNOCAL_1_UNITS | TOSCO (RODEO PLANT) | GEN | 1987-05-21 | 1987 | NATURAL GAS | FTUR |  | 49.85 | 57.3 | PGAE | NQC | FC | 4.22 | 5.24 | 4.86 | 3.83 | 2.59 | 4.47 | 2.87 | 2.19 | 2.63 | 4.34 | 2.75 | 3.17
UNVRSY_1_UNIT 1 | Berry Cogen 38 - Unit 1 | GEN | 1986-01-01 | 1986 | NATURAL GAS | FTUR |  | 38 | 38 | PGAE | NQC | FC | 35.76 | 31.33 | 35.27 | 30.82 | 34.6 | 33.48 | 33.01 | 32.07 | 31.52 | 28.94 | 34.85 | 34.73
USWND2_1_WIND1 | Golden Hills A | GEN | 2015-12-18 | 2015 | WIND | WIND |  | 42.96 | 43 | PGAE | NQC | FC | 14.11 | 15.14 | 13.5 | 14.26 | 14.75 | 10.88 | 9.68 | 9.09 | 9.33 | 7.82 | 9.88 | 12.63
USWND2_1_WIND2 | Golden Hills B | GEN | 2015-12-23 | 2015 | WIND | WIND |  | 42.96 | 43 | PGAE | NQC | FC | 14.11 | 15.14 | 13.5 | 14.26 | 14.75 | 10.88 | 9.68 | 9.09 | 9.33 | 7.82 | 9.88 | 12.63
USWND2_1_WIND3 | Golden Hills C | GEN | 2017-11-09 | 2017 | WIND | WIND |  | 46 | 46 | PGAE | NQC | FC | 15.1 | 16.21 | 14.45 | 15.27 | 15.8 | 11.65 | 10.36 | 9.73 | 9.99 | 8.38 | 10.58 | 13.52
USWND4_2_UNIT2 | Altamont Landfill Gas to Energy | GEN | 2018-02-01 | 2018 | BIOGAS | COMBUSTION TURBINE |  | 7.4 | 7.4 | PGAE | NQC | FC | 7.4 | 7.4 | 7.35 | 6.41 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.23 | 7.4 | 7.4
USWNDR_2_LABWD1 | LaBrisa Wind Project | GEN | 2019-06-28 | 2019 | WIND | WIND |  | 9 | 9 | PGAE | NQC | FC | 2.96 | 3.17 | 2.83 | 2.99 | 3.09 | 2.28 | 2.03 | 1.9 | 1.96 | 1.64 | 2.07 | 2.65
USWNDR_2_SMUD | SOLANO WIND FARM | GEN | 1994-01-01 | 1994 | WIND | WIND |  | 102.18 | 102.2 | PGAE | NQC | FC | 33.55 | 36 | 32.11 | 33.92 | 35.09 | 25.89 | 23.02 | 21.62 | 22.2 | 18.6 | 23.5 | 30.04
USWNDR_2_SMUD2 | Solano Wind Project Phase 3 | GEN | 2012-04-18 | 2012 | WIND | WIND |  | 127.8 | 128 | PGAE | NQC | FC | 41.97 | 45.03 | 40.16 | 42.42 | 43.89 | 32.38 | 28.79 | 27.04 | 27.77 | 23.27 | 29.4 | 37.57
USWPFK_6_FRICK | Frick Summit Wind Repower | GEN | 2021-07-02 | 2021 | WIND | WIND |  | 10 | 10 | PGAE | NQC | FC | 3.28 | 3.52 | 3.14 | 3.32 | 3.43 | 2.53 | 2.25 | 2.12 | 2.17 | 1.82 | 2.3 | 2.94
USWPJR_2_UNITS | Vasco Wind | GEN | 1988-01-01 | 1988 | WIND | WIND |  | 78.2 | 78.2 | PGAE | NQC | FC | 25.68 | 27.55 | 24.57 | 25.96 | 26.86 | 19.81 | 17.62 | 16.55 | 16.99 | 14.24 | 17.99 | 22.99
VACADX_1_SOLAR | Vaca-Dixon Solar Station | GEN | 2013-09-06 | 2013 | SUN | PHOTO VOLTAIC |  | 2.5 | 2.5 | PGAE | NQC | FC | 0.01 | 0.08 | 0.09 | 0.11 | 0.16 | 0.33 | 0.36 | 0.31 | 0.28 | 0.19 | 0.14 | 0.09
VACADX_1_UNITA1 | CalPeak Power Vaca Dixon Unit 1 | GEN | 2002-06-21 | 2002 | NATURAL GAS | COMBUSTION TURBINE |  | 51.91 | 57 | PGAE | NQC | PD | 50.61 | 50.61 | 50.61 | 50.61 | 50.61 | 50.61 | 50.61 | 50.61 | 50.61 | 50.61 | 50.61 | 50.61
VALLEY_5_ORTBT1 | Ortega Grid | GEN | 0 |  | LESR | OTHER |  | 20 | 20 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VALLEY_5_PERRIS | MWD Perris Hydroelectric Recovery Plant | GEN | 1983-01-01 | 1983 | WATER | HYDRO |  | 7.94 | 7.9 | SCE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 2.4 | 0 | 0 | 0 | 0
VALLEY_5_REDMTN | MWD Red Mountain Hydroelectric Recovery | GEN | 1985-01-01 | 1985 | WATER | HYDRO |  | 5.9 | 5.9 | SCE | NQC | FC | 1.49 | 1.39 | 0.46 | 1.37 | 1.35 | 1.26 | 0.8 | 1.21 | 1.59 | 1.6 | 1.31 | 1.01
VALLEY_5_SOLAR1 | Kona Solar - Meridian #1 | GEN | 2015-04-13 | 2015 | SUN | PHOTO VOLTAIC |  | 1.49 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VALLEY_5_SOLAR2 | AP North Lake Solar | GEN | 2015-08-11 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
VALTNE_2_AVASR1 | Valentine Solar | GEN | 2019-11-09 | 2019 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE | NQC | FC | 0.4 | 3 | 3.5 | 4.4 | 6.4 | 13.1 | 14.4 | 12.4 | 11.1 | 7.4 | 5.7 | 3.5
VALTNE_2_TBBBT1 | Tropico Solar Big Beau | GEN | 2022-12-27 | 2022 | HYBD | OTHER |  | 58 | 58 | SCE | NQC | ID | 18.17 | 19.41 | 19.68 | 20.18 | 21.22 | 24.61 | 25.23 | 24.17 | 23.42 | 21.52 | 20.58 | 19.41
VALTNE_2_TRSBT1 | Tropico Solar | GEN | 2022-12-27 | 2022 | HYBD | OTHER |  | 70 | 70 | SCE | NQC | ID | 22.21 | 23.7 | 24.02 | 24.63 | 25.88 | 29.96 | 30.71 | 29.43 | 28.53 | 26.23 | 25.1 | 23.69
VEAVST_1_SOLAR | Community Solar | GEN | 2017-02-10 | 2017 | SUN | PHOTO VOLTAIC |  | 14.4 | 15 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VEDDER_1_SEKERN | TEXACO EXPLORATION & PROD (SE KERN RIVER | GEN | 1989-01-31 | 1989 | NATURAL GAS | FTUR |  | 34.47 | 39.7 | PGAE | NQC | FC | 1.82 | 2.98 | 3.11 | 2.66 | 2.62 | 2.06 | 2.69 | 3.04 | 2.58 | 4.17 | 3.04 | 2.47
VEGA_6_SOLAR1 | Vega Solar | GEN | 2015-03-23 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VENWD_1_WIND3 | Painted Hills | GEN | 2021-04-14 | 2021 | WIND | WIND |  | 44.53 | 44.6 | SCE | NQC | FC | 7.87 | 8.37 | 7.35 | 7.04 | 7.49 | 6.87 | 6.38 | 4.85 | 5.01 | 4.65 | 6.26 | 7.58
VERNON_6_GONZL1 | H. Gonzales Unit #1 | GEN | 2013-06-13 | 2013 | NATURAL GAS | FTUR |  | 5.75 | 5.5 | SCE | NQC | FC | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75
VERNON_6_GONZL2 | H. Gonzales Unit #2 | GEN | 2013-06-13 | 2013 | NATURAL GAS | FTUR |  | 5.75 | 5.5 | SCE | NQC | FC | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75 | 5.75
VERNON_6_MALBRG | Malburg Generating Station | GEN | 2005-10-17 | 2005 | NATURAL GAS | COMBINED CYCLE |  | 139 | 0 | SCE | NQC | FC | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139
VERNON_7_CTG1 | VERNON_7_CTG1 | GEN | 0 |  | 0 | 0 |  | 43.57 | 43.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VERNON_7_CTG2 | VERNON_7_CTG2 | GEN | 0 |  | 0 | 0 |  | 43.57 | 43.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VERNON_7_STG3 | VERNON_7_STG3 | GEN | 0 |  | 0 | 0 |  | 51.87 | 51.9 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VESTAL_2_BTNBT1 | Bottleneck Energy Storage | GEN | 0 |  | LESR | OTHER |  | 80 | 80 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VESTAL_2_KERN | KERN RIVER PH 3 UNITS 1 & 2 AGGREGATE | GEN | 1907-01-01 | 1907 | WATER | HYDRO |  | 36.8 | 0 | SCE | NQC | FC | 9.05 | 10.04 | 8.61 | 20.79 | 26.24 | 14.06 | 2.25 | 0.3 | 0.26 | 0.28 | 3.88 | 7.04
VESTAL_2_RTS042 | SPVP042 Porterville Solar | GEN | 2012-11-24 | 2012 | SUN | PHOTO VOLTAIC |  | 5 | 5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VESTAL_2_SOLAR1 | NICOLIS | GEN | 2016-09-15 | 2016 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
VESTAL_2_SOLAR2 | TROPICO | GEN | 2016-09-14 | 2016 | SUN | PHOTO VOLTAIC |  | 14 | 14 | SCE | NQC | FC | 0.06 | 0.42 | 0.49 | 0.62 | 0.9 | 1.83 | 2.02 | 1.74 | 1.55 | 1.04 | 0.8 | 0.49
VESTAL_2_TS5SR1 | Tulare Solar 5 | GEN | 2022-04-29 | 2022 | SUN | PHOTO VOLTAIC |  | 55.83 | 55.9 | SCE | NQC | FC | 0.22 | 1.67 | 1.95 | 2.46 | 3.57 | 7.31 | 8.04 | 6.92 | 6.2 | 4.13 | 3.18 | 1.95
VESTAL_2_UNIT1 | CALGREN-PIXLEY | GEN | 2016-06-30 | 2016 | NATURAL GAS | FTUR |  | 5 | 11.2 | SCE | NQC | FC | 2.38 | 2.46 | 2.16 | 1.86 | 1.89 | 2 | 2.06 | 2.69 | 3 | 3.17 | 3.27 | 3.29
VESTAL_2_WELLHD | Wellhead Power Delano | GEN | 2013-01-16 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 49 | 49.5 | SCE | NQC | FC | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
VESTAL_6_KERNU1 | KERN RIVER PH 3 UNITS 1 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 20.5 | 20.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VESTAL_6_KERNU2 | KERN RIVER PH 3 UNITS 2 | GEN | 0 |  | NATURAL GAS | COMBUSTION TURBINE |  | 19.7 | 19.7 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VESTAL_6_QF | Isabella Hydro Dam 1 | GEN | 2021-02-05 | 2021 | WATER | HYDRO |  | 11.95 | 12 | SCE | NQC | FC | 3.81 | 2.01 | 1.96 | 2.92 | 2.51 | 3.82 | 3.24 | 2.49 | 2.27 | 1.7 | 1.82 | 1.75
VICPAS_2_SLOBT1 | Sloth BESS | GEN | 0 |  | LESR | OTHER |  | 15 | 15 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICPAS_2_SLOSR1 | Sloth | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 49.5 | 49.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICPAS_2_SOCBT1 | Sol Catcher BESS 1 | GEN | 0 |  | LESR | OTHER |  | 50 | 50 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICPAS_2_SOCBT2 | Sol Catcher BESS 2 | GEN | 0 |  | LESR | OTHER |  | 71 | 71 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICPAS_2_SOCSR1 | Sol Catcher BESS PV1 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 100 | 100 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICPAS_2_SOCSR2 | Sol Catcher BESS PV2 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 93.5 | 93.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICPAS_2_SOCSR3 | Sol Catcher BESS PV3 | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICPAS_2_VPSBT1 | Victory Pass Solar BESS | GEN | 0 |  | LESR | OTHER |  | 50 | 50 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICPAS_2_VPSSR1 | Victory Pass Solar | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 200 | 200 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_CREST | Victor Aggregate Solar Resources | GEN | 2017-09-13 | 2017 | SUN | PHOTO VOLTAIC |  | 24.5 | 38.2 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_EXSLRA | Expressway Solar A | GEN | 2014-05-07 | 2014 | SUN | PHOTO VOLTAIC |  | 2 | 2 | SCE | NQC | FC | 0.01 | 0.06 | 0.07 | 0.09 | 0.13 | 0.26 | 0.29 | 0.25 | 0.22 | 0.15 | 0.11 | 0.07
VICTOR_1_EXSLRB | Expressway Solar B | GEN | 2014-05-07 | 2014 | SUN | PHOTO VOLTAIC |  | 2 | 2 | SCE | NQC | FC | 0.01 | 0.06 | 0.07 | 0.09 | 0.13 | 0.26 | 0.29 | 0.25 | 0.22 | 0.15 | 0.11 | 0.07
VICTOR_1_LMASR1 | Madelyn | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1 | 1 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_LMISR2 | Landpro Mitchell | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_LRUSR3 | Landpro Rudy | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_LVSLR1 | Lone Valley Solar Park 1 | GEN | 2014-11-19 | 2014 | SUN | PHOTO VOLTAIC |  | 10 | 10 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_LVSLR2 | Lone Valley Solar Park 2 | GEN | 2014-11-22 | 2014 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_NUNSR4 | Nunn | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 1 | 1 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_SLRHES | Sunedison - Hesperia | GEN | 2014-08-08 | 2014 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_SOLAR1 | Victor Phelan Solar One | GEN | 2013-11-18 | 2013 | SUN | PHOTO VOLTAIC |  | 17.5 | 17.5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_SOLAR2 | Alamo Solar | GEN | 2015-05-15 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_SOLAR3 | Adelanto Solar 2 | GEN | 2015-07-01 | 2015 | SUN | PHOTO VOLTAIC |  | 7 | 7 | SCE | NQC | FC | 0.03 | 0.21 | 0.25 | 0.31 | 0.45 | 0.92 | 1.01 | 0.87 | 0.78 | 0.52 | 0.4 | 0.25
VICTOR_1_SOLAR4 | Adelanto Solar | GEN | 2015-09-03 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VICTOR_1_VDRYFA | Victor Dry Farm Ranch A | GEN | 2015-06-12 | 2015 | SUN | PHOTO VOLTAIC |  | 5 | 5 | SCE | NQC | FC | 0.02 | 0.15 | 0.18 | 0.22 | 0.32 | 0.66 | 0.72 | 0.62 | 0.56 | 0.37 | 0.29 | 0.18
VICTOR_1_VDRYFB | Victor Dry Farm Ranch B | GEN | 2015-06-12 | 2015 | SUN | PHOTO VOLTAIC |  | 5 | 5 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VIKING_2_VSHSB1 | Vikings Solar BESS Hybrid Project | TG | 0 |  | HYBD | OTHER |  | 150 | 150 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VILLPK_2_VALLYV | MWD Valley View Hydroelectric Recovery P | GEN | 1985-01-01 | 1985 | WATER | HYDRO |  | 4.1 | 4.1 | SCE | NQC | FC | 0 | 0 | 0 | 1.44 | 1.2 | 1.2 | 1.2 | 1.2 | 0 | 0.8 | 1.2 | 0
VILLPK_6_MWDYOR | Yorba Linda Hydroelectric Recovery Plant | GEN | 1981-01-01 | 1981 | WATER | HYDRO |  | 5.1 | 5.1 | SCE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 2.4 | 3.2 | 2.4 | 2.4 | 0
VISTA_6_QF | VISTA QFS | GEN | 1983-01-01 | 1983 | OTHER | OTHER |  | 0.18 | 0.6 | SCE | NQC | FC | 0.01 | 0.01 | 0.01 | 0.01 | 0.04 | 0.06 | 0.08 | 0.1 | 0.07 | 0.05 | 0.03 | 0.02
VISTRA_5_DALBT1 | Dallas Energy Storage | GEN | 2021-03-23 | 2021 | LESR | OTHER |  | 100 | 100 | PGAE | NQC | FC | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
VISTRA_5_DALBT2 | Dallas Energy Storage 2 | GEN | 2021-03-23 | 2021 | LESR | OTHER |  | 100 | 100 | PGAE | NQC | FC | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
VISTRA_5_DALBT3 | Dallas Energy Storage 3 | GEN | 2021-04-06 | 2021 | LESR | OTHER |  | 100 | 100 | PGAE | NQC | FC | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
VISTRA_5_DALBT4 | Dallas Energy Storage 4 | GEN | 2021-07-28 | 2021 | LESR | OTHER |  | 100 | 100 | PGAE | NQC | FC | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
VISTRA_5_PLABT1 | Plano Storage 1 | GEN | 2023-05-13 | 2023 | LESR | OTHER |  | 100.4 | 100.4 | PGAE | NQC | FC | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
VISTRA_5_PLABT2 | Plano Storage 2 | GEN | 2023-06-01 | 2023 | LESR | OTHER |  | 100.4 | 100.4 | PGAE | NQC | FC | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
VISTRA_5_PLABT3 | Plano Storage 3 | GEN | 2023-05-16 | 2023 | LESR | OTHER |  | 74.6 | 74.6 | PGAE | NQC | FC | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6
VISTRA_5_PLABT4 | Plano Storage 4 | GEN | 2023-06-02 | 2023 | LESR | OTHER |  | 74.6 | 74.6 | PGAE | NQC | FC | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6 | 74.6
VLCNTR_6_VCEBT1 | Valley Center Energy Storage | GEN | 2021-11-29 | 2021 | LESR | OTHER |  | 54 | 54 | SDGE | NQC | PD | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
VLCNTR_6_VCEBT2 | Valley Center Energy Storage B | GEN | 2021-12-16 | 2021 | LESR | OTHER |  | 85 | 85 | SDGE | NQC | PD | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
VLCNTR_6_VCSLR | Cole Grade | GEN | 2016-12-07 | 2016 | SUN | PHOTO VOLTAIC |  | 2.33 | 2.4 | SDGE | NQC | FC | 0.01 | 0.07 | 0.08 | 0.1 | 0.15 | 0.31 | 0.34 | 0.29 | 0.26 | 0.17 | 0.13 | 0.08
VLCNTR_6_VCSLR1 | Valley Center 1 | GEN | 2013-12-31 | 2013 | SUN | PHOTO VOLTAIC |  | 2.5 | 2.5 | SDGE | NQC | FC | 0.01 | 0.08 | 0.09 | 0.11 | 0.16 | 0.33 | 0.36 | 0.31 | 0.28 | 0.19 | 0.14 | 0.09
VLCNTR_6_VCSLR2 | Valley Center 2 | GEN | 2013-12-31 | 2013 | SUN | PHOTO VOLTAIC |  | 5 | 5 | SDGE | NQC | FC | 0.02 | 0.15 | 0.18 | 0.22 | 0.32 | 0.66 | 0.72 | 0.62 | 0.56 | 0.37 | 0.29 | 0.18
VLYHOM_7_SSJID | Woodward Power Plant | GEN | 2013-04-01 | 2013 | WATER | HYDRO |  | 3 | 5 | PGAE | NQC | FC | 0 | 0 | 0 | 0.4 | 0 | 0.1 | 0.44 | 0.29 | 0.02 | 0 | 0 | 0
VOLTA_2_UNIT 1 | VOLTA HYDRO UNIT 1 | GEN | 1980-01-01 | 1980 | WATER | HYDRO |  | 9.1 | 9.1 | PGAE | NQC | FC | 4.15 | 4.25 | 1.19 | 0.46 | 2.05 | 1.26 | 0.73 | 0.75 | 1.33 | 1.33 | 1.71 | 2.06
VOLTA_2_UNIT 2 | Volta Hydro Unit 2 | GEN | 1981-01-01 | 1981 | WATER | HYDRO |  | 1 | 1 | PGAE | NQC | FC | 0.29 | 0.4 | 0.3 | 0.2 | 0.37 | 0.24 | 0.16 | 0.09 | 0.21 | 0.17 | 0.23 | 0.26
VOLTA_6_BAILCK | Bailey Creek Ranch | GEN | 1982-05-26 | 1982 | WATER | HYDRO |  | 0.63 | 0.6 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VOLTA_6_DIGHYD | Digger Creek Ranch Hydro | GEN | 2014-07-02 | 2014 | WATER | HYDRO |  | 0.6 | 0.6 | PGAE | NQC | FC | 0.3 | 0.31 | 0.3 | 0.38 | 0.33 | 0.29 | 0.25 | 0.22 | 0.22 | 0.23 | 0.22 | 0.25
VOLTA_7_PONHY1 | Ponderosa Bailey Hydroelectric | GEN | 2020-03-20 | 2020 | WATER | HYDRO |  | 1.25 | 1.25 | PGAE | NQC | FC | 0.22 | 0.21 | 0.2 | 0.11 | 0.2 | 0.15 | 0 | 0 | 0 | 0.03 | 0.01 | 0.04
VOLTA_7_QFUNTS | VOLTA_7_QFUNTS | GEN | 2007-03-01 | 2007 | WATER | HYDRO |  | 0.15 | 2.3 | PGAE | NQC | FC | 0.08 | 0.07 | 0.06 | 0.05 | 0.05 | 0.04 | 0.04 | 0.02 | 0.01 | 0.01 | 0.03 | 0.04
VOYAGR_2_VOAWD5 | Voyager Wind Oasis Alta | GEN | 2021-04-26 | 2021 | WIND | WIND |  | 13.98 | 14 | SCE | NQC | FC | 2.47 | 2.63 | 2.31 | 2.21 | 2.35 | 2.16 | 2 | 1.52 | 1.57 | 1.46 | 1.97 | 2.38
VOYAGR_2_VOYWD1 | Voyager 1 | GEN | 2019-12-30 | 2019 | WIND | WIND |  | 128.91 | 131.1 | SCE | NQC | FC | 22.78 | 24.23 | 21.29 | 20.39 | 21.69 | 19.88 | 18.47 | 14.03 | 14.5 | 13.45 | 18.12 | 21.95
VOYAGR_2_VOYWD2 | Voyager Wind 2 | GEN | 2018-12-19 | 2018 | WIND | WIND |  | 126.35 | 128.7 | SCE | NQC | FC | 22.33 | 23.75 | 20.86 | 19.99 | 21.26 | 19.48 | 18.1 | 13.75 | 14.21 | 13.18 | 17.76 | 21.52
VOYAGR_2_VOYWD3 | Voyager Wind 3 | GEN | 2018-12-29 | 2018 | WIND | WIND |  | 42.45 | 43.2 | SCE | NQC | FC | 7.5 | 7.98 | 7.01 | 6.72 | 7.14 | 6.55 | 6.08 | 4.62 | 4.77 | 4.43 | 5.97 | 7.23
VOYAGR_2_VOYWD4 | Voyager Wind 4 | GEN | 2018-12-29 | 2018 | WIND | WIND |  | 21.01 | 21.6 | SCE | NQC | FC | 3.71 | 3.95 | 3.47 | 3.32 | 3.53 | 3.24 | 3.01 | 2.29 | 2.36 | 2.19 | 2.95 | 3.58
VSTAES_6_VESBT1 | Vista Energy Storage | GEN | 2018-06-26 | 2018 | LESR | OTHER |  | 40 | 40 | SDGE | NQC | PD | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
WADHAM_6_UNIT | Wadham Energy LP | GEN | 1989-03-24 | 1989 | WASTE TO POWER | STEAM |  | 29.07 | 32 | PGAE | NQC | FC | 25 | 24.83 | 24.03 | 22.2 | 16.53 | 24.4 | 23.93 | 23.44 | 24.37 | 23.6 | 13.83 | 24.61
WALCRK_2_CTG1 | Walnut Creek Energy Park Unit 1 | GEN | 2013-03-21 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 97.32 | 102.5 | SCE | NQC | FC | 96.43 | 96.43 | 96.43 | 96.43 | 96.43 | 96.43 | 96.43 | 96.43 | 96.43 | 96.43 | 96.43 | 96.43
WALCRK_2_CTG2 | Walnut Creek Energy Park Unit 2 | GEN | 2013-03-21 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 96.91 | 102.5 | SCE | NQC | FC | 96.91 | 96.91 | 96.91 | 96.91 | 96.91 | 96.91 | 96.91 | 96.91 | 96.91 | 96.91 | 96.91 | 96.91
WALCRK_2_CTG3 | Walnut Creek Energy Park Unit 3 | GEN | 2013-03-21 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 96.65 | 102.5 | SCE | NQC | FC | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65
WALCRK_2_CTG4 | Walnut Creek Energy Park Unit 4 | GEN | 2013-03-29 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 96.6 | 102.5 | SCE | NQC | FC | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49 | 96.49
WALCRK_2_CTG5 | Walnut Creek Energy Park Unit 5 | GEN | 2013-04-30 | 2013 | NATURAL GAS | COMBUSTION TURBINE |  | 96.65 | 102.5 | SCE | NQC | FC | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65 | 96.65
WALNUT_2_SOLAR | Industry MetroLink PV 1 | GEN | 2012-04-03 | 2012 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.6 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WALNUT_6_HILLGEN | Puente Hills | GEN | 2017-06-01 | 2017 | BIOGAS | OTHER |  | 47 | 50 | SCE | NQC | FC | 22.26 | 22.75 | 22.47 | 21.68 | 21.05 | 21.96 | 22 | 21.88 | 21.69 | 21.18 | 20.96 | 20.91
WALNUT_7_WCOVST | MM West Covina - ST Unit | GEN | 1996-10-05 | 1996 | BIOGAS | STEAM |  | 6.5 | 6.5 | SCE | NQC | FC | 4.88 | 4.87 | 4.87 | 5.22 | 5.16 | 5.12 | 5.07 | 5.02 | 4.99 | 4.77 | 4.94 | 4.94
WARNE_2_UNIT | WARNE HYDRO AGGREGATE | GEN | 1982-01-01 | 1982 | WATER | HYDRO |  | 76 | 0 | SCE | NQC | FC | 36.6 | 43.28 | 40.96 | 41.95 | 41.04 | 42.33 | 41.36 | 41.31 | 42.75 | 40.96 | 42.17 | 37.59
WARNE_2_UNIT 1 | WARNE HYDRO UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 39.1 | 39.1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WARNE_2_UNIT 2 | WARNE HYDRO UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 39.1 | 39.1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WAUKNA_1_SOLAR | Corcoran Solar | GEN | 2013-08-14 | 2013 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
WAUKNA_1_SOLAR2 | Corcoran 2 | GEN | 2015-05-05 | 2015 | SUN | PHOTO VOLTAIC |  | 19.75 | 19.8 | PGAE | NQC | FC | 0.08 | 0.59 | 0.69 | 0.87 | 1.26 | 2.59 | 2.84 | 2.45 | 2.19 | 1.46 | 1.13 | 0.69
WDFRDF_2_WFFBT1 | West Ford Flat Energy Storage | GEN | 0 |  | LESR | OTHER |  | 25 | 25 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WDLEAF_7_UNIT 1 | WOODLEAF HYDRO | GEN | 1963-01-01 | 1963 | WATER | HYDRO |  | 60 | 60 | PGAE | NQC | FC | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
WEBER_6_FORWRD | Forward | GEN | 2014-02-05 | 2014 | BIOGAS | RECIPROCATING ENGINE |  | 4.2 | 4.3 | PGAE | NQC | FC | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
WESCAN_2_BDSBT1 | Bateria Del Sur | GEN | 2023-06-23 | 2023 | LESR | OTHER |  | 131 | 131 | SDGE | NQC | PD | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131
WESTPT_2_UNIT | West Point Hydro Plant | GEN | 1948-01-01 | 1948 | WATER | HYDRO |  | 14 | 14 | PGAE | NQC | FC | 9.55 | 6.79 | 8.2 | 4.52 | 2.3 | 10.8 | 10.54 | 11.4 | 10.34 | 9.94 | 10.72 | 10.16
WFRESN_1_SOLAR | Joya Del Sol | GEN | 2012-12-21 | 2012 | SUN | PHOTO VOLTAIC |  | 1.5 | 1.5 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WHEATL_6_LNDFIL | G2 ENERGY, OSTROM ROAD LLC | GEN | 2013-09-01 | 2013 | BIOGAS | RECIPROCATING ENGINE |  | 3.55 | 3.55 | PGAE | NQC | FC | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55 | 3.55
WHELPP_2_NSPIN | WHELPP_2_NSPIN | GEN | 0 |  | OTHER | PUMP |  | 112.5 | 112.5 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WHITEH_2_MEADDYN1 | White Hills A | TG | 2020-12-16 | 2020 | WIND | WIND |  | 50 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WHITEH_2_MEADDYN2 | White Hills B | TG | 2020-12-16 | 2020 | WIND | WIND |  | 300 | 0 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WHITNY_6_SOLAR | Whitney Point Solar | GEN | 2017-04-15 | 2017 | SUN | PHOTO VOLTAIC |  | 20 | 22 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WHTWTR_1_WINDA1 | Whitewater Hill Wind Project | GEN | 2002-08-31 | 2002 | WIND | WIND |  | 61.5 | 61.5 | SCE | NQC | FC | 10.87 | 11.56 | 10.16 | 9.73 | 10.35 | 9.48 | 8.81 | 6.69 | 6.92 | 6.42 | 8.65 | 10.47
WILLMS_6_ARBBM1 | Abel Road Bioenergy | GEN | 2022-07-26 | 2022 | BIOMASS | OTHER |  | 3 | 3 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WISE_1_UNIT 1 | Wise Hydro Unit 1 | GEN | 1917-01-01 | 1917 | WATER | HYDRO |  | 14.5 | 14.5 | PGAE | NQC | FC | 3.77 | 4.97 | 5.2 | 6.76 | 8.2 | 7.46 | 8.34 | 8.85 | 7.34 | 4 | 0 | 4.08
WISE_1_UNIT 2 | WISE HYDRO UNIT 2 | GEN | 1986-01-01 | 1986 | WATER | HYDRO |  | 3.2 | 3.2 | PGAE | NQC | FC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WISHON_6_UNIT 1 | WISHON HYDRO UNIT 1 | GEN | 0 |  | WATER | HYDRO |  | 5.6 | 5.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WISHON_6_UNIT 2 | WISHON HYDRO UNIT 2 | GEN | 0 |  | WATER | HYDRO |  | 5.6 | 5.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WISHON_6_UNIT 3 | WISHON HYDRO UNIT 3 | GEN | 0 |  | WATER | HYDRO |  | 5.6 | 5.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WISHON_6_UNIT 4 | WISHON HYDRO UNIT 4 | GEN | 0 |  | WATER | HYDRO |  | 5.6 | 5.6 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WISHON_6_UNITS | Wishon/San Joaquin #1-A AGGREGATE | GEN | 1910-01-01 | 1910 | WATER | HYDRO |  | 18.4 | 0 | PGAE | NQC | FC | 1.61 | 1.76 | 2.5 | 2.16 | 0.8 | 0.43 | 0 | 0 | 0 | 6.72 | 5.11 | 1.5
WISTER_2_WISSR1 | Wister Solar | TG | 2022-07-12 | 2022 | SUN | PHOTO VOLTAIC |  | 20 | 20 | SDGE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WISTRA_2_WRSSR1 | Wistaria Ranch Solar | GEN | 2018-11-06 | 2018 | SUN | PHOTO VOLTAIC |  | 100 | 100 | SDGE | NQC | FC | 0.4 | 3 | 3.5 | 4.4 | 6.4 | 13.1 | 14.4 | 12.4 | 11.1 | 7.4 | 5.7 | 3.5
WLDWD_1_SOLAR1 | Wildwood Solar I | GEN | 2015-02-19 | 2015 | SUN | PHOTO VOLTAIC |  | 20 | 20 | PGAE | NQC | FC | 0.08 | 0.6 | 0.7 | 0.88 | 1.28 | 2.62 | 2.88 | 2.48 | 2.22 | 1.48 | 1.14 | 0.7
WLDWD_1_SOLAR2 | Wildwood Solar 2 | GEN | 2017-01-11 | 2017 | SUN | PHOTO VOLTAIC |  | 15 | 15 | PGAE | NQC | FC | 0.06 | 0.45 | 0.53 | 0.66 | 0.96 | 1.97 | 2.16 | 1.86 | 1.67 | 1.11 | 0.86 | 0.53
WNDGPP_2_NSPIN | WNDGPP_2_NSPIN | GEN | 0 |  | OTHER | PUMP |  | 239.1 | 239.1 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WNDMAS_2_UNIT 1 | BUENA VISTA ENERGY, LLC | GEN | 1983-12-24 | 1983 | WIND | WIND |  | 38 | 36 | PGAE | NQC | FC | 12.48 | 13.39 | 11.94 | 12.61 | 13.05 | 9.63 | 8.56 | 8.04 | 8.26 | 6.92 | 8.74 | 11.17
WNDSTR_2_WIND | Windstar | GEN | 2012-01-28 | 2012 | WIND | WIND |  | 120 | 0 | SCE | NQC | FC | 21.2 | 22.55 | 19.82 | 18.98 | 20.19 | 18.5 | 17.19 | 13.06 | 13.49 | 12.52 | 16.87 | 20.44
WNDSTR_2_WIND1 | Windstar Wind Farm | GEN | 0 |  | WIND | WIND |  | 60 | 60 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WNDSTR_2_WIND2 | Windstar Wind Farm | GEN | 0 |  | WIND | WIND |  | 60 | 60 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WOLFSK_1_UNITA1 | Wolfskill Energy Center | GEN | 2003-03-22 | 2003 | NATURAL GAS | COMBUSTION TURBINE |  | 48.68 | 49.9 | PGAE | NQC | FC | 46.9 | 46.9 | 46.9 | 46.9 | 46.9 | 46.9 | 46.9 | 46.9 | 46.9 | 46.9 | 46.9 | 46.9
WOODWR_1_HYDRO | Quinten Luallen | GEN | 2017-06-14 | 2017 | WATER | HYDRO |  | 7.3 | 7.3 | PGAE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WRGTSR_2_WSFSR1 | Wright Solar Freeman | GEN | 2019-12-31 | 2019 | SUN | PHOTO VOLTAIC |  | 200 | 200 | PGAE | NQC | FC | 0.8 | 6 | 7 | 8.8 | 12.8 | 26.2 | 28.8 | 24.8 | 22.2 | 14.8 | 11.4 | 7
WSENGY_1_UNIT 1 | Wheelabrator Shasta | GEN | 2017-12-01 | 2017 | BIOMASS | STEAM |  | 50 | 50 | PGAE | NQC | FC | 34.04 | 34.05 | 34.05 | 32.98 | 34.04 | 34.04 | 34.2 | 37.12 | 36.18 | 33.92 | 32.97 | 34.06
WSNR_2_CVPDYN | Central Valley 1 | TG | 2017-07-26 | 2017 | WATER | HYDRO |  | 10 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WSNR_2_TESLADYN | Central Valley Tesla | TG | 2017-12-13 | 2017 | WATER | HYDRO |  | 10 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WSNR_5_TRCYDYN | Central Valley Tracy | TG | 2017-12-13 | 2017 | WATER | HYDRO |  | 10 | 0 | PGAE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WSTWND_2_M89BT2 | Mojave 89 BESS 2B | GEN | 2023-05-25 | 2023 | LESR | OTHER |  | 70.6 | 70.6 | SCE | NQC | EO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WSTWND_2_M89WD2 | Mojave 89 Wind | GEN | 2023-05-25 | 2023 | WIND | WIND |  | 82.65 | 82.7 | SCE | NQC | FC | 14.6 | 15.53 | 13.65 | 13.08 | 13.9 | 12.74 | 11.84 | 9 | 9.29 | 8.62 | 11.62 | 14.08
WSTWND_2_M90WD2 | Mojave 90 | GEN | 2020-06-02 | 2020 | WIND | WIND |  | 64.82 | 64.9 | SCE | NQC | FC | 11.45 | 12.18 | 10.7 | 10.25 | 10.9 | 10 | 9.29 | 7.06 | 7.29 | 6.76 | 9.11 | 11.04
WSTWND_2_SBSBT1 | Sagebrush Solar 2 | GEN | 2023-05-23 | 2023 | LESR | OTHER |  | 80 | 80 | SCE | NQC | ID | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
WSTWND_2_SBSBT2 | Sagebrush Solar 2 ESS 40 | GEN | 0 |  | LESR | OTHER |  | 40 | 40 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WSTWND_2_SBSBT3 | Sagebrush Solar 2 ESS 59 | GEN | 0 |  | LESR | OTHER |  | 59 | 59 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
YELPIN_2_YP2BT1 | Yellow Pine 2 BESS | GEN | 2023-07-26 | 2023 | LESR | OTHER |  | 65 | 65 | SCE | NQC | ID | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
YELPIN_2_YP2BT2 | Yellow Pine 2 A BESS | GEN | 0 |  | LESR | OTHER |  | 53 | 53 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
YELPIN_2_YP2BT3 | Yellow Pine 2 B BESS | GEN | 0 |  | LESR | OTHER |  | 32 | 32 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
YELPIN_2_YP2SR1 | Yellow Pine 2 | GEN | 2023-07-26 | 2023 | SUN | PHOTO VOLTAIC |  | 125 | 125 | SCE | NQC | ID | 0.29 | 2.58 | 3.1 | 4.17 | 6.23 | 12.81 | 13.96 | 11.81 | 10.21 | 6.45 | 4.49 | 2.13
YELPIN_2_YP2SR2 | Yellow Pine 2 A PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 60 | 60 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
YELPIN_2_YP2SR3 | Yellow Pine 2 B PV | GEN | 0 |  | SUN | PHOTO VOLTAIC |  | 65 | 65 | SCE |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
YUBACT_1_SUNSWT | YUBA CITY COGEN | GEN | 1990-12-27 | 1990 | NATURAL GAS | COMBUSTION TURBINE |  | 49.97 | 49 | PGAE | NQC | FC | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97 | 49.97
YUBACT_6_UNITA1 | Yuba City Energy Center (Calpine) | GEN | 2002-07-26 | 2002 | NATURAL GAS | COMBUSTION TURBINE |  | 47.16 | 49.9 | PGAE | NQC | FC | 47.16 | 47.16 | 47.16 | 47.16 | 47.16 | 47.16 | 47.16 | 47.16 | 47.16 | 47.16 | 47.16 | 47.16
ZOND_6_UNIT | ZOND WINDSYSTEMS INC. | GEN | 1985-12-30 | 1985 | WIND | WIND |  | 17.1 | 24.1 | PGAE | NQC | FC | 5.62 | 6.02 | 5.37 | 5.68 | 5.87 | 4.33 | 3.85 | 3.62 | 3.72 | 3.11 | 3.93 | 5.03
Note on H1: Koppolu, Sai: Stack Analysis excludes Strategic Reserve Resources

## Expected Resource Agg. (NQC MW)
Resource Type | 2024-01-01 | 2024-02-01 | 2024-03-01 | 2024-04-01 | 2024-05-01 | 2024-06-01 | 2024-07-01 | 2024-08-01 | 2024-09-01 | 2024-10-01 | 2024-11-01 | 2024-12-01
Storage | 25 | 25 | 172 | 1505.25 | 2637.45 | 2840.15 | 2922.15 | 2922.15 | 2922.15 | 2922.15 | 2922.15 | 2922.15
Solar | 467 | 467 | 593 | 593 | 1887.5 | 1957.24 | 1957.24 | 1957.24 | 1957.24 | 1957.24 | 1957.24 | 1957.24
Other-Renewable | 5 | 5 | 5 | 5 | 7.55 | 7.55 | 7.55 | 7.55 | 7.55 | 7.55 | 7.55 | 7.55
*CAISO Public*

## Tables (hidden)
Month
No. | Month
1 | January
2 | February
3 | March
4 | April
5 | May
6 | June
7 | July
8 | August
9 | September
10 | October
11 | November
12 | December