## Instruction list
Introduction tab
General information
Fill out all general information section with facility data
Data submission requirement
Yes | you are rquired to submit data document
No | This is not a requirement for this facility
Data on file | ISO has data on file, please check and provide updates if any
Equipment Data tab
Review the data filled out for accuracy and update- please highlight changes in red
Only fill out sections applicable to generator technology
Fill data in white cells
Select drop down options from green cells
use "Unit" columns to input data for; 1) each invidual generating unit, or 2)each inverter type associated with generating unit, or 3)each CT/ST seperately for combined cycle units
Validation tab (use this tab for self-validation of submission)
The validation check-list should be completed with "Yes" or "N/A" to count as a complete submission
Supporting document validation
Generator Owner Confirmation |  | CAISO/PTO Review
Yes | You have provided requested document | Yes | CAISO/PTO to populate after submission review
No | You have not provided requested document | No
N/A | You confirmed document is not applicable | N/A
Equipment Data validation
Generator Owner Confirmation |  | CAISO/PTO Review
Yes | You have performed requested validation | Yes | CAISO/PTO to populate after submission review
No | You have not performed requested validation | No
N/A | You confirmed document is not applicable | N/A
What does Consistent mean?
Equipment data vs SLD
values in Equipment Data do not contradict values in SLD
Equipment data vs .epc file
values in Equipment Data do not contradict values in .epc file
Equipment data vs dyd file
values in Equipment Data do not contradict values in .dyd file
The ISO and PTO review notes are for ISO and PTO to track model reviews beyond completeness.
ISO and PTO Review Notes
ISO and PTO enter notes after reviewing the models. Issues identified do not count for incomplete submission, but need to be resolved before the models are updated in the ISO/PTO model database.

## Introduction
Required Generating and Interconnection Facility Data - Category 1 and 2 GENERATING AND INTERCONNECTION FACILITY DATA
CAISO Public Document
|  | Version: V4 | Version: DRAFT
|  | Last Updated: May 08, 2024 | Last Updated: April, 26, 2018
General Information
Generating Plant Name
ISO Market Resource_ID(s)
Generator Owner Name
Point of Interconnection (POI)
Point of Delivery to ISO Controlled Grid
Generating Facility Type (Thermal, hydro, solar PV, wind etc)
Net MW at Point of Interconnection*
On-Site Load for Co-Generation (MW)
Last Reactive Capability Test Date
Last Dynamic Model Test Date
Contact Person Name
Contact Person Email
Contact Person Phone
* Net MW at POI according to the generation interconnection agreement
Data Submission Requirement
No. | Item | Description | Required* | Reference
1 | Single-Line Diagram | Single-line diagram showing applicable equipment such as generating units, step-up transformers, auxiliary transformers, switches/disconnects of the interconnection, including the required protection devices and circuit breakers. For wind and photovoltaic generator plants, the one line diagram should include the distribution lines connecting the various groups of generating units, the generator capacitor banks, the step up transformers, the distribution lines. | Data on file
2 | Equipment Data | Enter data in the "Equipment Data" tab | Yes
3 | Test Report for Generator Real and Reactive Power Capability | The report shall verify the real and reactive power capability for each individual generating unit. A minimum of four points on the reactive capability curve shall be verified. The report shall be no more than 5-year old. | Yes | https://www.nerc.com/pa/Stand/Reliability%20Standards/MOD-025-2.pdf
4 | Power flow model in GE PSLF .epc format | An accuate power flow model representing the generating plant | Yes
5 | Dynamic model in GE PSLF .dyd format | An accuate dynamic model representing the generating plant in the transient stability analysis. The model must • Initialize without error; • A 10-second no-disturbance simulation at full real power output results in spread of Pg and Qg less than 1 or 1% | Yes
6 | Test Report for Dynamic Model | Test report that verifies the dynamic model. The report shall be no more than 10-year old | Yes | http://www.caiso.com/Documents/Presentation-Inverter-Based-Resource-Dynamic-Model-Validation-6-12-23.pdf#search=Dynamic%20Model
7 | Electromagnetic Transient Model for Sub-Synchronous Resonance Study | Study model from the manufacturer of the generating untis that is suitable for electomagnetic transient analysis | Yes | http://www.caiso.com/Pages/documentsbygroup.aspx?GroupID=95422303-C0DD-43DF-9470-5492167A5EC5
* Submission is not required if the data has already been received by the PTO and the CAISO. But if there are updates to the previous submission, please re-submit.
Warning
Generator Owners please enter information in white cells and choose from drop down list in green cells. Do not enter in any other cells.

## Equipment Data
0
Item # |  |  |  | UNITS
I. Overall Plant MW Information
I.1 | Total Generating Facility Gross Nameplate Capacity |  |  | MVA | 0
I.2 | Maximum Total Generating Facility Gross Output |  |  | MW |  | The gross MW output to achieve requested MW at POI
I.3 | Generating Facility Auxiliary Load |  |  | MW
I.4 | Maximum Net Output at Generating Facility |  |  | MW | 0
I.5 | Anticipated Losses between the Generating Facility and POI |  |  | MW |  | Include all transformer and line losses between the generating units and the POI at total Generating Facility gross output as calculated by the power flow model in .epc file
I.6 | Maximum Net Output at POI |  |  | MW | 0 | must match MW value derived from power flow model in .epc file
I.7 | Minimum Gross Output at Generating Facility |  |  | MW
I.8 | For combined cycle plants, specify the plant net output capacity for an outage of the steam turbine or an outage of a single combustion turbine |  |  | MW
II. Individual Generating Facility Characteristics
II.1 | Generating Facility Name |  |  |  | Unit 1 | Unit 2 | Unit 3 | Unit 4 | Unit 5 | Unit 6 | Unit 7 | Unit 8 | Unit 9
II.2 | Technology
II.3 | Type
II.4 | Manufacturer
II.5 | Model Name
II.6 | Model Number
II.8 | Year Manufactured
II.9 | Number of Individual Generators or Inverters
II.10 | Nominal Terminal Voltage |  |  | kV
II.11 | Individual generator rated MVA |  |  | MVA
II.12 | Individual generator rated MW |  |  | MW
II.13 | Individual generator power factor at rated MW
II.14 | Individual generator power factor regulation range at rated MW output |  | Leading (-)
II.15 |  |  | Lagging (+)
II.16 | Generator Voltage Regulation Range (+/-) |  |  | %
II.17 | Phase
II.18 | Connection
II.19 | Upward frequency response droop (increase output for low frequency) |  |  | %
II.20 | Downward frequency response droop (reduce output for high frequency) |  |  | %
II.21 | Frequency response deadband |  | +/- | Hz
II.22 | Generator/inverter-Level Reactive Power Control Mode
Skip Section III if the plant does not have synchronous generators
III. Synchronous Generator Information
III.1 | Generating Facility Name
A. Generator
III.2 | Dynamic Model Name
III.3 |  | If other, specify the model name and reason to use non-WECC approved model
B. Excitation for Each Generator
III.4 | Manufacture
III.5 | For exciter type, please choose from options 1 to 9 or describe the specific excitation system.
III.6 |  | Other? - Please Specify:
III.7 | Excitation Dynamic Model Name
III.7a | Over-Excitation Limiter Dynamic Model Name
III.7b | Under-Excitation Limiter (If yes, please provide relay setting document)
C. Power System Stabilizer for Each Generator
III.8 | Manufacturer
III.9 | Dynamic Model Name
D. Turbine-Governor for Each Generator
III.10 | Turbine Type
III.11 | Turbine manufacturer
III.12 | Dynamic Model Name
E. Short Circuit Data
III.13 | X"1 – positive sequence subtransient reactance (saturated) |  |  | p.u**
III.14 | X"1 – positive sequence subtransient reactance (unsaturated) |  |  | p.u**
III.15 | X2 – negative sequence reactance |  |  | p.u**
III.16 | X0 – zero sequence reactance |  |  | p.u**
III.17 | Generator MVA base |  |  | MVA
III.18 | Generator Grounding
III.19 |  | If grounded through impedance, please enter: | R: | ohms
III.20 |  |  | X: | ohms
** On generator MVA and nominal line voltage (kV) Base
F. Protection
III.20 | Under/Over Frequency Relay
III.21 | Under/Over Voltage Relay
III.22 | Out-of-Step Relay
If "Yes", include dynamic models for lhvrt and lhfrt in the .dyd submittal, provide out-of-step relay setting document and answer the followings:
V.17 | Are under/over frequency relay settings meeting NERC reliability standard PRC-024-2?
V.18 | If no, describe known limitation that prevents the relay settings from meeting PRC-024-2.
V.19 | Are under/over voltage relay settings meeting NERC reliability standard PRC-024-2?
V.20 | If no, describe known limitation that prevents the relay settings from meeting PRC-024-2.
Skip Section IV if the plant does not have induction generators (*Type 4 WTG are inverter-based)
IV. Induction Generator Information
IV.1 | Generating Facility Name
A. Dynamic Model Name (Use Section V-B.Dynamic Model Name for Type 3)
IV.2 | Generator Model
IV.3 | Turbine Model
IV.4 | Pitch Control Model if Type 1 Wind Turbine
IV.5 | Control Model if Type 2 Wind Turbine
IV.6 | Other? - Please Specify:
B. Short Circuit Data
IV.7 | Max current during fault detection |  |  | Amps
IV.8 | Duration of the max current |  |  | Cycles
C. Protection
IV.9 | Under/Over Frequency Relay
IV.10 | Under/Over Voltage Relay
If "Yes", include dynamic models for lhvrt and lhfrt in the .dyd submittal and answer the followings:
IV.11 | Are under/over frequency relay settings meeting NERC reliability standard PRC-024-2?
IV.12 | If no, describe known limitation that prevents the relay settings from meeting PRC-024-2.
IV.13 | Are under/over voltage relay setteings meeting NERC reliability standard PRC-024-2?
IV.14 | If no, describe known limitation that prevents the relay settings from meeting PRC-024-2.
Skip Section V if the plant does not have inverter-based generators
V. Inverter-Based Generator Information (Individual Inverter Data)
V.1 | Generating Facility Name
A. Maximum design fault contribution current (with LVRT enabled):
V.2 |  | Initial symmetrical short-circuit current (Ik'') |  | Amps
V.3 |  | First Peak of short circuit current (ip) |  | Amps
V.4 |  | Steady-state short circuit current (Ik) |  | Amps
V.5 |  | Time to reach steady-state current |  | ms
* Refer to IEC 60909 for definitions of the quantities above.
B. Dynamic Model Name
| If solar resources connected to the distribution system, | If
V.7 |  | Distributed Solar PV Model
Otherwise,
V.8 |  | Generator/Converter Model
V.9 |  | Electrical Control Model
V.10 |  | Plant Control Model
V.11 |  | Drive Train Model if Type 3 or 4 Wind Turbine Geneator
V.12 |  | Aerodynamic Model if Type 3 Wind Turbine Generator
V.13 |  | Pitch Control Model if Type 3 Wind Turbine
V.14 |  | Torque Control Model if Type 3 Wind Turbine
C. Protection
V.15 | Under/Over Frequency Relay
V.16 | Under/Over Voltage Relay
If "Yes", include dynamic models for lhvrt and lhfrt in the .dyd submittal and answer the followings:
V.17 | Are under/over frequency relay settings meeting NERC reliability standard PRC-024-2?
V.18 | If no describe known limitation that prevents the relay settings from meeting PRC-024-2.
V.19 | Are under/over voltage relay settings meeting NERC reliability standard PRC-024-2?
V.20 | If no, describe known limitation that prevents the relay settings from meeting PRC-024-2.
V.21 | Please specify current injection priority during and after a fault
V.22 | Does inverter use momentary cessation?
If "Yes", please provide the momentary cessation settings below (Sections V.23 ­ V.27). Momentary cessation must be modeled consistent with NERC’s Modeling Momentary Cessation Guideline. Refer to the NERC alert for technical details at: https://www.nerc.com/comm/PC/NERCModelingNotifications/Modeling_Notification_-_Modeling_Momentary_Cessation_-_2018-02-27.pdf As required by the NERC modeling guideline, REEC_A MUST be used for the Electrical Control Models and NOT REEC_B. The dynamic models must be validated to make sure there are no initializion errors and perform as expected during a disturbance run.
V.23 | Low voltage momentary cessation voltage threshold |  |  | p.u.
V.24 | High voltage momentary cessation voltage threshold |  |  | p.u.
V.25 | Time delay before the inverter begins injecting current after momentary cessation, once voltage has returned to within the momentary cessation voltage threshold(s) |  |  | seconds
V.26 | Active current ramp rate when recovering from momentary cessation |  |  | p.u./sec
V.27 | MVA base for the active current ramp rate above |  |  | MVA
Skip Section VI if the plant does not have energy-storage generators
VI. Energy Storage Information
VI.1 | Select the source of charging ( transmission gird, on-site generator, etc.)
VI.2 | If selected "other" above, explain | bar: Unit 9
VI.3 | Select the operation of charging |  |  |  | Unit 1: Follow ISO dispatch instructions
Storage Device Specification Data (Name)
VI.4 | Total Storage Capability |  |  | MWh | bar: Unit 9
VI.5 | Charge/Discharge Cycle Efficiency |  |  | % | bar: Unit 9
Provide rated MW capacity associated with different durations below. Enter gross MW value at the equipment terminal.
VI.6 | Rated Storage Discharging Power |  |  | MW | bar: Unit 9
VI.7 | Discharge Duration under Rated Power |  |  | Hours | bar: Unit 9
VI.8 | Maximum Storage Discharging Power |  |  | MW | bar: Unit 9
VI.9 | Discharge Duration under Maximum Power |  |  | Hours | bar: Unit 9
VI.10 | Rated Storage Charging Power |  |  | MW | bar: Unit 9
VI.11 | Charge Duration under Rated Power |  |  | Hours | bar: Unit 9
VI.12 | Maximum Storage Charging Power |  |  | MW | bar: Unit 9
VI.13 | Charge Duration under Maximum Power |  |  | Hours | bar: Unit 9
VI.14 | Maximum Storage Charging Power in the GIA |  |  | MW | bar: Unit 9
Primary frequency response operating range
VI.15 |  | Minimum State of Charge |  | % | bar: Unit 9
VI.16 |  | Maximum State of Charge |  | % | bar: Unit 9
VII. Plant Level Control
VII.1 | 1) Reactive power capability from generators |  | Qmax | MVARS | Unit 3: For your reference, Qmax and Qmin to the right are calculated from the gross MVA and MW. You may enter any Qmax and Qmin within the calculated range.; Unit 7: 0
VII.2 |  |  | Qmin | MVARS | Unit 7: 0
VII.3 | Expected ambient temperature for the reactive capability above |  |  | ⁰C | bar: Unit 2 to Unit 9
VII.4 | 2) Additional reactive devices |  |  |  | Unit 1: Var Device 1; Unit 3: Var Device 2; Unit 5: Var Device 3; Unit 7: Var Device 4
VII.5 |  |  | Type of Device
VII.6 |  |  | If other, please select static or dynamic and describe | bar: Unit 1; Unit 3; Unit 5; Unit 7; Unit 9
VII.7 |  |  | Qmax | MVARS | bar: Unit 9
VII.8 |  |  | Qmin | MVARS | bar: Unit 9
VII.9 |  |  | Location | bar: Unit 9
Power Plant Controller
VII.10 | Is there a Power Plant Controller (PPC)? |  |  |  | Unit 2: If yes, please answer the followings VII.11 to VII.24
VII.11 | PPC manufacturer | bar: Unit 2 to Unit 9
PPC VOLTAGE/VAR CONTROL
VII.12 | Plant level voltage/Var control mode under cntinuous normal conditions |  |  |  | Unit 2: If other, please explain
VII.13 | Plant level voltage/Var control mode under abnormal voltage conditions |  |  |  | Unit 2: If other, please explain
VII.14 | Does the PPC freeze voltage/Var control at low voltage?
VII.15 | If yes above, enter the voltage at which PPC freezes |  |  | p.u. | bar: Unit 2 to Unit 9
VII.16 | Does the PPC implement voltage droop control?
VII.17 | If yes above, enter the voltage droop |  |  | % | bar: Unit 2 to Unit 9
VII.18 | Provide a general description of the control coordination among generators/inverters, reactive devices and transformer tap changers. | bar: Unit 9
PPC FREQUENCY/MW CONTROL
VII.19 | Does the plant have the primary frequency response capability |  |  |  | Unit 2: If yes, please answer the followings
VII.20 | If yes above, is the primary frequency response capability enabled in operation?
VII.21 | Does the plant have the Automatic Generation Control capability?
VII.22 | Describe how the MW at Point of Interconnection is controlled. | bar: Unit 9
VII.23 | MW upward ramp rate limit |  |  | MW/min | bar: Unit 2 to Unit 9
VII.24 | MW downward ramp rate limit |  |  | MW/min | bar: Unit 2 to Unit 9
VIII. Transformer Data
| Transformer Name |  |  |  | Unit 1: XFMR1; Unit 4: XFMR2; Unit 7: XFRM3
VIII.1 | No. of Transformers
VIII.2 | Transformer Type
[5 empty] | H Winding | X Winding | Y Winding | H Winding | X Winding | Y Winding | H Winding | X Winding | Y Winding
RATING
VIII.3 | Rated MVA (Please enter the rating to model the transformer in the interconnection studies) |  |  | MVA
VIII.4 | Connection (Delta, Wye, Gnd.)
VIII.5 | Cooling Type (OA,OA/FA, etc.)
VIII.6 | Temperature Rise Rating |  |  | ⁰C
VIII.7 | Rated Voltage |  |  | kV
VIII.8 | BIL |  |  | kV
VIII.9 | Available Taps (% of rating)
VIII.10 | Load Tap Changer? (Yes or No)
VIII.11 | Tap Settings |  |  | % of rating
| IMPEDANCE (Z) |  |  |  | H-X | H-Y | X-Y | H-X | H-Y | X-Y | H-X | H-Y | X-Y
VIII.12 | Positive Sequence |  |  | %
VIII.13 | Zero Sequence |  |  | %
VIII.14 | MVA Base |  |  | MVA
VIII.15 | Tested Taps
| WINDING RESISTANCE |  |  |  | H-X | H-Y | X-Y | H-X | H-Y | X-Y | H-X | H-Y | X-Y
VIII.16 | X/R Ratio
Current Transformer Ratios
VIII.17 |  | H | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.18 |  | X | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.19 |  | Y | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.20 |  | N | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
Percent Exciting Current at:
VIII.21 |  | 100% rated voltage | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.22 |  | 110% rated voltage | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
GEOMAGNETIC DISTURBANCE DATA
VIII.23 | Is the high side voltage greater than 200KV? | bar: Unit 1 to Unit 9
VIII.24 | Is the high side of the transformer winding wye-grounded | bar: Unit 1 to Unit 9
If "Yes" to the above 2 questions, provide data below
VIII.25 | DC Resistance of the Transformer |  |  | ohms | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.26 | Main Substation Earth Resistivity |  |  | ohms | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.27 | Does the transformer have a GIC blocking device?
VIII.28 | If the answer is "Yes" above, is the blocking device enabled?
VIII. Transformer Data (continued)
| Transformer Name |  |  |  | Unit 1: XFMR4; Unit 4: XFMR5; Unit 7: XFMR6
VIII.1 | No. of Transformer
VIII.2 | Transformer Type
[5 empty] | H Winding | X Winding | Y Winding | H Winding | X Winding | Y Winding | H Winding | X Winding | Y Winding
RATING
VIII.3 | Rated MVA |  |  | MVA
VIII.4 | Connection (Delta, Wye, Gnd.)
VIII.5 | Cooling Type (OA,OA/FA, etc.)
VIII.6 | Temperature Rise Rating |  |  | ⁰C
VIII.7 | Rated Voltage |  |  | kV
VIII.8 | Basic Insulation Level(BIL)
VIII.9 | Available Taps (% of rating)
VIII.10 | Load Tap Changer? (Yes or No)
VIII.11 | Tap Settings of LTC
| IMPEDANCE (Z) |  |  |  | H-X | H-Y | X-Y | H-X | H-Y | X-Y | H-X | H-Y | X-Y
VIII.12 | Percent |  |  | %
VIII.13 | Zero Sequence |  |  | %
VIII.14 | MVA Base |  |  | MVA
| WINDING RESISTANCE |  |  |  | H-X | H-Y | X-Y | H-X | H-Y | X-Y | H-X | H-Y | X-Y
VIII.16 | X/R Ratio
Current Transformer Ratios
VIII.17 |  | H | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.18 |  | X | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.19 |  | Y | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.20 |  | N | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
Percent Exciting Current at:
VIII.21 |  | 100% rated voltage | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.22 |  | 110% rated voltage | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
GEOMAGNETIC DISTURBANCE DATA
VIII.23 | Is the high side voltage greater than 200KV? | bar: Unit 1 to Unit 9
VIII.24 | Is the high side of the transformer winding wye-grounded | bar: Unit 1 to Unit 9
If "Yes" to the above 2 questions, provide data below
VIII.25 | DC Resistance of the Transformer |  |  | ohms | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.26 | Main Substation Earth Resistivity | bar: Unit 2 to Unit 3; Unit 5 to Unit 6; Unit 8 to Unit 9
VIII.27 | Does the transformer have a GIC blocking device?
VIII.28 | If the answer is "Yes" above, is the blocking device enabled?
IX. Interconnection Facilities Line Data
[5 empty] | Line1 | Line 2 | Line 3 | Line 4
IX.1 | Nominal Voltage |  |  | kV | bar: Unit 5 to Unit 9
IX.2 | Line Length |  |  | Miles | bar: Unit 5 to Unit 9
IX.3 | Line Termination Points |  |  | From: | bar: Unit 5 to Unit 9
To: | bar: Unit 5 to Unit 9
IX.4 | Conductor Type | bar: Unit 5 to Unit 9
IX.5 | Conductor Size | bar: Unit 5 to Unit 9
Summer line ratings in amperes
IX.6 |  | Normal |  | Amps | bar: Unit 5 to Unit 9
IX.7 |  | Emergency |  | Amps | bar: Unit 5 to Unit 9
Summer line ratings in MVA (Calculation)
IX.8 |  | Normal |  | MVA | Unit 1: 0; Unit 2: 0; Unit 3: 0; Unit 4: 0
IX.9 |  | Emergency |  | MVA | Unit 1: 0; Unit 2: 0; Unit 3: 0; Unit 4: 0
Winter line ratings in amperes
IX.10 |  | Normal |  | Amps | bar: Unit 5 to Unit 9
IX.11 |  | Emergency |  | Amps | bar: Unit 5 to Unit 9
Winter line ratings in MVA (Calculation)
IX.12 |  | Normal |  | MVA | Unit 1: 0; Unit 2: 0; Unit 3: 0; Unit 4: 0
IX.13 |  | Emergency |  | MVA | Unit 1: 0; Unit 2: 0; Unit 3: 0; Unit 4: 0
IX.14 | Positive Sequence Resistance (R) (for entire line length) |  |  | p.u.** | bar: Unit 5 to Unit 9
IX.15 | Positive Sequence Reactance (X) (for entire line length) |  |  | p.u.** | bar: Unit 5 to Unit 9
IX.16 | Zero Sequence Resistance (R0) (for entire line length) |  |  | p.u.** | bar: Unit 5 to Unit 9
IX.17 | Zero Reactance (X0) (for entire line length) |  |  | p.u.** | bar: Unit 5 to Unit 9
IX.18 | Line Charging (B) (for entire line length) |  |  | p.u.** | bar: Unit 5 to Unit 9
** On 100-MVA and nominal line voltage (kV) Base
X. For generators with a collector system, provide Collector System Equivalence Data
| Line |  |  |  | Unit 1: Collector 1; Unit 2: Collector 2; Unit 3: Collector 3; Unit 4: Collector 4; Unit 5: Collector 5
X.1 | Nominal Voltage |  |  | kV | bar: Unit 6 to Unit 9
Summer line ratings in Amperes
X.2 |  | Normal |  | Amps | bar: Unit 6 to Unit 9
X.3 |  | Emergency |  | Amps | bar: Unit 6 to Unit 9
Summer line ratings in MVA (Calculation)
X.4 |  | Normal |  | MVA | Unit 1: 0; Unit 2: 0; Unit 3: 0; Unit 4: 0; Unit 5: 0
X.5 |  | Emergency |  | MVA | Unit 1: 0; Unit 2: 0; Unit 3: 0; Unit 4: 0; Unit 5: 0
Winter line ratings in Amperes
X.6 |  | Normal |  | Amps | bar: Unit 6 to Unit 9
X.7 |  | Emergency |  | Amps | bar: Unit 6 to Unit 9
Winter line ratings in MVA (Calculation)
X.8 |  | Normal |  | MVA | Unit 1: 0; Unit 2: 0; Unit 3: 0; Unit 4: 0; Unit 5: 0
X.9 |  | Emergency |  | MVA | Unit 1: 0; Unit 2: 0; Unit 3: 0; Unit 4: 0; Unit 5: 0
X.10 | Positive Sequence Resistance (R1) (for entire line length of each collector circuit) |  |  | p.u.** | bar: Unit 6 to Unit 9
X.11 | Positive Sequence Reactance (X1) (for entire line length of each collector circuit) |  |  | p.u.** | bar: Unit 6 to Unit 9
X.12 | Zero Sequence Resistance (R0) (for entire line length of each collector circuit) |  |  | p.u.** | bar: Unit 6 to Unit 9
X.13 | Zero Reactance (X0) (for entire line length of each collector circuit) |  |  | p.u.** | bar: Unit 6 to Unit 9
X.14 | Line Charging (B) (for entire line length of each collector circuit) |  |  | p.u.** | bar: Unit 6 to Unit 9
** On 100-MVA and nominal line voltage (kV) Base
Please enter information in white cells and choose from drop down list in green cells. Do not enter in any other cells.

## Validation
0
Generator Owner Confirmation & Validation Checklist |  |  |  |  | Comment & Validation Tracking |  |  |  | Comment & Validation Tracking
The following section is intended for: 1) the Generator Owner to review and ensure all items are included and tasks are complete as "Yes" or "N/A" prior to submitting this form. Please verify each item listed below and enter in Column A. 2) the CAISO and PTO to review the data and attachments for completeness and sufficient to consider the submittal valid. |  |  |  |  | The following section is intended to identify and track comments and recommendations to and from the parties involved in the submittal validation process. DO NOT DELETE OR CHANGE PREVIOUS COMMENTS. |  |  |  | The following section is intended to identify and track comments and recommendations to and from the parties involved in the submittal validation process. DO NOT DELETE OR CHANGE PREVIOUS COMMENTS.
Generator Owner Confirmation |  | Objective is All Answers = Yes or N/A | CAISO & PTO Review |  | Version Control: |  |  |  | Version Control:
[5 empty] | Date: | Reviewed By: | Comment: |  | Date: | Reviewed By: | Comment:
Supporting Document Submittal Confirmation (see Instructions for further details)
Choose | Single line diagram |  |  | Choose
Choose | Test Report for Generator Real and Reactive Power Capability |  |  | Choose
Choose | Power flow model in GE PSLF .epc format |  |  | Choose
Choose | Dynamic model in GE PSLF .dyd format |  |  | Choose
Choose | Test Report for Dynamic Model |  |  | Choose
Choose | Electromagnetic Transient Model for Sub-Synchronous Resonance Study |  |  | Choose
Equipment Data Validation
[5 empty] | Comments: |  |  |  | Comments:
Choose | Are all applicable Equipment Data filled out? |  |  | Choose | Date: | mm/dd/yyyy | Commenter Name: |  | Date: | mm/dd/yyyy | Commenter Name:
Insert Notes Here: |  |  |  |  | Representing: |  |  | Choose One | Representing: |  |  | Choose One
[5 empty] | Comment here: |  |  |  | Comment here:
Choose | Are Equipment Data consistent with single line diagram? |  |  | Choose
Insert Notes Here:
Choose | Are Equipment Data consistent with power flow model? |  |  | Choose
Insert Notes Here:
Choose | Are Equipment Data consistent with dynamic model? |  |  | Choose
Insert Notes Here: |  |  |  |  | Date: | mm/dd/yyyy | Commenter Name: |  | Date: | mm/dd/yyyy | Commenter Name:
[5 empty] | Representing: |  |  | Choose One | Representing: |  |  | Choose One
[5 empty] | Comment here: |  |  |  | Comment here:
Choose | Is the test report for generator real and reactive capability less than 5-year old? |  |  | Choose
Insert Notes Here:
Choose | Are the real and reactive capability in the power flow model supported by the capability test report? |  |  | Choose
Insert Notes Here:
Choose | Is the test report for dynamic model less than 10-year old? |  |  | Choose
Insert Notes Here:
[5 empty] | Date: | mm/dd/yyyy | Commenter Name: |  | Date: | mm/dd/yyyy | Commenter Name:
Choose | Are all necessary models included in dynamic model file? |  |  | Choose | Representing: |  |  | Choose One | Representing: |  |  | Choose One
Insert Notes Here: |  |  |  |  | Comment here: |  |  |  | Comment here:
Choose | Does the dynamic model intialize without errors? |  |  | Choose
Insert Notes Here:
Choose | Does the 10-second no-disturbance simulation at full real power output result in spread of Pg and Qg less than 1 or 1%? |  |  | Choose
Insert Notes Here:
[5 empty] | Date: | mm/dd/yyyy | Commenter Name: |  | Date: | mm/dd/yyyy | Commenter Name:
PTO and ISO Review Notes |  |  |  |  | Representing: |  |  | Choose One | Representing: |  |  | Choose One
The following section is intended for the CAISO and PTO to perform review of the models beyond completeness check. |  |  |  |  | Comment here: |  |  |  | Comment here:
| Are the parameters of the dynamic model within reasonable range and meet requirements of applicable reliability standards? |  |  | Choose
Insert Notes Here:
| Are all voltage control devices properly coordindated in the power flow model, i.e. no hunting among voltage regulations? |  |  | Choose
Insert Notes Here:
| Are voltage controls consistent between the power flow model and dynamic model? |  |  | Choose
Insert Notes Here: |  |  |  |  | Date: | mm/dd/yyyy | Commenter Name: |  | Date: | mm/dd/yyyy | Commenter Name:
[5 empty] | Representing: |  |  | Choose One | Representing: |  |  | Choose One
[5 empty] | Comment here: |  |  |  | Comment here:
| Does the generator meet its reactive capability requirement? |  |  | Choose
Insert Notes Here:
| Do the protection settings meet the interconnection requirement? |  |  | Choose
Insert Notes Here:
| Is the BASE LOAD flag set correctely in the power flow model? |  |  | Choose | Date: | mm/dd/yyyy | Commenter Name: |  | Date: | mm/dd/yyyy | Commenter Name:
Insert Notes Here: |  |  |  |  | Representing: |  |  | Choose One | Representing: |  |  | Choose One
[5 empty] | Comment here: |  |  |  | Comment here:
| If EMT models are required, are EMT simulation results consistent with GE PSLF transient stability simulation results for a 3-phase bus fault at the POI? |  |  | Choose
Insert Notes Here:
Any other comments
Insert Notes Here:

## IBR EMT Checklist
EMT Model Generator Owner Confirmation & Validation Checklist | [5 empty] | EMT Model PTO and ISO Review Checklist
The following section is intended for: 1) the Generator Owner to review and ensure all items are included and EMT model is compliant with the requirement. Please answer each item listed below and enter in Column A. 2) the CAISO and PTO to verify the data and attachments. | [5 empty] | The following section is intended for: The CAISO and PTO to review EMT model performance and provide additional detailed review notes.
Generator Owner Confirmation |  | EMT Model Requirement |  | CAISO & PTO Review |  |  |  | CAISO & PTO Review
Supporting Documentation | [5 empty] | Supporting Documentation & Model Submission
Choose | Are the supporting documentation submitted? GO, please list the files below. |  |  |  | Choose | 1.a | The Vendor’s name and the specific version of the model should be clearly observable in the .pscx case file. |  | Choose
File Name |  |  | Description |  |  | Insert Notes Here:
[6 empty] | 1.b | Documentation and supporting model filenames should not conflict with model version shown in the .pscx case file. |  | Choose
Choose | Does the documentation include instruction for setup and running the model? |  |  |  | Choose | Insert Notes Here:
Insert Notes Here:
Choose | Doesthe documentation provides a clear way to identify site-specific settings and equipment configuration? |  |  |  | Choose
Insert Notes Here:
Model Submission
Choose | Are the complete model files submitted? GO, please list the files below. |  |  |  | Choose
File Name |  |  | Description
Insert Notes Here:
Choose | Is the model supplied with a sample test case including site specific plant representation? |  |  |  | Choose
Insert Notes Here:
Choose | Does the model schematic align with the single line diagram and include all devices from the inverters to the Point of Interconnection? |  |  |  | Choose
Insert Notes Here:
Model Accuracy | [5 empty] | Model Accuracy
Choose | Does the model use the actual firmware code from the inverter for power electronic controls ("real code")? |  |  |  |  | 2.a | Parameters of the gen-tie line, collectors, transformers align with the PSLF models. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | If not using real code, is a model validation report included? |  |  |  | Choose | 2.b | Number of inverters, inverter capacity and operating modes for voltage control and frequency control match the PSLF models. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Does the model include the plant level controller? List all the plant level controller below, e.g. power plant controller, customized phase locked loop systems, ride-through controllers, sub-synchronous control interaction damping controllers, etc. |  |  |  | Choose | 2.c | Power plant controller voltage control and frequency control match the PSLF models |  | Choose
Insert Notes Here:
Choose | Does the plant level controller control generating resources other than the subject resource in this model submission?
Insert Notes Here:
Choose | Are the operating modes which require system specific adjustment accessible? Please describe how to access mode settings below. |  |  |  | Choose
Insert Notes Here:
Choose | Does the model include automatically controlled capacitor and reactor banks? |  |  |  | Choose
Insert Notes Here:
Choose | Are the transformer magnetizing curves included? |  |  |  | Choose
Insert Notes Here:
Choose | Does the model include pertinent electrical and mechanical features, such as gearboxes, pitch controllers, or other features which impact the plant performance in the simulation period? |  |  |  | Choose
Insert Notes Here:
Choose | Are all protections which could impact ride-through performance modeled in detail? Please list the protections included in the model below. |  |  |  | Choose
Insert Notes Here:
Choose | Has the model being validated at different operating conditions ranging from minimum power through maximum power? |  |  |  | Choose
Insert Notes Here:
Choose | Is the model configured for the specific site being evaluated, as far as they are known? |  |  |  | Choose
Insert Notes Here:
Model Usability | [5 empty] | Model Usability
Choose | Are pertinent control or hardware options accessible to the user (e.g., adjustable protection thresholds, real power recovery ramp rates, or Sub-Synchronous Control Interaction damping controllers) |  |  |  | Choose | 3.a | PPC accepts an external active power setpoint. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Are there diagnostic flags accessible? Please provide the description of the diagnostic flags below. |  |  |  | Choose | 3.b | PPC accepts a voltage or reactive power setpoint. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
| Please provide the grid strength in terms of simple short circuit ratio at POI that the model is designed for. |  |  |  |  | 3.c | PPC has a mechanism to implement a settable voltage droop. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Does the model run at a time step between 10 μs to 20 μs? Please specify the time step required by the model below. |  |  |  | Choose | 3.d | If the primary frequency response is enabled, the plant responds to frequency changes by increasing or decreasing its active power as appropriate. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Is the model restricted to the time step provided above? |  |  |  | Choose | 3.e | Model initializes to the setpoints specified in the PPC. If droops or deadbands are utilized, the initial values may differ from the setpoints. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Does the model initialize itself? |  |  |  | Choose | 3.f | If external voltage control devices (STATCOM/DVAR, SVC, MSCs) are included in the plant, ensure that the voltage control of these devices is coordinated with the PPC, with no potential for VAR looping or oscillations. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Does the model initialize to P, Q, V setpoints in 5 seconds or less? |  |  |  | Choose | 3.g | Protection settings are implemented. These could be available as inputs in the model, or hard-coded in the black-boxed controls. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Does the model accept external reference variables for active and reactive power? |  |  |  | Choose
Insert Notes Here:
Model Basic Performance
Choose | Could the external references be changed dynamically during the simulation? |  |  |  | Choose | 4.a | Instantaneous voltage and current waveforms have minimal distortion, and no oscillations are observed. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Could the protection models be disabled for troubleshooting? |  |  |  | Choose | 4.b | Model is able to ride-through and recover from a temporary (no line outage or drop in SCR), 6-cycle, zero-impedance, three-phase fault at the high side of the station transformer, with a POI level SCR of 3. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Is the active power capacity scalable? |  |  |  | Choose | 4.c | Model responds to a step change in PPC voltage setpoint, reaching 90% of the new value between 1 and 10 seconds in a test system with POI level SCR of 3. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Is the active power dispatchable? |  |  |  | Choose | 4.d | Model responds to a step change in PPC active power setpoint, reaching 90% of the new value between 1 and 10 seconds in a test system with POI level SCR of 3. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Is the model compatible with Intel FORTRAN version 12 and higher? Please specify Intel FORTRAN version required below. |  |  |  | Choose | 4.e | Model trips or blocks when terminal voltage rises above 1.3 pu for 1.5 second. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Does the model compile using PSCAD version 4.6.3 or higher? |  |  |  | Choose | 4.f | Model trips or blocks when terminal voltage falls below the protection setting for specified time period. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Does the model support multiple instances of its own definition in a single PSCAD case? |  |  |  | Choose | 4.g | Model clearly displays trip / diagnostic signals indicating the status of all pertinent protection elements. |  | Choose
Insert Notes Here: | [5 empty] | Insert Notes Here:
Choose | Does the model support the PSCAD "snapshot" feature? |  |  |  | Choose
Insert Notes Here:
Choose | Does the model support the PSCAD "multiple run" feature?
Insert Notes Here:
Choose | Does the model support "copy transfer" feature to replicate the components in a different PSCAD case?
Insert Notes Here:
Choose | Is it true that the model does not use PSCAD layer functionality?
Insert Notes Here:

## Choices - to be hidden (hidden)
Type | Choose One |  | Y/N | Choose One | Gov Type | Choose One
| Induction |  |  | Yes |  | Steam
| Synchronous |  |  | No |  | Gas
| DC With Inverter |  |  | N/A |  | Combined Cycle
| Doubly Fed |  |  |  |  | Hydro
|  |  | Y/N | Choose One
Turbine Type | Choose one |  |  | Yes (See Below) | RE gen model | REGC_A
| 1: steam turbine (except steam of combined cycle) |  |  | No
| 2: combined cycle steam part |  |  | N/A
3: steam cross-compound
| 4: combined cycle total unit (planned gens and details for separate model not available) |  |  |  | RE control model | REEC_A
| 5: hydro |  |  |  |  | REEC_C
| 6: Internal Combustion Engine (diesel, piston, reciprocating) |  | Turbine Type | Choose One
| 7: diesel turbo charged |  |  | Type 1
| 11: GT (single shaft, does not include turbine part) |  |  | Type 2
| 12: aero derivative GT |  |  | Type 3 | RE PPC model | REPC_A
| 13: single shaft combined cycle |  |  |  |  | REPC_B
21: type 1 wind turbine (onshore only)
| 22: type 2 wind turbine (onshore only) |  |  |  | Type 3/4 WTG
| 23: type 3 wind turbine (onshore only) |  |  |  | Drive Train | WTGT_A | Drive train model for Wind type 3/4 (doubly-fed and full converter)
| 24: type 4 wind turbine (onshore only) |  |  |  | Areodynamic | WTGA_A | Aerodynamic model for Wind type 3 (doubly-fed)
| 25: wind turbine (offshore) |  |  |  | Pitch Control | WTGP_A | Pitch control model for Wind type 3
| 29: combined cycle combustion turbine part |  |  |  | Torque Control | WTGQ_A | Torque control model for Wind type 3
31: photovoltaic
31b: DC-coupled PV and battery (DC side charging only)
41: motor pump
| 42: energy storage - battery |  |  |  | DISTRIBUTED SOLAR PV MODELS | PVD1 | Distributed Photovoltaic system model, simplified
| 42s: DC-coupled PV and battery |  |  |  |  | DER_A | Distributed Energy Resource model, more detailed
43: energy storage - flywheel
44: energy storage - other
| 46: energy storage - compressed air |  |  |  | var device | static
| 47: energy storage - concentrated solar power |  |  |  |  | dynamic
51: hydrokinetic, axial flow turbine
52: hydrokinetic - wave buoy
| 53: hydrokinetic - other |  |  |  | WTG model | WT1G | Generator model for generic Type-1 wind turbines, one or two-cage induction generator
| 54: energy storage - reversible hydraulic turbine |  |  |  |  | WT2G | Generator model for generic Type-2 wind turbines, induction generator with external rotor resistance
Phase | 99: other
| Choose One |  |  |  | WTT model | WT1T | Wind turbine model for Type-1 wind turbines (conventional directly connected induction generator)
| Single Phase |  |  |  |  | WT2T | Wind turbine model for Type-2 wind turbines (directly connected induction generator wind turbines with an external rotor resistance)
Connection | Three Phase
| Choose One |  |  |  | WTE model | WT2E | Rotor resistance control model for wound-rotor induction wind-turbine generator WT2G
Delta
Grounded WYE
| Ungrounded WYE |  |  |  | WTP model | WT1P_B | Generic wind turbine pitch controller for WTGs of Type 1 and 2
Impedance Grounded
Grounding
[5 empty] | Winding Connection | Wye
| Choose One |  |  |  |  | Wye Grounded
| Solidly Grounded |  |  |  |  | Delta
| Grounded through Impedance |  |  |  |  | Delta (Burried)
Var Device | Ungrounded
| Choose One |  |  |  | Y/N | Yes
| Fixed Capacitor |  |  |  |  | No
Fixed Reactor
| SVD |  |  |  | Reactive Power Control Mode | Power Factor Control Mode
| SVC |  |  |  |  | Voltage Control Mode
| STATCOM |  |  |  |  | Reactive Power Control Mode
Excitation | Other (Explain Below) |  |  |  |  | Other
Choose One
Rotating DC commutator exciter with continuously acting regulator. The regulator power source is independent of the generator terminal voltage and current.
Rotating DC commentator exciter with continuously acting regulator. The regulator power source is bus fed from the generator terminal voltage.
Rotating DC commutator exciter with non-continuously acting regulator (i.e., regulator adjustments are made in discrete increments).
Rotating AC Alternator Exciter with non-controlled (diode) rectifiers. The regulator power source is independent of the generator terminal voltage and current (not bus-fed).
Rotating AC Alternator Exciter with controlled (thyristor) rectifiers. The regulator power source is fed from the exciter output voltage.
Rotating AC Alternator Exciter with controlled (thyristor) rectifiers.
Static Exciter with controlled (thyristor) rectifiers. The regulator power source is bus-fed from the generator terminal voltage.
Static Exciter with controlled (thyristor) rectifiers. The regulator power source is bus-fed from a combination of generator terminal voltage and current (compound-source controlled rectifiers system.
Other? (Specify):
GENERATOR MODELS |  | This model is still approved but should be transitioned to gentpj model after future testing.
Round rotor. This model is still approved but should be transitioned to gentpj model after future testing.
| GENTPF | modified gentpf with improved saturation modeling. The gentpj model should be used after future testing.
| GENROU | Cross compound generator. This model is still approved but should be transitioned to gentpj model after future testing.
GENTPJ
GENCC
Other (Explain Below)
EXCITATION SYSTEM MODELS |  | Brushless AC |  |  | submission requirement | Yes
|  | 2005 IEEE standard - updated AC1A with OEL/UEL inputs |  |  |  | No
| EXAC1 | exac1 with altered rate feedback source |  |  |  | Data on file
| ESAC1A | HIR Brushless
| EXAC1A | 2005 IEEE standard - updated AC2A |  |  | validation | Choose
| EXAC2 | GE Alterrex (rare) |  |  |  | Yes
| ESAC2A | 2005 IEEE standard - updated AC3A |  |  |  | No
| EXAC3A | Rotating AC with controlled rectifier (Althyrex) (rare) |  |  |  | N/A
| ESAC3A | 2005 IEEE standard - updated AC4A
| EXAC4 | Simplified brushless exciter |  |  | represent | Choose One
| ESAC4A | 2005 IEEE standard - updated AC6A |  |  |  | PTO
| ESAC5A | 2005 IEEE standard - new |  |  |  | GO
| ESAC6A | Brushless exciter with PID voltage regulator |  |  |  | CAISO
| ESAC7B | 2005 IEEE standard - updated AC8B |  |  | Active/Reactive Current Priority | Active (P) Current Priority
| EXAC8B | Static with ABB regulator |  |  |  | Reactive (Q) Current Priority
| ESAC8B | Rotating DC
| EXBBC | 2005 IEEE standard - updated DC1A |  |  | Single Phase Shell or Single Phase Core Form
| EXDC1 | Rotating DC with terminal fed pilot, alternate feedback |  |  | Three Phase Shell Form
| ESDC1A | Rotating DC with terminal fed pilot |  |  | Thee Phase 3-legged Core Form
| EXDC2 | 2005 IEEE standard - updated DC2A |  |  | Thee Phase 5-legged Core Form
| EXDC2A | Rotating, noncontinuous - minor differences between models
| ESDC2A | Rotating, noncontinuous
| EXDC4 | Rotating DC with PID
| ESDC3A | Static PI transformer fed excitation system
| ESDC4B | Static with double lead/lag
| EXELI | 2005 IEEE standard type ST1A
| EXST1 | SCPT - lead/lag block (Tc, Tb) added
| ESST1A | lead/lag block (Tc, Tb) is included to match the WECC FM
| EXST2 | 2005 IEEE Standard updated
| EXST2A | Modified IEEE ST3
| ESST2A | Use for GE Generex
| EXST3 | 2005 IEEE standard - updated ST3A
| EXST3A | GE EX2000 bus fed potential source, static compound and Generrex-PPS or -CPS, and SILCOmatic 5 excitation systems, with proportional plus integral (PI) voltage controller
| ESST3A | 2005 IEEE Standard - updated ST4B
| EXST4B | variation of ST1A
| ESST4B | variation of ST4B with field current limit
| ESST5B | static with limiters (Alstom)
| ESST6B | old type 1
| ESST7B | general purpose rotating exciter
| IEEET1 | use where negative field current may be a problem
Over-Excitation | REXS
| SCRX | over-excitation limiter
Under-Excitation | N/A
| OEL1 | under-excitation limiter
| N/A | under-excitation limiter
UEL1
UEL2
PSS model |  | Dual input PSS - Old WSCC model
Dual input PSS (delta P-omega)
| WSCCST | Single input PSS, dual lead lag
| PSS2A | pss2a + transient stabilizer
| IEEEST | Generic single input PSS
| PSSSB | Dual input PSS - Extra lead/lag (or rate) block added at end (up to 4 lead/lags total)
| PSS1A | Thyripol, Unitrol
| PSS2B | ABB multi-band
PSS3B
PSS4B
TURBINE/GOVERNOR MODELS |  | Double derivative hydro governor and turbine. (Represents WECC G2 governor plus turbine model.) Use hyg3 for new models
General governor model
| G2WSCC | PID governor and turbine. (Represents WECC GP governor plus turbine model.) Use hyg3 for new models
GGOV1
| GPWSCC | PID governor, double derivative governor and turbine. (Represents WECC GP governor, WECC G2 governor plus turbine model.)
| H6E | Hydro turbine and governor. Represents plants with straight-forward penstock configurations and electro-hydraulic governors that mimic the permanent/temporary droop characteristics of traditional dashpot-type hydraulic governors.
| HYG3 | Hydro turbine and governor. Represents plants with straight-forward penstock configurations and hydraulic governors of traditional 'dashpot' type.
| HYGOV | Fourth order lead-lag governor and hydro turbine.
| HYGOV4 | IEEE steam turbine/governor model (with deadband and nonlinear valve gain added)
| HYGOVR | IEEE hydro turbine/governor model. Represents plants with straightforward penstock configurations and hydraulic-dashpot governors.
| IEEEG1 | Turbine Load Controller model
| IEEEG3 | Hydro turbine and governor. Represents plants with straight forward penstock configurations and "three term" electro-hydraulic governors (i.e. Woodard electronic). Use hyg3 for new models
| LCFB1 | Basic steam turbine and governor
| PIDGOV | General governor model with GE gas turbine control features
TGOV1
GGOV3
ES source of charging | transmission grid
on-site generator only
other (please explain)
ES charging operation | Follow ISO dispatch instructions