## Cost Details
2025 DesertLink Generator Interconnection Unit Cost Guide |  |  |  | Voltages | 500 kV | Notes/Comments: DesertLink has no 115 kV, 138 kV, or 230 kV facilities on its system. These connections will be estimated on an as-needed basis
Revised as of: February 2025
Equipment Categories |  |  |  | Units
New Air Insulated Substation
|  | Complete 3-CB ring bus substation, equipped with one line position to terminate a single gen-tie and (2) outgoing lines. |  | lump sum | 27222 | Includes all necessary substation equipment, including operating buses, laid out as a three position ring bus (ultimately configurable as a breaker-and-a-half) to loop transmission line, substation control building, and associated protective relays. Includes base costs of ground grid and fencing. Does not include telecom, licensing, environmental mitigation, land acquisition, or site preparation.
New Gas Insulated Substation
|  | Complete breaker-and-a-half substation equipped with (3) line positions and (5) CBs |  | lump sum | * | Estimated as-needed
New Substation Equipment
Additional AIS positions to terminate gen-ties and transformer banks
|  |  | Single breaker (add third breaker to breaker-and-a-half) | per unit | 4350 | Addition of a position to existing site includes cost of related disconnect switches and protection equipment for the breaker position. Line protection and terminal equipment estimated separately. Site expansion not included and will be estimated on a lump sum basis if required.
|  |  | Breaker-and-a-half bay (2CB) | per set | 9350
|  |  | Breaker-and-a-half bay (3CB) | per set | 13100
Transformer banks
|  |  | 500/230 kV (4) single phase transformers | per set | 37466 | 500 MVA transformer (three single phase units with spare). Includes cost for bank protection on 500 kV and 230 kV. Assumes space is available in the substation. Does not include cost for breakers or disconnect switches.
Miscellaneous New Substation Equipment
|  | Reactive devices |  | lump sum | * | Estimated as-needed
|  | Phase shifting transformer |  | lump sum | *
|  | Protection equipment |  | lump sum | *
|  | IT/communications equipment |  | lump sum | *
|  | Metering equipment |  | lump sum | *
Replacement Substation Equipment
|  | Station equipment |  | lump sum | * | Estimated as-needed
New High Voltage Transmission Line
|  | Double circuit, strung on both sides, tubular steel pole |  | per mile | 5067.7 | Unit cost per mile shown is based on flat land/rural setting and considers no rocks, no crossings, minimal access and matting required, engineering and construction costs only. Environmental, permitting, and right of way acquisition costs are not included. Additional factors applied according to Factors & Assumptions tab.
|  | Double circuit capable, strung on one side, tubular steel pole |  | per mile | 4363.7
|  | Single circuit, tubular steel pole |  | per mile | 3022.95
|  | Double circuit, strung on both sides, lattice tower |  | per mile | 4607
|  | Double circuit capable, strung on one side, lattice tower |  | per mile | 3967
|  | Single circuit, lattice tower |  | per mile | 2879
Transmission Line Modifications
|  | Removal of existing transmission line |  | per mile | * | Estimated as-needed
|  | Reconductor/upgrade of existing transmission line |  | per mile | *
|  | Conductoring open position on existing structures |  | per mile | *
* Scope will be estimated on an as-needed basis using project-specific information and requirements

## Factors & Assumptions
Bulk Transmission Factors for use in developing cost estimates in Phase I Generator Interconnection Studies
As of February 2025
Simplified example on how to apply factors:
[8 empty] | $ millions | Apply Factor | Delta
| Hypothetical baseline cost per mile for double circuit 230 kV line (strung one side) using lattice towers: | [6 empty] | 2
Known characteristics of proposed transmission line ROW at Phase I study:
|  | Will be constructed in mountainous terrain | [5 empty] | 2 | 2.0 x 2.0 = 4 | 2
|  | Rural population density | [5 empty] | 1 | 2.0 x 1.0 = 2 | 0
|  | Line Length (short) | [5 empty] | 1.45 | 2.0 x 1.45 = 2.9 | 0.9
|  | High wind-prone area (but not icy) | [5 empty] | 1.35 | 2.0 x 1.35 = 2.7 | 0.7
|  |  | Summation of applied factors | [6 empty] | 3.6
|  |  | Baseline estimated cost per mile | [6 empty] | 2
|  |  | Estimated cost per mile including applied factors ($ million/mile) | [6 empty] | 7.2
|  | Factor Types: |  |  | Low Impact factors |  | Medium Impact factors | High Impact factors
|  |  | Terrain |  | flat |  | hilly | mountain |  | forest
|  |  | Population density |  | rural | desert | suburban | urban/metro
|  |  | Line length |  | Long (>10 miles) |  | Short (3 to 10 miles) | Tap (<3 miles)
|  |  | Weather study |  | 1/2" ice or 20# wind |  | 1" ice and 6# wind | > 2" ice and 6# wind
|  | Factor Amounts: |  |  | Low Impact factors |  | Medium Impact factors | High Impact factors
|  |  | Terrain |  | 1.0X to 1.2X |  | 1.2X to 1.4X | 1.4X to 2.0X
|  |  | Population density |  | 1.0X to 1.1X |  | 1.2X | 1.5X
|  |  | Line length |  | 1.0X |  | 1.45X | 1.75X
|  |  | Weather study |  | 1.0X to 1.2X |  | 1.25X | 1.5X
|  |  | Factor Type | Explanation of Factor issues and Factor multipliers
|  |  | Terrain | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
|  |  | Population density | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
|  |  | Line length | The length of transmission lines affects the per mile cost. Shorter lines will have higher unit cost due to mobilization/de-mobilization, lack of economy of scale, stringing operations, and other construction activities.
|  |  | Weather study | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure and foundations or an increased number of structures to reduce the span lengths.
Other assumptions underlying unit cost guide:
General labor: based on 5x10 work schedule.
Substation and transmission line costs exclude contingency. 20%-50% may be added based on project risks.
Unit costs exclude owner's representative fee for EPC construction and internal labor.
Unit costs include costs for material engineering, procurement, and installation.
Unit costs exclude allocated corporate overhead, including P&B, A&G, payroll tax, and AFUDC. These will be added to total cost estimates, if required.
Unit costs exclude generator's responsibility for Income Tax Component of Contribution (ITCC). These will be added to total cost estimates, if required.
Unit costs exclude licensing and permitting costs.
Unit costs exclude costs driven by site-specific characteristics including site grading and stormwater management, geotechnical conditions, contamination, environmental monitoring and mitigation, land costs, transmission line crossings, etc.
Unit cost are given without the benefit of any project-specific engineering. Unforeseen conflicts and/or scope may impact costs. A signed interconnection agreement is required before final design/engineering can start. Construction will not commence until all of the above conditions have been addressed.

## Escalation Rates & Factors
ESCALATION OVERVIEW:
Cost estimates are in 2025 constant dollars and then escalated over the years during which the project will be constructed, arriving at project costs in 2025 constant dollars escalated to OD year.
DEFINITIONS:
Project cost in 2025 constant dollars represents the cost of the project if all costs were paid for in 2025.
Project cost escalated to OD year represents the cost of the project if all costs were paid for in the OD year.
Mathematical formula: constant dollars escalated to OD year | [5 empty] | = Cost in Constant Dollars + Escalation to OD Year
= Cost in Constant Dollars x Escalation Factor
Proposed Escalation Rate - Effective 1/1/2025
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Escalation Rate | 0% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%
Escalation Factors | 1 | 1.025 | 1.0506 | 1.0769 | 1.1038 | 1.1314 | 1.1597 | 1.1887 | 1.2184 | 1.2489 | 1.2801
2025-2034 | Escalation Rates assumed to be 2.5% annually.