## PGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service July 2022 TDF | Expected In-Service Oct TDF 2022 | Expected In-Service January TDF 2023 | Expected In-Service April TDF 2023 | Agregate MW in Queue with Executed LGIA | Notes
21rsmt-4 | Monta Vista 115 kV circuit breaker 1322 overstress | Replace Monta Vista 115 kV circuit breaker 1322 | PG&E | RA-21 | Reliability | SCD overstress | In-Service | 2021 | 2021-10-01 |  | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 1200 | In-Service
20rsmt-7a | Tesla 500 kV circuit breaker 632 overstress | Replace Tesla 500 kV circuit breaker 632 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Service | 2021 | 2021-12-03 |  | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 850 | In-Service
C13P2-GGR01 | Tesla 500 kV circuit breakers 622 overstress | Replace Tesla 500 kV circuit breaker 622 with 63 kA interrupting capability. Only went to 50 kA | PG&E | C13 | Reliability | SCD overstress | In-Service | 2021 | [7 empty] | 2021-12-20 | 400 | In-Service
C12P2-GRNU3 | Midway Substation 500 kV CB 712 overstress | Replace Midway Substation 500 kV CB 712 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Service | 2021 | 2022-12-31 |  | 2025-12-31 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 1800 | In-Service
C9P2-N09 | Re-conductor Stockton A-Weber #3 60 kV Line (Stockton A-Hazelton Jct) | Re-conductor 0.9 mi of Stockton A-Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC. | PG&E | C9 | Deliverability | Re-conductor | In-Service | 2018 | 2022-01-14 |  | 2022-03-31 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 25 | In-Service
C12P1-NPN02 | Lodi Substation 60 kV circuit breakers 12 and 22 overstress | (blank) | PG&E | C12 | Reliability | SCD overstress | In-Service | 2011 | 2020-08-04 |  | 2022-03-28 | 2022-12-29 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 0 | In-Service
20rsmt-3 | Midway 230 kV Bus Section E overload mitigation | Replace limiting conductor and/or fittings on Bus Section E to achieve 3372 A min. rating | PG&E | RA-20 | Reliability | Bus Flow | In-Service | 2021 |  |  | 2022-09-30 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 409.7 | In-Service
C11P2-FP01 | Midway 500 kV circuit breakers 732, 802, 832 and 842 overstress | Replace Midway 500 kV circuit breakers 732, 802, 832 and 842 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Service | 2021 | 2022-12-31 |  | 2022-09-30 | 2025-12-31 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2100.1 | In-Service
22rsmt-3 | Metcalf 230 kV Substation Circuit Breaker #No 292 Upgrade | Upgrade Metcalf Circuit Breaker #292 due to overstress issues | PG&E | (blank) | Capacity | (blank) | In-Service | 2022 |  |  |  | 2025-01-01 | 2025-12-01 | 2022-09-27 | 2022-09-27 | 2022-09-27 | 1395 | In-Service
C11P2-FC01 | Midway 500kV CB's 722 Overstress | Midway Sub: Replace 500kV CB's 722, SW's and Relays | PG&E | C11 | Reliability | SCD overstress | In-Service | 2021 | 2022-09-30 |  | 2025-12-31 | 2025-12-31 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2100.1 | In-Service
C12P2-KC01 | Midway Substation 500kV CB 722 Overload mitigation | Replace Midway 500 kV CB 722 to achieve 3600 A emergency rating | PG&E | C12 | Reliability | Bus Flow | In-Service | 2021 | 2022-12-31 |  | 2025-12-31 | 2025-12-31 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 3231.05 | In-Service
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | PG&E | C13 | Reliability | SCD overstress | In-Service | 2018 | 2022-10-10 |  | 2025-05-31 | 2022-09-28 | 2022-12-01 | 2022-12-07 | 2022-11-01 | 2022-11-01 | 2195 | In-Service
C8P2-6 | Re-conductor Los Banos-Q779 SS #1 230 kV Line | Re-conductor 4.5 mi Los Banos-Padre Flat SS #1 230 kV Line with 1113 ACSS and upgrade equipment to 1900 A. | PG&E | C8 | Deliverability | Re-conductor | In-Service | 2017 | 2022-10-24 |  | 2023-03-01 | 2023-02-28 | 2023-02-28 | 2022-12-14 | 2022-12-24 | 2022-12-24 | 632 | In-Service
19rsmt-3 | Schindler 70kV Bus Normal & Outage Overload | Upgrade Schindler 70 kV Bus to 1113 kcmil AAC | PG&E | RA-19 | Reliability | Bus Flow | Not Triggered | [9 empty] | 0 | Not triggered
C13P1-GPN06 | Birds Landing 230 kV CBs 422, 222, 412, 212 Overload Mitigation | Upgrade Birds Landing Sw Sta 230 kV bays 1 and 2 to 3000 A equipment and replacing 6 circuit breakers and associated switches/relays | PG&E | C13 | (blank) | (blank) | Removed | [9 empty] | 0 | Removed
C13P1-KPN02 | Midway Substation 230 kV bus and 27 circuit breakers overstress | Install 2 x 16 ohm series bus reactors between Midway Substation 230 kV bus sections D and E (16 ohm parallel / 8 ohm net) | PG&E | C13 | Reliability | SCD overstress | Not Triggered | [9 empty] | 0 | Not triggered
C13P2-FPT04 | Jackson Switching Station (CHSR Site 10) | (blank) | PG&E | C13 | (blank) | (blank) | Removed | [9 empty] | 0 | Removed
C13P2-FPT05 | CHSR Site 8 | (blank) | PG&E | C13 | (blank) | (blank) | Removed | [9 empty] | 0 | Removed
C9P2-F17 | Panoche 115 kV circuit breakers 152 overstress | Replace Panoche 115 kV circuit breaker 152 and associated switches/relays | PG&E | C9 | Reliability | SCD overstress | Removed | [9 empty] | 0 | Removed
C8P1-35 | Re-conductor Los Banos-Quinto SS 230 kV Line | Re-conductor 6.11 mi Quinto Sw Sta-Los Banos 230 kV Line with super bundled 795 ACSS | PG&E | C8 | Deliverability | Re-conductor | In-Flight | 2017 | 2022-03-03 |  | 2022-05-31 | 2023-05-16 | 2023-05-16 | 2023-05-16 | 2023-04-28 | 2023-05-10 | 1110.62 | Q2-2023: Tline crews were delayed in Q1 2023 due to storm response. Crews have returned back to complete work through clearance extensions.
C12P2-PNU-02 | Gates 230 kV circuit breakers 352, 362 and 372 overstress mitigation (Cap Banks) | Replace Gates 230 kV circuit breakers 352, 362 and 372 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2022 | 2022-10-24 |  | 2023-04-30 | 2023-03-31 | 2023-03-31 | 2023-04-06 | 2023-04-06 | 2023-05-23 | 2992.67 | Q2-2023: In construction. Tracking to End of May In-service. Clearances and work directly tied to work under C9P2-F13-F15 Gates 230kV Bus Section E and CB 312, 322, 2102, 2202 overload mitigation (BAAH). Most significant risk to schedule lies with testing the cap banks. If they fail to pass intital testing and have to be tested again, the scheduled In-service could be delayed
C9P2-F13-F15 | Gates 230kV Bus Section E and CB 312, 322, 2102, 2202 overload mitigation (BAAH) | Gates Substation 230 kV circuit breakers 312, 322, 2102, 2202 overload – convert bus section E to BAAH and move Panoche-Gates #1 and #2 230 kV lines and Q1117/Q1120/Q1139/Q1242/Q1243 into bus section E | PG&E | C9 | Reliability | Bus Flow | In-Flight | 2019 | 2021-08-06 |  | 2023-03-31 | 2023-03-14 | 2023-05-31 | 2023-03-14 | 2023-05-23 | 2023-05-31 | 1993.95 | Q2-2023: In construction. Tracking to End of May In-service. Clearances and work directly tied to work under C12P2-PNU-02 Gates 230 kV circuit breakers 352, 362 and 372 overstress mitigation (Cap Banks)
C8P2-3 | QC8RAS-08 RAS (Deliverability Triggered RNU) | QC8RAS-08 RAS to trip Generation offline for outage AND overload of either Gates 500/230 kV Transformer Bank 11 or 12 | PG&E | C8 | Deliverability | RAS (Deliverability) | In-Flight | 2017 |  |  | 2023-01-12 | 2023-01-12 | 2023-12-31 | 2024-05-03 | 2024-05-03 | 2024-05-03 | 2870.57 | Q2-2023: PG&E protection informed the Gates BAAH team that this RAS is not impactful to interconnection projects until all elements are in place in 2024. Schedule sequencing to align with STATCOM project Bank 12 relay rack relocations. Impacts only deliverability.
C8P1-34 | Re-conductor Padre Flat SS-Panoche #1 230 kV Line | Re-conductor 32.59 mi Q779/Padre Flat SS-Panoche #1 230 kV Line with 795 ACSS | PG&E | C8 | Deliverability | Re-conductor | In-Flight | 2017 | 2023-09-21 | 2023-02-10 | 2024-05-31 | 2024-05-21 | 2024-05-20 | 2024-05-20 | 2024-05-10 | 2024-05-10 | 600 | Q2-2023: The reconductor project requires negotiation and settlements for property easement revisions and somenegotiations are ongoing. A group of property owners have been unreachable and others have informed PG&E they are unwilling to sign offer letters. PG&E cannot move ahead into construction until rig hts are perfected. Unless these rights are resolved by June 2023, it is possible the project schedule will slip a year to allow for PG&E to pursure legal action. Due to common property owners, negotiation effort are bundled with C9P1-F11
C8P2-15 | Cottonwood Substation 230 kV Circuit Breaker 522 and 542 Overstress | Cottonwood Substation 230 kV CB Overstress: Replace CB 522 & 542 (rated @ 34.5KA, overstress close-in fault is 35,179A or 2%, 679A). | PG&E | C8 | Reliability | SCD overstress | In-Flight | 2018 | 2023-08-29 |  | 2023-07-28 | 2023-08-15 | 2023-08-15 | 2024-09-30 | 2024-09-30 | 2024-09-04 | 700 | Q2-2023: Civil Const Start planned Aug 2023. Triggering project has suspended. however one other active interconnection project requires this upgrade.
20rsmt-7b | Tesla 500 kV circuit breakers 542 and 642 overstress | Replace Tesla 500 kV circuit breakers 542 and 642 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 2024-03-29 |  | 2024-07-31 | 2023-09-20 | 2024-04-12 | 2024-07-05 | 2024-07-12 | 2024-09-24 | 2680 | Q2-2023: Issue for construction due April 2023, Release to construction due July 2023, Construction start scheduled for March 2024. On track for planned In-service date
C12P1-NPT03 | Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 overstress | Replace Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2020 | 2021-06-01 |  | 2024-12-31 | 2024-12-31 | 2023-11-10 | 2024-05-01 | 2024-12-31 | 2024-09-30 | 49.9 | Q2-2023: In construction. A recent interconnection project has triggered this for Generation.
20rsmt-5 | Tesla 500 kV circuit breaker 612 overstress | Replace Tesla Substation 500 kV CB 612 and associated switches/relays | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 2024-08-22 |  | 2024-03-01 | 2024-05-28 | 2024-07-05 | 2024-08-08 | 2024-08-15 | 2024-10-28 | 850 | Q2-2023: Issue for construction due April 2023, Release to construction due July 2023, Construction start scheduled for August 2024. On track for planned In-service date
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 1) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2021-07-09 |  | 2026-02-28 | 2023-02-01 | 2023-04-11 | 2024-11-12 | 2024-11-12 | 2024-11-12 | 200 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
20rsmt-6 | 20RSMTRAS-02 (Reliability) to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | 20RSMTRAS-02 RAS to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | PG&E | RA-20 | Reliability | RAS (Reliability) | In-Flight | 2020 | 2024-05-21 |  | 2023-12-31 | 2023-12-29 | 2023-12-29 | 2023-10-31 | 2023-12-31 | 2024-11-14 | 100 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024. Interconnection project has triggered an interim solution which mitigates the need for this RAS to go in-service. This project only impacts deliverability to the connecting project.
C12P1-NPT01 | Gold Hill Substation 115 kV circuit breakers 142 and 172 overstress | Replace Gold Hill Substation 115 kV circuit breakers 142 and 172 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2021 | 2024-03-05 |  | 2023-09-30 | 2024-01-04 | 2023-11-13 | 2025-07-02 | 2025-08-28 | 2025-01-28 | 49.9 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
C11P2-ND03 | North Dublin-Cayetano 230 kV Line | Reconductor North Dublin-Cayetano 230 kV Line 2.63 miles OH Line & 2.82 UG cable with new UG cable 797 MVA/2000 A | PG&E | C11 | Deliverability | Re-conductor | In-Flight | 2021 | 2024-09-18 | 2023-08-18 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-03-25 | 2025-03-25 | 2025-02-10 | 90.8 | Q2-2023: T-line design underway of Above and Unground components. Nearing 60% design complete. Substation design working toward 305 package. CPUC permitting, Environmental, Biological, and Cultural requirements being evaluated. Existing row of way land rights require evaluation if perfecting is required before releasing to construction. Perfecting land rights if required would push out the expected schedule.
C11P2-NR01 | Cottonwood Substation 230 kV circuit breakers 232, 242 overstress | Replace Cottonwood Substation 230 kV circuit breakers 232, 242 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Flight | 2022 | 2024-08-19 |  | 2024-02-28 | 2024-04-02 | 2024-05-24 | 2025-08-28 | 2025-08-28 | 2025-03-07 | 500 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
C12P2-GRNU2 | Gates Substation 230 kV Bus Overstress | Install series bus reactors between Gates Substation 230 kV bus sections E and F | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2022 | 2024-01-31 |  | 2025-12-01 | 2025-12-01 | 2025-12-31 | 2025-03-31 | 2025-03-31 | 2025-03-31 | 2300 | Q2-2023: Issue for construction due Q2 2023. Expected construction to start in January 2024.
C13P1-KPN02 | Convert Midway Substation 230 kV to BAAH | Convert Midway Substation 230 kV to BAAH in order to install bus reactors & RAS | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2016 |  |  | 2024-08-08: 2025-04-25; 2024-08-15: 2025-04-25; 2024-10-28: 2025-04-25 | 0 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
C9P1-F11 | Re-conductor Dos Amigos PP-Panoche #3 230 kV Line | Re-conductor 23.63 mi Dos Amigos PP-Panoche #3 230 kV Line with 795 ACSS | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2017 | 2024-09-17 |  | 2025-05-14 | 2025-04-30 | 2025-04-30 | 2025-04-30 | 2025-04-30 | 2025-04-30 | 632 | Q2-2023: The reconductor project requires negotiation and settlements for property easement revisions and some negotiations are ongoing. A group of property owners have been unreachable and others have informed PG&E they are unwilling to sign offer letters. PG&E cannot move ahead into construction until rights are perfected. Unless these rights are resolved by June 2023, it is possible the project schedule will slip a year to allow for PG&E to pursure legal action. Due to common property owners, negotiation effort are bundled with C8P1-34
C11P2-NP01 | Contra Costa 230kV SW's 601, 603 overload | Contra Costa PP: Replace 230kV SW's 601 & 603 and jumpers. | PG&E | C11 | Reliability | Bus Flow | In-Flight | 2021 | 2024-12-09 |  | 2025-12-31 | 2025-12-31 | 2025-07-07 | 2025-05-02 | 2025-05-30 | 2025-05-23 | 0 | See C11P2-NP02, C11P2-NP01 Line Reconfiguration notes
C11P2-NP02 | Contra Costa 230kV Bus Sections D, E and F and circuit breaker 820 overload | Contra Costa PP: Reconductor Bus Sections D, E and F. Replace circuit breaker 820. | PG&E | C11 | Reliability | Bus Flow | In-Flight | 2021 | 2024-12-09 |  | 2025-12-31 | 2025-12-31 | 2025-07-07 | 2025-05-02 | 2025-05-30 | 2025-05-23 | 490.8 | See C11P2-NP02, C11P2-NP01 Line Reconfiguration notes
C12P1-NPT04 | Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 overstress | Replace Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | Initiating | 2021 | 2024-03-18 |  | 2024-03-31 | 2024-06-27 | 2024-12-02 | 2025-03-06 | 2025-05-20 | 2025-08-14 | 1840.8 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 2 - incl CB282) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2025-05-01 |  | 2026-02-28 | 2023-12-05 | 2023-12-05 | 2025-12-05 | 2025-12-05 | 2025-12-05 | 200 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
21rsmt-SCD-23 | El Cerrito G 115kV CB 112, 142, 132 Overstress | Replace Overstressed Circuit Breakers | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2011 | 2024-02-14 |  |  | 2024-07-18 | 2024-07-17 | 2025-11-14 | 2025-12-26 | 2025-12-26 | 0 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024. it has been removed by reassessment.
(blank) | Tesla MPAC | New 230kV MPAC building relocates 230kV equipment from existing Control Building | PG&E | n/a | Reliability | MPAC | In-Flight | 2018 | 2025-03-27 |  |  | n/a | n/a | 2024-10-09 | 2025-12-31 | 2025-12-31 | 0 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024. Impacted Interconnections to be planned to be installed in the existing control building.
C9P1-F12 | Re-conductor Borden-Gregg #2 230 kV Line | Re-conductor 6.25 mi Borden-Gregg #2 230 kV Line with 1113 ACSS | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2017 | 2025-08-08 | 2023-10-13 | 2025-05-31 | 2025-05-07 | 2025-05-07 | 2025-05-07 | 2025-05-07 | 2026-01-16 | 632 | Q2-2023: Ongoing alternate route coordination with property owners to mitigate schedule, land, and environmental impacts reulting in schedule delays.
20rsmt-4 | Metcalf 115kV breakers Overstress (almost all breakers) | Install 4-3 ohm reactors at low side of Metcalf 115 kV 230kV Transformers | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 2025-05-02 |  | 2025-02-28 | 2025-08-22 | 2025-09-03 | 2025-11-04 | 2026-01-29 | 2026-02-05 | 1145 | Q2-2023: Scope approved. Release to construction planned in Q3-2023. This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024. An interim solution has mitigated the breaker overstress thus the interconnecting projects are not impacted by this upgrade.
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 overstress | Replace Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2018 | 2024-10-22 |  | 2025-05-31 | 2025-05-29 | 2025-05-21 | 2026-02-17 | 2025-05-13 | 2026-02-26 | 2195 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024. An interim solution has mitigated the breaker overstress thus the interconnecting projects are not impacted by this upgrade.
C12P1-GPT01 | Ames Distribution 115 kV circuit breaker 132 overstress | Replace Ames Distribution 115 kV circuit breaker 132 | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2019 | 2025-12-24 |  | 2024-03-31 | 2024-06-14 | 2024-08-22 | 2026-03-10 | 2026-03-10 | 2026-03-10 | 450 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
C8P2-1 | Re-conductor Borden-Gregg #1 230 kV Line | Re-conductor 6.25 mi Borden-Gregg #1 230 kV Line with 1113 ACSS and upgrade equipment to 2000 A minimum (this is the existing Borden-Gregg 230 kV Line) | PG&E | C8 | Deliverability | Re-conductor | In-Flight | 2017 | 2026-01-30 | 2023-10-13 | 2026-01-05 | 2026-01-05 | 2026-01-05 | 2026-01-05 | 2026-01-05 | 2026-05-07 | 632 | Q2-2023: Ongoing alternate route coordination with property owners to mitigate schedule, land, and environmental impacts reulting in schedule delays.
C11P2-ND01 | Re-conductor Fulton-Hopland 60 kV Line (Fitch Mountain Tap-Geysers Jct) | Re-conductor Fulton-Hopland 60 kV Line (Fitch Mountain Tap 009/005A-Geysers Jct 016/004) ~7 mi total length with 715 AAC | PG&E | C11 | Deliverability | Re-conductor | In-Flight | 2018 | 2025-12-15 | 2024-11-01 | 2026-03-31 | 2027-12-31 | 2027-12-31 | 2025-11-03 | 2026-02-13 | 2026-05-25 | 230 | Q2-2023: Scope has increased from a reconductor to include poles and line replacement. A Complete rebuild is planned. Many factors are to be evaluated in 2023 to determine the permitting and environmental impacts.
C9P2-N02 | Re-conductor Fulton-Hopland 60 kV Line (Geysers Jct-Cloverdale Jct-Hopland) | Re-conductor 24.21 mi Fulton-Hopland 60 kV Line (Geysers Jct 016/003A-Cloverdale Jct 026/002-Hopland) with 715 AAC and upgrade any limiting equipment | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2019 | 2025-12-15 | 2024-11-01 | 2027-05-31 | 2027-03-31 | 2027-12-31 | 2025-11-03 | 2026-02-13 | 2026-05-25 | 230 | Q2-2023: Scope has increased from a reconductor to include poles and line replacement. A Complete rebuild is planned. Many factors are to be evaluated in 2023 to determine the permitting and environmental impacts.
21rsmt-1 | Henrietta Substation 70kV CBs 12 and 72 Overstress | Henrietta Sub: Replace 70kV CB 12 & 72 and switches. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2025-07-14 |  | 2025-12-31 | 2026-06-16 | 2025-02-26 | 2026-09-14 | 2026-10-07 | 2026-10-07 | 0 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 3 - incl CB262) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2026-01-01 |  | 2026-02-28 | 2024-10-16 | 2024-10-16 | 2026-12-07 | 2026-12-07 | 2026-12-07 | 200 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
(blank) | Morro Bay MPAC | New 230kV MPAC building relocates 230kV equipment from existing Control Building | PG&E | n/a | Reliability | MPAC | In-Flight | 2014 | 2026-01-05 |  |  | n/a | n/a | 2027-03-09 | 2027-05-06 | 2027-05-06 | 0 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
21rsmt-5 | Palo Alto 115 kV circuit breakers 412 and 442 overstress | Replace Palo Alto 115 kV circuit breakers 412 and 442 with 63 kA interrupting capability | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2026-10-21 |  | 2024-09-30 | 2025-03-27 | 2026-06-10 | 2027-11-08 | 2027-11-08 | 2027-11-08 | 250 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 4 - incl CB182) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2027-02-02 |  | 2026-02-28 | 2025-12-09 | 2025-12-09 | 2027-12-13 | 2027-12-13 | 2027-12-13 | 200 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024.
C12P2-LDNU1 | Ripon-Manteca 115 kV Line Reconductor | Reconductor Ripon-Manteca 115 kV line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total) | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2028-06-26 | 2024-12-04 | 2027-12-31 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2028-09-11 | 99 | Q2-2023: Scope has increased from a reconductor to include structure and line replacement. A Complete rebuild using 715 AAC conductor is planned. An NOC is expected however space limitations exist to construct replacement structures. If alternatives are required, it could change the permitting situation. A shoofly is being considered to mitigate the need for a higher permit. Many factors are to be evaluated in 2023 to determine the permitting and environmental impacts.
C12P2-LDNU2 | Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line Reconductor | Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV line 25.23 miles section of various conductors from 018/115-043/277 | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2028-06-26 | 2024-12-04 | 2027-12-31 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2028-09-11 | 99 | Q2-2023: Scope has increased from a reconductor to include structure and line replacement. Half of this line is already known to require only an NOC under a complete rebuild with like for like structures. Permitting requirements for the remaining 12 miles are in development. Many factors are to be evaluated in 2023 to determine the permitting and environmental impacts.
C12P2-LDNU3 | Bellota-Riverbank-Melones Sw Sta 115 kV Line 115 kV Line Reconductor | Reconductor a total of 17 miles of Bellota-Riverbank-Melones SW STA 115 kV Line with 477 ACSS | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2028-06-26 | 2024-12-04 | 2027-12-31 | 2027-12-16 | 2027-12-31 | 2027-12-31 | 2027-12-31 | 2028-09-11 | 99 | Q2-2023: Scope has increased from a reconductor to include structure and line replacement. Presently the team is proceeding with a 477 ACSS conductor and evaluating a bundled conductor option to provide more capacity which would NOT trigger TSP structures and a higher permit. Moving forward with this option could allow like for like structure replacements and help reduce permitting and environmental impacts. PG&E expects a determination on this approach by middle of April. Many factors are to be evaluated in 2023 to determine the permitting and environmental impacts.
C12P2-LDNU4 | Stanislaus-Melones SW STA-Riverbank Jct Sw Sta 115 kV Line Reconductor | Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/043 | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2028-06-26 | 2024-12-04 | 2027-12-31 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2028-09-11 | 99 | Q2-2023: Scope has increased from a reconductor to include structure and line replacement. A complete rebuild using 715 AAC conductor is planned. Team expects an NOC however many factors are to be evaluated in 2023 to determine the permitting and environmental impacts.
C12P1-GCR01 | Moraga 115 kV circuit breakers 582, 612, 622, 642 and 712 overstress | Replace Moraga 115 kV circuit breakers 582, 612, 622, 642 and 712 | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2022 | 2028-08-01 |  | 2026-10-01 | 2027-01-01 | 2028-11-23 | 2029-10-10 | 2028-11-23 | 2028-11-23 | 220 | Q2-2023: This project has been delayed due to 2023 funding limitations. Work is planned to resume in 2024. A triggering Interconnection project has signed requiring this project however that project has gone into suspension.
C8P2-10 | QC8RAS-02 SPS (Deliverability Triggered RNU) | QC8SPS-02 SPS to modify the existing Hatchet Ridge SPS to trip Q1106 200 MW wind and Hatchet Ridge 102 MW wind for thermal overloads on the Q1106 SS-Cottonwood, Carberry SS-Round Mountain or Pit #3-Carberry SS 230 kV Lines. | PG&E | C8 | Deliverability | RAS (Deliverability) | Deferred | 2017 | 2028-05-23 |  | 2023-07-28 | 2023-07-28 | 2023-07-28 | TBD | 2027-03-31 | 2028-12-07 | 200 | Q2-2023: In-service date shown aligns with overall new Switching Station construction. Triggering Interconnection Project has suspended for 1-year
22rsmt-4 | New 230 kV switching station to loop Dos Amigos – Panoche # 3 230 kV | Build a new 2 bay 230 kV BAAH switching station to loop in the Dos Amigos – Panoche # 3 230 kV Line requiring access road, land and land rights acquisition and permitting, remote end protection upgrades, and OPGW/fiber telecommunication work | PG&E | RA-22 | Deliverability | New Station | Initiating |  |  |  |  | n/a | n/a | 2028-12-31 | 2028-12-31 | 2028-12-31 | 632 | Q2-2023: This project has been delayed due to 2023 funding limitations. Project initating activites in development. Work is estimated to kickoff in 2024.

## SCE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected July 2022 TDF | Expected In-Service Oct TDF 2022 | Expected In-Service January TDF 2023 | Expected In-Service April TDF 2023 | Agregate MW in Queue with Executed LGIA | Notes
SCE-2021RA-E-R6 | West of Colorado River CRAS Palo Verde Extension | Include Palo Verde sub in WOCR CRAS | SCE | 2021 Reassessment | RNU | RAS/CRAS | Cancelled | N/A | N/A | 43800 | 2023-12-01 | Dec-23 | 2023-12-01 | 2023-12-01 | N/A | N/A |  | Trigger Year based on Upgrade Facility Agreement.
PIN8449 | Whirlwind 230 kV Circuit Breaker Upgrade | ATRA: Install 2 TRV to upgrade breaker rating | SCE | ATRA 2021 | SCE | SCD Over Stress | Cancelled | N/A | N/A | 44531 | 2023-12-01 | New | 2023-12-01 | 2023-12-01 | N/A |  |  | Project cancelled due to circuit breaker re-rate
PIN8450 | Vista 230 kV Circuit Breaker Upgrade | ATRA: Upgrade one 230 kV circuit breaker | SCE | ATRA 2021 | SCE | SCD Over Stress | Cancelled | N/A | N/A | 44531 | 45261 | New | 45261 | 45261 | N/A |  |  | Project cancelled due to circuit breaker re-rate
PIN8454 | Antelope 230 kV Circuit Breaker Upgrade | ATRA: Replace 2 Circuit breakers | SCE | ATRA 2021 | SCE | SCD Over Stress | Cancelled | N/A | N/A | 44531 | 2023-12-01 | New | 2023-12-01 | 2023-12-01 | N/A |  |  | Project cancelled due to circuit breaker re-rate
PIN8455 | Vincent 500 kV Circuit Breaker Upgrade | ATRA: Upgrade 3 500 kV CB, and install 4 TRV Capacitor to increase breaker rating | SCE | ATRA 2021 | SCE | SCD Over Stress | Cancelled | N/A | N/A | 44531 | 2023-12-01 | New | 2023-12-01 | 2023-12-01 | N/A |  |  | Project cancelled due to circuit breaker re-rate
SCE-C11P2-NOL-R3 | Upgrade Roadway 115kV Operating/Transfer Bus | Upgrade Roadway 115 kV Operating/Transfer Bus with 1590 kcmil ACSR conductor or equivalent. | SCE | C11 Phase II | GRNU | Substation Expansion | In-service Jun-22 | 44652 | N/A | 44136 | 2022-10-01 | 2022-06-01 | 2022-06-01 | In-service Jun-22 | In-service Jun-22 |  |  | Trigger Year based on GIA date.
SCE-C3C4P2-E-D1 | Red Bluff 2AA | Install Red Bluff 500/230kV bank No. 2 | SCE | C3&4 Phase II | DNU | Capacity Increase | In-service May-22 | 44228 | N/A | 41913 | 2021-10-01 | 2022-05-31 | 2022-05-01 | In-service May-22 | In-service May-22 |  |  | Trigger Year based on GIA date.
SCE-C8P2-E-CR-M | West of Colorado River CRAS -Include monitoring infrastructure relays to monitor the Red Bluff 2nd AA bank | West of Colorado River CRAS -Include monitoring infrastructure relays to monitor the Red Bluff 2nd AA bank | SCE | C8 Phase II | RNU | RAS/CRAS | In-service May-22 | 44256 | N/A | 43435 | 2021-08-01 | 2022-05-31 | 2022-05-01 | In-service May-22 | In-service May-22 |  |  | Project need was postponed from original ISD due to delays from projects in the triggering queue. Trigger Year based on GIA date.
SCE-TCP2-E-R1 | Colorado River Substation Expansion - Reliability | Expand Colorado River substation and install Colorado River 1AA bank | SCE | TC Phase II | RNU | Capacity Increase | In-service Nov-21 | N/A | N/A | 40513 | N/A | In-service Nov-21 | In-service Nov-21 | In-service Nov-21 | In-service Nov-21 |  |  | Trigger Year based on GIA date.
SCE-TCP2-E-R5 | Colorado River Corridor RAS - CR Transformers | Develop a SPS to trip 500 MW TC2 generation at the Colorado River 500/220 kV Substation to mitigate the overload by on one AA bank for the loss of another AA bank (T‐1 contingency) | SCE | TC Phase II | RNU | RAS/CRAS | In-service May-22 | 44317 | N/A | 43101 | 2021-12-01 | 2022-03-01 | 2022-04-01 | In-service May-22 | In-service May-22 |  |  | Trigger Year based on GIA date.
SCE-C3C4P2-SCD | Vincent CB Upgrades | Upgrade Vincent 500kV CBs | SCE | C3&4 Phase II | RNU | SCD Over Stress | Cancelled | N/A | N/A | N/A | N/A | 2024-06-01 | [5 empty] | Project replaced by new project PIN8455 identified via ATRA
SCE-C8P2-POS-C11 | 220 kV line position at Colorado River Substation. | 220 kV line position at Colorado River Substation | SCE | C11 Phase II | CANU-IR | N/A | N/A | N/A | N/A | N/A | N/A | 2022-08-31 | [5 empty] | Recommending removal of project as not applicable to the TDF scope
SCE-PreC12-SCD-Vincent-C12 | Vincent 500kV SCD (Install seven (7) sets of 500 kV TRV) |  | SCE | C12 Phase II | CANU-GR | SCD Over Stress | Cancelled | N/A | N/A | N/A | N/A | 2024-06-01 | [5 empty] | Project replaced by new project PIN8455 identified via ATRA
SCE-C9C10-N | Windhub AA Bank cRAS - monitoring infrastructure | Windhub AA Bank cRAS - monitoring infrastructure | SCE | 2021 Reassessment | GRNU | RAS/CRAS | Construction | 44713 | N/A | 44409 | 44866 | 44958 | 44958 | 44958 | 44986 | 45046 | 1800 | Trigger Year based on 2021 Reassessment
SCE-C9P2-N-R1 | Whirlwind AA Bank CRAS Monitoring Infrastructure | Implement Whirlwind AA Bank CRAS - monitoring infrastructure | SCE | 2018 Reassessment | GRNU | RAS/CRAS | Design | 45047 | N/A | 44013 | 44866 | 44958 | 44958 | 44958 | 45078 | 45078 | 1014.87 | Trigger Year based on 2020 Reassessment.
SCE-C11P2-N-L1 | Pardee – Pastoria- Warne 220 kV T/L rating increase | Upgrade terminal equipment and fix ground clearance for Pardee – Pastoria- Warne 230kV line | SCE | C11 Phase II | LDNU | Capacity Increase | Design | 45033 | N/A | 44013 | 44849 | 45170 | 45078 | 45078 | 45383 | 45078 | 109.7285 | Revised ISD due to delays in triggering project. Apr-24 date provided in Jan2023 TDF was for more work than what is described.
SCE-C10P2-E-R3 | West of Colorado River CRAS Inland/Devers Extension - monitoring infrastructure | Infrastructure to convert the formally referred to as the New Devers RAS and the Inland RAS to centralized RAS platform | SCE | C10 Phase II | RNU | RAS/CRAS | Construction | 44197 | N/A | 43435 | 44470 | Aug-25 | 44986 | 44986 | 45078 | 45192 | 3688 | Trigger Year based on GIA date. Revised ISD due to CRAS resources and outage constraints. Combining CRAS testing with other projects that are completed later than expected
SCE-TCP2-EOP-R4 | Lugo - Victorville RAS | Trip generation for Eldorado area 500kV line outages. | SCE | TC Phase II | RNU | RAS/CRAS | Permitting | 45069 | N/A | 40787 | 44166 | 45047 | 45047 | 45047 | 45261 | 45261 | 530 | Trigger Year based on GIA. Additional working areas caused SCE to refile application
SCE-C12P2-N-R2 | Tehachapi CRAS: monitoring infrastructure addition | Add N-1 to RAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | 45597 | N/A | 44228 | 2024-09-01 | 2024-09-01 | 2024-09-01 | 2024-09-01 | 2025-04-01 | 2025-04-01 | 2000 | Trigger year based on GIA. Schedule adjusted to meet earliest generation in-service date
SCE-C11P2-EOP-R1 | Lugo - Victorville CRAS - monitoring infrastructure | Infrastructure to convert the Lugo - Victorville RAS to centralized RAS platform | SCE | C11 Phase II | GRNU | RAS/CRAS | Design | 45473 | N/A | 43770 | 2024-06-01 | Jun-25 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 550 | Trigger Year based on the date of the QC11 Phase 2 report.
SCE-C72021-EOP | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | SCE | 2021 Reassessment | RNU | RAS/CRAS | Design | 45444 | N/A | 44409 | 2025-06-01 | 2025-06-30 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 594 | Trigger Year based on 2021 Reassessment report date.
SCE-C9P2-NOL-R1 | New North of Lugo RAS - Backbone Portion | New North of Lugo RAS combining HDPP RAS and Calcite RAS | SCE | C9 Phase II | RNU | RAS/CRAS | Design | 45473 | N/A | 43040 | 2024-06-01 | 2024-06-30 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 450 | Trigger Year based on Letter Agreement.
PIN8483-RNU | South of Vincent CRAS | Add lines south of Vincent to the Tehachapi CRAS | SCE | C13 Phase II | RNU | RAS/CRAS | Initiation | 45689 | N/A | 2021-12-31 | 2026-04-30 |  |  | New | 2026-02-01 | 2026-02-01 | 100 | Trigger Year based on GIA date.
SCE-C11P2-E-R1-C12 | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub | SCE | C12 Phase II | PNU | RAS/CRAS | Design | Pending | N/A | 43891 | 2026-10-01 | 2026-10-01 | 2026-10-01 | 2026-10-01 | 2027-10-01 | 2027-10-01 | 1460 | Trigger Year based on Riverside Transmission Reliability Project CPUC CPCN approval date. Contingent on Wildlife Substation schedule
SCE-C12P2-N-R3 | Moorpark CRAS: monitoring infrastructure | New Moorpark CRAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | Pending | N/A | 44378 | 45474 | 45474 | 45474 | 45474 | 45474 | Pending | 635 | Trigger year based on GIA. On-hold due to delays in associated project.
PIN6902 | Calcite Substation | New four position 220 kV switchrack | SCE | Serial LGIP | GRNU | New Substation | Permitting | Pending | Pending | 44165 | 2024-01-31 |  |  | New | TBD | TBD | 400 | Trigger Year based on GIA date. At the request of the IC, CAISO approved suspension of the associated project.
SCE-C11P2-E-R1 | West of Colorado Rivers CRAS - Inland/Devers Extension – additional remote monitoring | Additional infrastructure to convert the formally known Inland Empire RAS to centralized RAS platform | SCE | C11 Phase II | GRNU | RAS/CRAS | Design | Pending | N/A | 43435 | 2025-08-01 | 2025-08-01 | 2025-08-01 | 2027-04-01 | TBD | TBD | 150 | Contingent on Alberhill licensing schedule. Trigger Year based on GIA date.

## SDGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected July 2022 TDF | Expected In-Service Oct TDF 2022 | Expected In-Service January TDF 2023 | Expected In-Service April TDF 2023 | Agregate MW in Queue with Executed LGIA | Notes
SDGE-EXISTING-RNU-01 | Imperial Valley Existing/Modified RAS' | Imperial Valley Existing/Modified RAS' | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-7.1 | Existing Miguel BK 80 / 81 | Existing Miguel BK 80 / 81 | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-02 | Existing Otay Mesa RASs | Existing Otay Mesa RASs | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-04 | Existing ECO/BUE anti-islanding scheme for radial generators | Existing ECO/BUE anti-islanding scheme for radial generators | SDGE |  | PNU |  | Operational
SDGE-C11-PHII-RNU-02 | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | SDGE | C11 Phase II | PNU | Reliability | Operational |  | N/A | N/A | 2022-06-01 | 2022-06-01 | 2022-06-01 | 2022-06-18 | 2022-06-18 |  |  | Placed in service on 6/18/22
SDGE-C08-PHII-RNU-03.1 | TL680 OLS | Overload Scheme to protect TL680C. Previously named as Modify TL684 RAS. | SDGE | C8 Phase II | GRNU | Deliverability | In design |  | N/A | Jun-24 | [5 empty] | Jun-24 | 600 | This overload scheme does not trip generation, and is not needed for projects to come online, impacts NQC values.
SDGE-C07-PHI-RNU-01 | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | SDGE | C7 Phase I | PNU | Reliability | In design |  | N/A | 45078 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 527.8 | New CEC RAS - will mitigate the overload of 23006 for the loss of 23010 AND 23002; protect TL23011B from overloading for loss of 23003; and protect 23003 from overloading for the loss of TL23011. Project on track for Jun-2023 ISD
SDGE-C08-PHII-RNU-04 | Participate in the proposed RAS to protect TL23003 & TL23011 Encina to San Luis Rey 230 kV lines (Proposed grouping RAS to protect Encina/Pen/San Luis Rey 230kV Lines) | Proposed RAS to Protect TL23003 Encina - San Luis Rey 230 kV line | SDGE | C8 Phase II | PNU
SDGE-PRE-AMEND-RNU-01.2 | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | SDGE |  | CANU-GR

## GLW-VEA
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service July 2022 TDF | Expected In-Service Oct TDF 2022 | Expected In-Service January TDF 2023 | Expected In-Service April TDF 2023 | Agregate MW in Queue with Executed LGIA | Notes
VEA-C6P2-EOP-R5 | VEA Vista RAS | VEA Vista RAS: Install a new RAS to protect Jackass Flats - Mercury Switch 138 kV line under contingency conditions | VEA | C6 Phase II | RNU | Thermal | Cancelled | N/A | N/A | N/A | N/A | 2022-09-30 | 2022-11-22 |  |  |  |  | Supply chain issues pushed out the project outside the outage windows. As a result, a new outage plan was developed and the new anticipated in-service date is November 2022
VEA-C8P2-VEA-R2 | Innovation RAS | Install a new Innovation RAS | GLW | C8 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 |  | Delays in construction of Yellow Pine are delaying placing this upgrade into service. Current estimated In-service Date is is July 2023.
VEA-C9P2-EOP-R3 | Innovation RAS (VEA-GLW portion) | New Innovation RAS (include Desert View RAS from QC8) to trip generation under N-1 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 |  | Delays in construction of Yellow Pine are delaying placing this upgrade into service. Current estimated In-service Date is is July 2023.
VEA-C9P2-EOP-R4 | Sloan Canyon RAS (fka Bob RAS - VEA-GLW portion) | New Sloan Canyon RAS to trip generation under N-1 and N-2 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 |  | Delays in construction of Yellow Pine are delaying placing this upgrade into service. Current estimated In-service Date is is July 2023.
GLW-2021-EOP-L1 | Trout Canyon - Sloan Canyon 230kV line upgrade | Trout Canyon - Sloan Canyon 230kV line upgrade | GLW | 2021 Reassessment | LDNU |  |  |  |  | N/A | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 |  | --