## PGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Trigger Year | Current Expected Construction Start | Expected CPUC Permit Application | Previous In-Service Jan 2022 TDF | Previous In-Service Apr 2022 TDF | Previous In-Service Jul 2022 TDF | Previous In-Service Oct 2022 TDF | Previous In-Service Jan 2023 TDF | Previous In-Service Apr 2023 TDF | Previous In-Service Jul 2023 TDF | Previous In-Service Oct 2023 TDF | Previous In-Service Jan 2024 TDF | Previous In-Service July 2024 TDF | Previous In-Service Jan 2025 TDF | Previous In-Service July 2025 TDF | Current In-Service Jan 2026 TDF (Current) | Agregate MW in Queue with Executed LGIA | Notes
19rsmt-3 | Schindler 70kV Bus Normal & Outage Overload | Upgrade Schindler 70 kV Bus to 1113 kcmil AAC | PG&E | RA-19 | Reliability | Bus Flow | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
21rsmt-5 | Palo Alto 115 kV circuit breakers 412 and 442 overstress | Replace Palo Alto 115 kV circuit breakers 412 and 442 with 63 kA interrupting capability | PG&E | RA-21 | Reliability | SCD overstress | Removed | 2021 |  | 47260 | 45565 | 45743 | 46183 | 46699 | 46699 | 46699 | 46699 | 47206 | 47409 | 48129 | 48218 | 48218 | 48218 | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
22rsmt-2 | Cottonwood 60 kV many CB overstress upgrade | Replace Cottonwood 60 kV circuit breakers 22, 32, 42, 52, 62, 82 | PG&E | RA-22 | Reliability | SCD overstress | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C13P1-NCA02 | Cottonwood 230 kV circuit breaker 212, 242 & 282 overstress | Replace Cottonwood 230 kV circuit breaker 212, 242 & 282 | PG&E | C13 | Reliability | SCD overstress | Removed | 2025 | [12 empty] | N/A | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C13P1-WGR03 | Mesa Substation 115 kV CBs 142 overstress | Replace Mesa Substation 115 kV CB 142 with 63 kA interrupting capability | PG&E | C14 | Reliability | SCD overstress | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P1-GGD01 | PGAE_250_QC14P1RAS-03-gbay-tassajara–q1877ss-overload-RAS | RAS to trips Q1877 at Q1877SS Switching Station when an overload occurs in GRANT-Q1877SS or Q1877SS-EASTSHORE 115kV Lines due to outage of Q1877SS-EASTSHORE or GRANT-Q1877SS 115kV Lines, respectively, when Q1877 is in discharging mode. | PG&E | C14 | Reliability | RAS (Reliability) | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A |  | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P1-GGR03 | Ames Distribution 115 kV circuit breaker 112 & 122 overstress | Replace Ames Distribution 115 kV circuit breakers 112 & 122 | PG&E | C14 | Reliability | SCD overstress | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P1-GGR06 | Newark 115 kV bus overstress beyond 63 kA | Install series bus reactors between Newark Substation 115 kV bus secions E and F | PG&E | C14 | Reliability | SCD overstress | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P2-FGR05 | Transient stability mitigation: Panoche-Mendota 115 kV lines RAS | RAS should trip the output of Q1940 for the loss of Panoche-Mendota 115 kV line to mitigate the oscillations and voltage criteria violations. | PG&E | C14 | Reliability | RAS (Reliability) | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P2-FPN02 | Los Banos 230 kV circuit breaker 252 & 262 overstress | Relocate CB 262, 242 & 252 and their line terminal to the new 230 kV BAAH bus section. 242 & 252 line terminals would be crossed if we only move one line. | PG&E | C14 | Reliability | SCD overstress | Removed | 2023 |  | 2027-09-21 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2028-04-01 | 2028-04-01 | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects. Project In-Service date improved due to study needs and other test results for capacity and saftey concerns
C14P2-FPN05 | Los Banos: Q1381 is assigned a 230 kV BAAH Bus Section CB 262 Overtress | Needed for CB 262 Overtress GRNU | PG&E | C14 | Reliability | SCD overstress | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P2-GGR10 | Claremont (OAK K) 115 kV circuit breaker 122 overstress | Replace Claremont (OAK K) 115 kV circuit breaker 122 | PG&E | C14 | Reliability | SCD overstress | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P2-GGR11 | Palermo 115 kV CB 152 overstress | Replace Palermo 115 kV CB 152 | PG&E | C14 | Reliability | SCD overstress | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P2-GGR13 | Ravenswood 115 kV CB 132 and 142 | Replace Ravenswood 115 kV CB 132 and 142 | PG&E | C14 | Reliability | SCD overstress | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P2-GGR15 | Pittsburg Substation 230 kV Bus Section E overload. enhance conductor rating | Seek enhanced ratings of 2964/3372A for 2-2300 kcmil AL conductor. Assumes replacement of all fittings to compression and limited reconductor work to attach new fittings. | PG&E | C14 | Reliability | Bus Flow | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P2-GGR16 | Pittsburg Substation 115 kV Bus Section E overload. Reconductor/Reinforce Bus. | Reconductor bus to 3-2300 kcmil. Evaluate and Reinforce Structures. | PG&E | C14 | Reliability | Bus Flow | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P2-KGR09 | Kern PP 70 kV circuit breaker 62 overstress | Replace Kern PP 70 kV circuit breaker 62 | PG&E | C14 | Reliability | SCD overstress | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C14P2-SGR01 | Midway Substation 500 kV circuit breaker 712 overload mitigation | Replace Midway 500 kV CB 712, switches and jumpers to achieve 4000 A normal rating | PG&E | C14 | Reliability | Bus Flow | Removed |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. No longer assigned to Generation projects
C9P2-F17 | Panoche 115 kV circuit breakers 152 overstress | Replace Panoche 115 kV circuit breaker 152 and associated switches/relays | PG&E | C9 | Reliability | SCD overstress | Removed |  |  | 2026-03-06 | [8 empty] | 2027-12-30 |  | TBD | N/A | N/A | 0 | Q1 - 2026 - Removed. Upgrade came back as C14P2-FPN06 132 & 152 overstress mitigation
C14P1-KGR11 | Midway 500 kV CB 742, 912, 942 Overstress: Rerate Midway 500 kV CB 742, 822, 912, 942 | Rerate Midway 500 kV CB 742, 822, 912, 942 | PG&E | C14 | Reliability | SCD overstress | In-Service | 2024 |  | 2025-07-21 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | 2031-03-31 | 2025-10-09 | 1500 | Q1 - 2026 - In-Service as of : CB 822: 08/21/25 CB 942: 08/29/25 CB 912: 09/19/25 CB 742: 10/09/25
C8P2-15 | Cottonwood Substation 230 kV Circuit Breaker 522 and 542 Overstress | Cottonwood Substation 230 kV CB Overstress: Replace CB 522 & 542 (rated @ 34.5KA, overstress close-in fault is 35,179A or 2%, 679A). | PG&E | C8 | Reliability | SCD overstress | In-Service | 2018 |  | 2025-06-09 | 2023-07-28 | 2023-08-15 | 2023-08-15 | 2024-09-30 | 2024-09-30 | 2024-09-04 | 2025-12-31 | 2025-12-01 | 2025-02-17 | 2025-12-31 | 2025-12-31 | 2026-02-25 | 2025-07-15 | 200 | Q1 - 2026 - Project went online in Q3 2025 and was not published as In-service during the Jul 2025 TDF report.
C9P2-F13-F15 | Gates 230kV Bus Section E and CB 312, 322, 2102, 2202 overload mitigation (BAAH) | Gates Substation 230 kV circuit breakers 312, 322, 2102, 2202 overload – convert bus section E to BAAH and move Panoche-Gates #1 and #2 230 kV lines and Q1117/Q1120/Q1139/Q1242/Q1243 into bus section E | PG&E | C9 | Reliability | Bus Flow | In-Service | 2019 |  | 2021-08-06 | 2023-03-31 | 2023-03-14 | 2023-05-31 | 2023-03-14 | 2023-05-23 | 2023-05-31 | 2023-04-17 | 2023-04-17 | 2023-04-17 | 2023-04-17 | 2023-04-17 | 2023-04-17 | 2023-04-17 | 2441.3 | Q1 - 2026 - In-Service
C9P2-N09 | Re-conductor Stockton A-Weber #3 60 kV Line (Stockton A-Hazelton Jct) | Re-conductor 0.9 mi of Stockton A-Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC. | PG&E | C9 | Reliability | Re-conductor | In-Service | 2018 |  | 2022-01-14 | 2022-03-31 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 0 | Q1 - 2026 - In-Service
20rsmt-3 | Midway 230 kV Bus Section E overload mitigation | Replace limiting conductor and/or fittings on Bus Section E to achieve 3372 A min. rating | PG&E | RA-20 | Reliability | Bus Flow | In-Service | 2021 |  |  | 2022-09-30 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 44773 | 44773 | 370 | Q1 - 2026 - In-Service
20rsmt-7a | Tesla 500 kV circuit breaker 632 overstress | Replace Tesla 500 kV circuit breaker 632 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Service | 2021 |  |  | 44533 | 44533 | 44533 | 44533 | 44533 | 44533 | 44533 | 44533 | 44533 | 44533 | 44533 | 44533 | 44533 | 1260 | Q1 - 2026 - In-Service
20rsmt-7b | Tesla 500 kV circuit breakers 542 and 642 overstress | Replace Tesla 500 kV circuit breakers 542 and 642 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Service | 2020 |  | 45551 | 45504 | 45189 | 45394 | 45478 | 45485 | 45559 | 45616 | 45415 | 45838 | 45874 | 45747 | 45743 | 45743 | 4830 | Q1 - 2026 - In-Service
21rsmt-3 | Kern PP Substation 115 kV CB overstress (BAAH Conversion Phase 1 - CB282) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Service | 2021 |  | 44386 | 46081 | 45265 | 45265 | 45996 | 45996 | 45996 | 45996 | 45717 | 45604 | 45747 | 45747 | 45666 | 45666 | 110 | Q1 - 2026 - In-Service
21rsmt-SCD-23 | El Cerrito G 115kV CB 112, 142, 132 Overstress | Replace Overstressed Circuit Breakers | PG&E | RA-21 | Reliability | SCD overstress | In-Service | 2011 |  | 45303 | N/A | 45491 | 45490 | 45975 | 46017 | 46017 | 46017 | 45778 | 45778 | 45784 | 45642 | 45642 | 45642 | 0 | Q1 - 2026 - In-Service
C11P2-FC01 | Midway 500kV CB's 722 Overstress | Midway Sub: Replace 500kV CB's 722, SW's and Relays | PG&E | C11 | Reliability | SCD overstress | In-Service | 2021 |  |  | 46022 | 46022 | 44834 | 44834 | 44834 | 44834 | 44834 | 44834 | 44834 | 44834 | 44834 | 44834 | 44834 | 2300.1 | Q1 - 2026 - In-Service
C11P2-FP01 | Midway 500 kV circuit breakers 732, 752, 802, 812, 832, 842 & 852 overstress | Replace Midway 500 kV circuit breakers 732, 802, 832 and 842 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Service | 2021 |  |  | 44834 | 46022 | 44803 | 44803 | 44803 | 44803 | 44803 | 44803 | 44803 | 44803 | 44803 | 44803 | 44803 | 2300.1 | Q1 - 2026 - In-Service
C11P2-NC01 | Tesla Substation 230 kV bus section C-D and circuit breakers 372, 382 and 842 overstress (reactors) TESLA: 230KV BUS REACTORS C - D | Increase Tesla Substation 230 kV series bus reactors between bus section C and D and D and E | PG&E | C11 | Reliability | SCD overstress | In-Service | 2019 |  | 45092 | 45230 | 45226 | 45197 | 45259 | 45279 | 45380 | 45380 | 45380 | 45400 | 45376 | 45376 | 45376 | 45376 | 1212.3 | Q1 - 2026 - In-Service
C12P1-GCR01 | Moraga: Repl OCBs 612 & 622 | Replace Moraga 115 kV circuit breakers 612, 622 | PG&E | C12 | Reliability | SCD overstress | In-Service | 2022 |  | 2023-09-19 | 2026-10-01 | 2027-01-01 | 2028-11-23 | 2029-10-10 | 2028-11-23 | 2028-11-23 | 2028-11-23 | 2028-11-23 | 2024-02-18 | 2026-12-03 | 2032-02-04 | 2024-02-18 | 2024-02-18 | 0 | Q1 - 2026 - In-Service
C12P1-GPT01 | Ames Distribution 115 kV circuit breaker 132 overstress | Replace Ames Distribution 115 kV circuit breaker 132 | PG&E | C12 | Reliability | SCD overstress | In-Service | 2019 |  | 2025-03-18 | 45382 | 2024-06-14 | 2024-08-22 | 2026-03-10 | 2026-03-10 | 2026-03-10 | 2026-03-10 | 2028-03-24 | 2028-03-24 | 2030-08-08 | 2026-03-23 | 2025-03-28 | 2025-03-28 | 600 | Q1 - 2026 - In-Service
C12P1-NPT01 | Gold Hill Substation 115 kV circuit breakers 142 overstress | Replace Gold Hill Substation 115 kV circuit breakers 142 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Service | 2021 |  | 45378 | 45199 | 2024-01-04 | 2023-11-13 | 2025-07-02 | 2025-08-28 | 2025-01-28 | 2025-01-01 | 2025-01-01 | 45617 | 2024-12-31 | 2024-11-27 | 2025-11-14 | 2025-12-06 | 49.9 | Q1 - 2026 - In-Service
C12P1-NPT03 | Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 overstress | Replace Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Service | 2020 |  | 2021-06-01 | 2024-12-31 | 2024-12-31 | 2023-11-10 | 2024-05-01 | 2024-12-31 | 2024-09-30 | 2024-09-30 | 2024-12-31 | 2024-12-30 | 2025-05-21 | 2025-05-21 | 2025-04-30 | 2025-04-30 | 0 | Q1 - 2026 - In-Service
C12P2-GRNU2 | Gates Substation 230 kV Bus Overstress (Reactors on Bus E and F) | Install series bus reactors between Gates Substation 230 kV bus sections E and F | PG&E | C12 | Reliability | SCD overstress | In-Service | 2022 |  |  | 2025-12-01 | 2025-12-01 | 2025-12-31 | 2025-03-31 | 2025-03-31 | 2025-03-31 | 2024-05-31 |  | 2026-04-30 | 2026-04-27 | 2026-04-10 | 2025-12-31 | 2025-12-11 | 3700.01 | Q1 - 2026 - In-Service
C12P2-GRNU3 | Midway Substation 500 kV CB 712 overstress | Replace Midway Substation 500 kV CB 712 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Service | 2021 |  |  | 2025-12-31 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2000 | Q1 - 2026 - In-Service
C12P2-KC01 | Midway Substation 500kV CB 722 Overload mitigation | Replace Midway 500 kV CB 722 to achieve 3600 A emergency rating | PG&E | C12 | Reliability | Bus Flow | In-Service | 2021 |  |  | 2025-12-31 | 2025-12-31 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2025.1 | Q1 - 2026 - In-Service
C12P2-PNU-02 | Gates 230 kV circuit breakers 352, 362 and 372 overstress mitigation (Cap Banks) | Replace Gates 230 kV circuit breakers 352, 362 and 372 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Service | 2022 |  | 2022-10-24 | 2023-04-30 | 2023-03-31 | 2023-03-31 | 2023-04-06 | 2023-04-06 | 2023-05-23 | 2023-07-14 | 2023-07-12 | 2023-07-12 | 2023-07-12 | 2023-07-12 | 2023-07-12 | 2023-07-12 | 2336.4 | Q1 - 2026 - In-Service
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | PG&E | C13 | Reliability | SCD overstress | In-Service | 2018 |  | 2022-10-10 | 2025-05-31 | 2022-09-28 | 2022-12-01 | 2022-12-07 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 500 | Q1 - 2026 - In-Service
C13P2-GGR01 | Tesla 500 kV circuit breakers 622 overstress | Replace Tesla 500 kV circuit breaker 622 with 63 kA interrupting capability. Only went to 50 kA | PG&E | C13 | Reliability | SCD overstress | In-Service | 2021 | [7 empty] | 2021-12-20 | 2021-12-20 | 2021-12-20 | 2021-12-20 | 2021-12-20 | 2021-12-20 | 2021-12-20 | 2021-12-20 | 400 | Q1 - 2026 - In-Service
C13P2-SGR01 | Midway Substation 500 kV switches 721 & 723 overload. | Replace Midway 500 kV Switch 721 & 723 to achieve 4000 A normal rating | PG&E | C13 | Reliability | Bus Flow | In-Service | 2022 |  | 45587 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2024-11-22 | 2024-11-22 | 2024-11-22 | 2720.01 | Q1 - 2026 - In-Service
C13P2-SPN01 | Midway Substation 500 kV Control Building | Existing PG&E project to replace the 500 kV Control Building at Midway (Needed for Midway RAS) | PG&E | C13 | Reliability | RAS (Reliability) | In-Service | 2024 |  | 2022-03-01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2023-03-15 | 2023-03-15 | 2023-03-15 | 2023-03-15 | 2020 | Q1 - 2026 - In-Service
20rsmt-4 | Metcalf 115kV breakers Overstress (almost all breakers), install bus reactors on 230kV banks due to existing space constraints on the 115kV Bus | Install 4-3 ohm reactors at low side of Metcalf 115 kV 230kV Transformers | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 |  | 2026-10-23 | 2025-02-28 | 2025-08-22 | 2025-09-03 | 2025-11-04 | 2026-01-29 | 2026-02-05 | 2026-07-10 | 2027-04-09 | 2027-03-04 | 2029-12-31 | 2027-04-19 | 2027-10-05 | 2027-02-26 | 1200 | Q1 - 2026 - In-flight. Design complete April 2026. Does not delay Generation.
20rsmt-5 | Tesla 500 kV circuit breaker 612 overstress | Replace Tesla Substation 500 kV CB 612 and associated switches/relays | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 |  | 45953 | 45352 | 45440 | 45478 | 45512 | 45519 | 45593 | 45838 | 45706 | 46111 | 45961 | 46181 | 46184 | 46184 | 810 | Q1 - 2026 - No schedule changes at this time.
20rsmt-6 | 20RSMTRAS-02 (Reliability) to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | 20RSMTRAS-02 RAS to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | PG&E | RA-20 | Reliability | RAS (Reliability) | In-Flight | 2020 |  | 2027-01-14 | 2023-12-31 | 2023-12-29 | 2023-12-29 | 2023-10-31 | 2023-12-31 | 2024-11-14 | 2024-11-14 | 2025-05-08 | 2025-07-03 | 2026-07-02 | 2027-07-13 | 2027-07-13 | 2027-07-13 | 100 | Q1 - 2026 - Construction sequencing depends on Midway Bus D BAAH conversion and MPAC project activity. In-Service date subject to change depending on sequencing
21rsmt-1 | Henrietta Substation 70kV CBs 12 and 72 Overstress | Henrietta Sub: Replace 70kV CB 12 & 72 and switches. | PG&E | RA-21 | Reliability | SCD overstress | Not Triggered | 2021 |  |  | 46022 | 46189 | 45714 | 46279 | 46302 | 46302 | 46302 | 46302 | 46302 | 46714 | 47205 | TBD | TBD | 0 | Q1 - 2026 - Not Triggered by Generation.
21rsmt-3 | Kern PP Substation 115 kV CB overstress (BAAH Conversion Phase 3 - CB262) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 |  | 46113 | 46081 | 45581 | 45581 | 46363 | 46363 | 46363 | 46363 | 46357 | 46360 | 45747 | 46387 | 46507 | 46507 | 110 | Q1 - 2026 - Triggered by Generation. Construction start Q2 2026. On schedule for In-Service date in 2027.
21rsmt-3 | Kern PP Substation 115 kV CB overstress (BAAH Conversion Phase 4 - CB182) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 |  | 2027-11-01 | 46081 | 44958 | 45027 | 45608 | 45608 | 45608 | 45608 | 46784 | 46734 | 2025-03-31 | 2026-02-28 | 46815 | 46815 | 110 | Q1 - 2026 - Triggered by Generation. Construction Start Q3 2027. On schedule for In-Service date in 2028
24RSMT-GPN01 | Tesla 230 kV & 500 kV Bus Overstress mitigation | Tesla 230 kV & 500 kV Bus Overstress mitigation: Extend 230 kV and 500 kV buses into new sections, add one (1) 500/230 kV XFMR and new control buildings. Design for future SCD Mitigation and additional elements. | PG&E | RA-24 | Reliability | SCD overstress | In-Flight | 2024 |  | 47101 | [8 empty] | 47956 |  | N/A | 48132 | 47956 | 3950 | Q1 - 2026 – Project kicked off Nov 2025. Scoping in development; geosciences contractor onboarding for fault mapping. Layout alternatives (AIS/GIS) under evaluation. Updates to scheduling and planning targeted for May 2026.
C11P2-NP01 | Contra Costa 230kV SW's 601, 603 overload. Replaced by Line relocation project | Contra Costa PP: Replace 230kV SW's 601 & 603 and jumpers. | PG&E | C11 | Reliability | Bus Flow | Replaced | 2021 |  | 45565 | 46022 | 46022 | 45845 | 45779 | 45807 | 45800 | 45799 | 45800 | 45800 | 45799 | 45909 | 46043 | 46080 | 0 | Q1 - 2026 - See notes for Contra Costa PP 230 kV Line Terminals Reconfiguration Project (C11P2-NP02, C11P2-NP01)
C11P2-NP02 | Contra Costa 230kV Bus Sections D, E and F and circuit breaker 820 overload. Replaced by Line relocation project | Contra Costa PP: Reconductor Bus Sections D, E and F. Replace circuit breaker 820. | PG&E | C11 | Reliability | Bus Flow | Replaced | 2021 |  | 45565 | 46022 | 46022 | 45845 | 45779 | 45807 | 45800 | 45799 | 45800 | 45800 | 45799 | 45909 | 46043 | 46080 | 580 | Q1 - 2026 - See notes for Contra Costa PP 230 kV Line Terminals Reconfiguration Project (C11P2-NP02, C11P2-NP01)
C11P2-NP02 | Contra Costa PP 230 kV Line Terminals Reconfiguration Project (C11P2-NP02, C11P2-NP01) | Swap the Lone Tree line and Birds Landing Sw Sta. line between Sec 2D and Sec 2E and Move the Wind Master (Delta) line to section 2E. Replaces the need for: Contra Costa 230kV Bus Sections D, E and F and circuit breaker 820 overload Contra Costa 230kV SW's 601, 603 overload | PG&E | C11 | Reliability | Bus Flow | In-Flight | 2022 |  | 45565 | 2025-12-31 | 2025-12-31 | 2025-07-07 | 2025-02-04 | 2025-05-30 | 2025-05-23 | 2025-05-22 | 2025-05-23 | 2025-05-23 | 2025-05-22 | 2025-09-09 | 2026-01-21 | 2026-02-27 | 580 | Q1 - 2026 - In construction. In-Service date extected on plan Feb 2026
C11P2-NR01 | Cottonwood Substation 230 kV circuit breakers 222, 232, 242 overstress | Replace Cottonwood Substation 230 kV circuit breakers 222, 232, 242 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Flight | 2022 |  | 2026-04-30 | 2024-02-28 | 2024-04-02 | 2024-05-24 | 2025-08-28 | 2025-08-28 | 2025-03-07 | 2025-05-22 | 2027-01-25 | 2026-06-18 | 2027-08-25 | 2026-07-01 | 2026-12-31 | 2026-08-13 | 0 | Q1 - 2026 - Design completed. Approaching construction start Q2 2026. Small In-Service date change due to construction and resourcing impacts.
C12P1-GCR01 | Moraga: EM REPL CB 642 & 712 | Replace Moraga 115 kV circuit breakers 642 and 712 | PG&E | C12 | Reliability | SCD overstress | Not Triggered | 2022 |  | 2025-11-03 | [8 empty] | 2026-05-29 |  | 2032-02-04 | 2026-05-15 | 2026-05-29 | 0 | Q1 - 2026 - Not Triggered by Generation
C12P1-GCR01 | Moraga: Repl OCB 582 | Replace Moraga 115 kV circuit breakers 582 | PG&E | C12 | Reliability | SCD overstress | Not Triggered | [13 empty] | 2032-02-04 | TBD | TBD | 0 | Q1 - 2026 - Not Triggered by Generation
C12P1-NPT01 | Gold Hill Substation 115 kV circuit breakers 172 overstress with Bank 5 | Replace Gold Hill Substation 115 kV circuit breakers 172 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2021 |  | 2024-03-01 | 2023-09-30 | 2024-01-04 | 2023-11-13 | 2025-07-02 | 2025-08-28 | 2025-01-28 | 2025-01-01 | 2025-01-01 | 2024-11-21 | 2024-12-31 | 2024-11-27 | 2026-05-29 | 2026-05-29 | 49.9 | Q1 - 2026 - In construction. On schedule for In-Service date May 2026
C12P1-NPT04 | Vaca Dixon Substation 230 kV circuit breakers 442 overstress | Replace Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2021 |  | 2026-03-09 | 2024-03-31 | 2024-06-27 | 2024-12-02 | 2025-03-06 | 2025-05-20 | 2025-08-14 | 2025-10-16 | 2025-10-16 | 2027-06-09 | 2026-11-05 | 2027-05-28 | 2026-04-10 | 2026-06-04 | 850 | Q1 - 2026 - Design completed. Construction start March 2026.
C12P1-NPT04 | Vaca Dixon Substation 230 kV circuit breakers 452 overstress | Replace Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2021 |  | 2026-10-19 | 2024-03-31 | 2024-06-27 | 2024-12-02 | 2025-03-06 | 2025-05-20 | 2025-08-14 | 2025-10-16 | 2025-10-16 | 2027-06-09 | 2026-11-05 | 2027-05-28 | 2026-11-06 | 2027-01-08 | 850 | Q1 - 2026 - Design completed. Construction start Oct 2026.
C12P1-NPT04 | Vaca Dixon Substation 230 kV circuit breakers 462 overstress | Replace Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2021 |  | 2026-06-16 | 2024-03-31 | 2024-06-27 | 2024-12-02 | 2025-03-06 | 2025-05-20 | 2025-08-14 | 2025-10-16 | 2025-10-16 | 2027-06-09 | 2026-11-05 | 2027-05-28 | 2026-07-24 | 2026-10-02 | 850 | Q1 - 2026 - Design completed. Construction start June 2026.
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 overstress. | Replace Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2018 |  | 2026-10-01 | 2025-05-31 | 2025-05-29 | 2025-05-21 | 2026-02-17 | 2025-05-13 | 2026-02-26 | 2025-09-23 | 2027-05-01 | 2029-05-30 | 2027-08-25 | 2028-01-28 | 2026-01-06 | 2026-12-21 | 500 | Q1 - 2026 - Recently triggered by Generation. Does not delay Generation backfeed. Procurement delays impacting the changes in In-Service date reported.
C13P1-KGR01 | QC13P2RAS-04 Modify existing Midway 500/230 kV transformer overload SPS | Midway 500/230 kV transformer overload SPS to include transformer outage detection and transformer overload detection for Bank 11, 12, and 13 | PG&E | C13 | Reliability | RAS (Reliability) | In-Flight | 2024 |  | 2028-10-05 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2030-10-12 | 2030-10-12 | 2028-03-31 | 2029-02-28 | 870 | Q1 - 2026 - Depends on Midway Bus D conversion for the RAS component install. The In-Service date of the Midway project completes in Feb 2029. The In-Service date is subject to change after construction sequencing further into 2026.
C13P1-KGR05 | Midway Substation 230 kV bus and 27 circuit breakers overstress - Revsed to Install (2) Bus Reactors. Install 2 x 16 ohm series bus reactors between Midway Substation 230 kV bus sections D and E (16 ohm parallel/8 ohm net) | Install 2 x 16 ohm series bus reactors between Midway Substation 230 kV bus sections D and E (16 ohm parallel/8 ohm net) | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2024 |  | 2024-12-02 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2030-10-12 | 2030-10-12 | 2031-03-31 | 2031-03-31 | 1910 | Q1 - 2026 - Dependeny on construction sequencing with Midway Bus D BAAH conversion and related work activity. FIn-Service date changes may result after sequencing planning is complete further into 2026.
C13P1-KPN02 | Midway 230 kV Bus D BAAH Conversion: (Needed to install reactors between Bus Sections D & E) | Convert Midway Substation 230 kV to BAAH in order to install bus reactors & RAS | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2016 |  | 2027-02-10 | N/A | N/A | N/A | 2025-04-25 | 2025-04-25 | 2025-04-25 | 2025-05-08 | 2027-12-27 | 2030-02-28 | 2028-01-21 | 2030-08-22 | 2027-11-04 | 2027-11-04 | 1910 | Q1 - 2026 - Project In-Service date improved due to recalibration in PG&E's work portfolio.
C13P1-KPN03 | Midway 230 kV Bus D BAAH Conversion: (Needed for Midway 500/230 kV Transformer overload RAS) | Midway 230 kV Bus D BAAH Conversion: Convert Midway Substation 230 kV to BAAH needed for Midway 500/230 kV Transformer overload RAS | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2025 |  | 46743 | [8 empty] | 2029-02-07 |  |  | 2030-02-01 | 2029-02-07 | 570 | Q1 - 2026 - Project In-Service date improved due to recalibration in PG&E's work portfolio. To maintain In-Service date, key activites at Midway Sub and on Midway-Kern Lines #3 & #4 must be completed in 2026.
C14P1-GGR08 | Sobrante 115 kV CB 112 overstress | Replace Sobrante 115 kV circuit breaker 112 | PG&E | C14 | Reliability | SCD overstress | Not Triggered |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD |  | TBD | TBD | 0 | Q1 - 2026 - Not Triggered by Generation
C14P1-GGR09 | Tesla 230 kV Bus Overstress (2 CB with Line relocations) | Relocate a Tesla - Tracy #2 230kV line to Bus Sect. C - into BAAH bay position where Newark #2 line resides today. Newark #2 will shift to a new BAAH bay. Includes costs for (9) 230kV T-Line structures (4,000 feet of new line), BAAH bay w/2 CB's. | PG&E | C14 | Reliability | SCD overstress | In-Flight | 2024 | 2028-01-20 | 2029-01-11 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | 2031-04-11 | 2031-04-18 | 3950 | Q1 - 2026 – Project kicked off Nov 2025. Scoping in development; geosciences contractor onboarding for fault mapping. Layout alternatives (AIS/GIS) under evaluation. Updates to scheduling and planning targeted for May 2026.
C14P1-NGR02 | Cottonwood 230 kV circuit breaker 272 & 292 overstress | Replace Cottonwood 230 kV circuit breaker 272 & 292 | PG&E | C14 | Reliability | SCD overstress | Not Assigned | 2025 |  | 47035 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD |  | 47191 | 47340 | 0 | Q1 - 2026 - No longer assigned to Generation
C14P2-FGR04 | Los Banos 500 kV circuit breakers 822, 832 & 842 overstress | Replace Los Banos 500 kV circuit breakers 822, 832 & 842 | PG&E | C14 | Reliability | SCD overstress | In-Flight | 2024 |  | 46113 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | 47573 | 46477 | 46266 | 2600 | Q1 - 2026 - Breakers are sequenced to go online: CB 822 (Oct 2025 In-Service date), CB 832 (May 2026 In-Service date) CB 842 (Sep 2026 In-Service date)
C14P2-FGR06 | Transient Stability: Updated dynamic models required | Updated dynamic models required that exhibits acceptable performance. | PG&E | C14 | Reliability | Transient Stability | Initiating | 2025 |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | TBD | TBD | 25 | Q1 - 2026 - Not a project This is a transient study. When complete, it will be reported as completed.
C14P2-FPN03 | Los Banos 230 kV circuit breakers 212 & 222 overstress | Replace Los Banos 230 kV circuit breakers 212 & 222 | PG&E | C14 | Reliability | SCD overstress | In-Flight | 2023 |  | 2027-09-30 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2028-04-01 | 2028-04-01 | 2027-08-06 | 2027-09-30 | 1900 | Q1 - 2026 - Slight date modification. In-Service date subject to change pending construction sequencing for fall 2026 planning.
C14P2-FPN06 | Panoche 115 kV circuit breakers 152 overstress | Replace Panoche 115 kV circuit breakers 152 and associated switches | PG&E | C14 | Reliability | SCD overstress | In-Flight | 2022 |  | 2027-01-05 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2028-03-31 | 2028-04-26 | 2028-05-01 | 125 | Q1 - 2026 - Project in design. Slight date modifications.
C14P2-FPN07 | Panoche 230 kV bus overstress above 40 kA design and circuit breakers 212, 232, 242 ,252, 262, 272, 282, 292, 302, 312, 332, 412 & 422 overstress mitigation | Convert Panoche 230 kV Bus D to BAAH & Replace Bus E Overstressed CBs | PG&E | C14 | Reliability | SCD overstress | In-Flight | 2022 |  | 2026-04-20 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2028-04-28 | 2028-01-21 | 2028-02-18 | 2028-04-27 | 2600 | Q1 - 2026 - Project in design. Slight date modifications.
C14P2-GGR12 | Pittsburg 230 kV bus overstress. Bus D-E 230kV Buss Reactors | Install bus reactors between 230 kV sections D & E | PG&E | C14 | Reliability | SCD overstress | In-Flight | 2024 |  | 2028-01-07 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | 2030-04-11 | 2030-04-11 | 2300 | Q1 - 2026 - This project is undergoing a feasbiity review prior to scoping. The In-Service date is subject to change.
C14P2-GGR14 | Birds Landing Sw Sta 230 kV CB 212, 412 overload mitigation | Upgrade Birds Landing Sw Sta 230 kV bay 2 to 3000 A equipment and replacing 3 circuit breakers and associated switches/relays | PG&E | C14 | Reliability | Bus Flow | Not Triggered |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD |  | TBD | TBD | 0 | Q1 - 2026 - Not Triggered by Generation
C14P2-GGR17 | Midway 230 kV reactor replacement: Replace existing 9 ohm Midway 500/230 kV reactors with 13 ohm reactors | Replace existing 9 ohm Midway 500/230 kV reactors with 13 ohm reactors, | PG&E | C14 | Reliability | Reactor Upgrade | In-Flight | 2025 |  | 2028-09-07 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | 2029-03-31 | 2029-03-30 | 570 | Q1 - 2026 - Project developing scope. Proceeding to long lead material procurements in Q1 2026.
C14P2-GPN01 | Pittsburg 115 kV bus overstress. Bus D-E 115kV Buss Reactors | Install bus reactors between 115 kV sections D & E | PG&E | C14 | Reliability | SCD overstress | In-Flight | 2023 |  | 2027-04-30 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2028-05-12 | 2028-05-30 | 2028-05-26 | 2028-05-26 | 1000 | Q1 - 2026 - Triggered by Generation
C14P2-GPT04 | Ravenswood 115 kV CB 152, 312, 322 overstress | Replace Ravenswood 115 kV CB 152, 312, 322 | PG&E | C14 | Reliability | SCD overstress | In Flight | 2025 |  | 2032-07-08 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TBD | TBD | N/A | 2029-03-31 | 815 | Q1 - 2026 - Recently triggered by Generation. Project to be re-kicked off in 2026. In-Service date highly dependent on Long lead material procurements early in project.
POS-Q1932-NU1 | Wilson Sub: Convert 115 kV DBSB to BAAH | Wilson Sub: Convert 115 kV DBSB to BAAH | PG&E | C14 | Reliability | SCD overstress | In-Flight | 2023 |  | 2027-12-17 | [8 empty] | 2030-05-31 |  | 2029-12-21 | 2029-12-21 | 2030-05-31 | 200 | Q1 - 2026 - See C14P2-NFT03 for status.

## SCE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Previous In-Service Jan 2022 TDF | Previous In-Service Apr 2022 TDF | Previous In-Service Jul 2022 TDF | Previous In-Service Oct 2022 TDF | Previous In-Service Jan 2023 TDF | Previous In-Service Apr 2023 TDF | Previous In-Service Jul 2023 TDF | Previous In-Service Oct 2023 TDF | Previous In-Service Jan 2024 TDF | Previous In-Service July 2024 TDF | Previous In-Service Jan 2025 TDF | Previous In-Service July 2025 TDF | Current In-Service Jan 2026 TDF (Current) | Agregate MW in Queue with Executed LGIA | Notes
SCE-C10P2-E-R3 | West of Colorado River CRAS Inland/Devers Extension - monitoring infrastructure | Infrastructure to convert the formally referred to as the New Devers RAS and the Inland RAS to centralized RAS platform | SCE | C10 Phase II | RNU | RAS/CRAS | Closeout | 2022-03-01 | N/A | 43435 | 44470 | Aug-25 | 44986 | 44986 | 45078 | 45192 | 45192 | 2024-03-01 | 2024-03-01 | 2024-04-01 | Completed | Closeout | Closeout | 4855 | Project completed and it will be removed from future TDF's.
SCE-C9C10-N | Windhub AA Bank cRAS - monitoring infrastructure | Windhub AA Bank cRAS - monitoring infrastructure | SCE | 2021 Reassessment | GRNU | RAS/CRAS | Closeout | 2022-04-01 | N/A | 44409 | 44866 | 44958 | 44958 | 44958 | 44986 | 45046 | 2023-12-31 | 2023-09-01 | 2024-12-31 | 2024-02-01 | Completed | 2022-04-01 | Closeout | 1800 | Project completed and it will be removed from future TDF's.
PIN6902 | Calcite Substation | New four position 220 kV switchrack | SCE | Serial LGIP | GRNU | New Substation | Design | 2028-01-01 | 2025-04-01 | 44165 | 2024-01-31 |  |  | New | TBD | TBD | 2027-03-01 | 2027-03-01 | 2027-12-31 | 2027-11-01 | 2028-06-01 | 2028-06-01 | 2028-06-01 | 400 | Customer Avantus received County Planning Commission certified the Final Environmental Impact Report (FEIR) for both Avantus Sienna Solar project and SCEs Calcite Substation. Subsequently, Morongo Basin Conservation Association (MBCA) filed an appeal of this action to the County Board of Supervisors. The date for the Boards appeal hearing is currently schedule for 13th Jan 2026. October 2025: Adoption of the recirculated final EIR by the County of San Bernardino. Completion dates continue to be contingent on licensing activities.
SCE-C11P2-EOP-R1 | Lugo - Victorville CRAS - monitoring infrastructure | Infrastructure to convert the Lugo - Victorville RAS to centralized RAS platform | SCE | C11 Phase II | GRNU | RAS/CRAS | Design | 2025-09-25 | N/A | 43770 | 2024-06-01 | Jun-25 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-30 | 2025-06-01 | 2026-06-30 | 2027-12-30 | 2028-06-01 | 2028-06-30 | 2028-06-30 | 700 | Aggregate MW in queue will consist of existing projects to be converted from RAS to CRAS in addition to new projects that will be added.
SCE-TCP2-EOP-R4 | Lugo - Victorville RAS | Trip generation for Eldorado area 500kV line outages. | SCE | TC Phase II | RNU | RAS/CRAS | Execution | 2025-01-01 | N/A | 40787 | 44166 | 45047 | 45047 | 45047 | 45261 | 45261 | 2024-04-30 | 2024-06-30 | 2024-12-31 | 2025-06-30 | 2025-05-01 | 2025-12-30 | 2026-03-31 | 550 | Environmental permit approval delay and limited availability of 500kV tranmission line outages.
SCE-C12P2-N-R3 | Moorpark CRAS: monitoring infrastructure | New Moorpark CRAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | Q3 2027, accommodate design completion, permiting, long-lead material procurement, and outage coordination | N/A | 44378 | 45474 | 45474 | 45474 | 45474 | 45474 | Pending | 2025-10-15 | 2025-10-15 | 2025-10-15 | 2027-12-01 | 2028-06-01 | 2028-12-31 | 2028-12-31 | 715 | Project was on hold during the last few months. Scope of work is required for the now triggered expansion of the Moorpark CRAS triggered by QC13 generation interconnection projects.
SCE-C9P2-NOL-R1 | New North of Lugo RAS - Backbone Portion | New North of Lugo RAS combining HDPP RAS and Calcite RAS | SCE | C9 Phase II | RNU | RAS/CRAS | Design | 2029-01-01 | N/A | 43040 | 2024-06-01 | 2024-06-30 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2026-06-01 | 2026-06-01 | 2026-06-01 | 2030-06-30 | 1930-06-01 | 2030-06-30 | 2031-06-30 | 600 | Project sequencing and outage constraints are responsible for defering this work to a future completion date.
SCE-C11P2-N-L1 | Pardee – Pastoria – Warne 220 kV T/L rating increase | Upgrade terminal equipment and fix ground clearance for Pardee – Pastoria- Warne 230kV line | SCE | C11 Phase II | LDNU | Capacity Increase | Closeout | 2023-06-01 | N/A | 44013 | 44849 | 45170 | 45078 | 45078 | 45383 | 45078 | 2023-10-30 | 2024-03-29 | 2024-03-29 | 2025-12-01 | 2025-12-01 | 2025-09-26 | 2025-09-26 | 340 | Commercially operational
SCE-C72021-EOP | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | SCE | 2021 Reassessment | RNU | RAS/CRAS | Design | 2025-09-25 | N/A | 44409 | 2025-06-01 | 2025-06-30 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2026-06-30 | 2027-12-30 | 2028-06-01 | 2028-06-30 | 2028-06-30 | 897 | Note that out of these MW, only Q1341 will be converted over to the CRAS, leaving this value at 250 MW. Projects associated with the remaining MW will no longer participate on the CRAS. SCE proposes that this line item be removed since it only applies to the conversion of one existing project from the RAS to CRAS. This single project will be converted over to the CRAS platform as part of the work to take place under ID: SCE-C11P2-EOP-R1
PIN8483-RNU | South of Vincent CRAS | Add lines south of Vincent to the Tehachapi CRAS | SCE | C13 Phase II | RNU | RAS/CRAS | Design | 2027-06-01 | N/A | 2021-12-31 | 2026-04-30 |  |  | New | 2026-02-01 | 2026-02-01 | 2026-02-01 | 2027-12-15 | 2027-12-15 | 2026-05-01 | 2026-05-01 | 2027-11-03 | 2027-12-31 | 1400 | The monitoring infrastructure for the South of Vincent CRAS is currently forecasted to be complete by the end of Q4 2027. This date is dependent on other upgrades being completed on schedule within the area including the Lugo-Victorville 500kV T/L Upgrade Project.
SCE-C12P2-N-R2 | Tehachapi CRAS: monitoring infrastructure addition | Add N-1 to RAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Execution | 2026-01-01 | N/A | 44228 | 2024-09-01 | 2024-09-01 | 2024-09-01 | 2024-09-01 | 2025-04-01 | 2025-04-01 | 2025-11-01 | 2026-03-01 | 2026-03-01 | 2026-03-01 | 2026-03-01 | 2026-03-01 | 2026-11-24 | 3300 | Completion dates are subject to change based on activities that are required to complete with with neighboring utilities.
SCE-C9P2-N-R1 | Whirlwind AA Bank CRAS Monitoring Infrastructure | Implement Whirlwind AA Bank CRAS - monitoring infrastructure | SCE | 2018 Reassessment | GRNU | RAS/CRAS | Execution | 2023-07-05 | N/A | 44013 | 44866 | 44958 | 44958 | 44958 | 45078 | 45078 | 2024-03-30 | 2024-06-01 | 2024-12-31 | 2024-12-31 | 2025-06-01 | 2025-06-01 | 2025-03-01 | 1490 | Resource availability and interdependencies with Tehachapi CRAS.
SCE-C11P2-E-R1 | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub | SCE | C11 Phase II | RNU | RAS/CRAS | Design | Q4 of 2029 | N/A | 43891 | 2026-10-01 | 2026-10-01 | 2026-10-01 | 2026-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 2029-10-01 | 2029-10-01 | 2029-10-01 | 2029-10-01 | 865 | The delay related to in-servicing this portion of the CRAS has been caused by the City of Riverside due to their pursuit of the underground work which had delayed licensing and overall project initiation. MW value reduced since Q1529/TOT899 is no longer required to participate on the CRAS
SCE-C10P2-E-R3 | WOCR CRAS Inland/Devers Extension Monitoring (QC10) at Alberhill Sub | WOCR CRAS Inland/Devers Extension Monitoring (QC10) at Alberhill Sub | SCE | C10 Phase II | RNU | RAS/CRAS | Design | Pending | N/A | 43435 | 2025-08-01 | 2025-08-01 | 2025-08-01 | 2027-04-01 | TBD | TBD | TBD | 2029-06-01 | 2029-06-01 | Pending | On hold | On hold | On Hold | 5927 | CRAS monitoring installation to be incorporated into Alberhill Substation construction. Hold/subject to be cancelled due to Alberhill Substation Project ISD of 12/2029.
New: CAISO to provide ID (Devers 220 kV SCD Mitigation) | Devers 220 kV SCD Mitigation | Replace one (1) circuit breaker at Devers 220 kV substation with a circuit breaker with fault interrupting capability of 63kA and a tested X/R of 35 or higher. | SCE | QC13 | RNU | SCD | Plan/Analyze | Pending | N/A | 44501 | [11 empty] | New | TBD | 1204.8
New: CAISO to provide ID (Devers 220 kV SCD Mitigation: 80kA Upgrade) | Devers 220 kV SCD Mitigation: 80kA Upgrade | Upgrade Devers 220 Switchrack to 80 kA | SCE | QC14 | RNU | SCD | Plan/Analyze | Pending | N/A | 45321 | [11 empty] | New | 2030-11-28 | 2200
New: CAISO to provide ID (Mira Loma B 220 kV SCD Mitigation: 80kA Upgrade) | Mira Loma B 220 kV SCD Mitigation: 80kA Upgrade | Upgrade Mira Loma B 220 Switchrack to 80 kA | SCE | QC14 | RNU | SCD | Initiation | Pending | N/A | 45321 | [11 empty] | New | 2029-10-31 | 4950
New: CAISO to provide ID (Pardee 220 kV SCD Mitigation) | Pardee 220 kV SCD Mitigation | De-loop the Pardee 220 kV bus from the Pastoria-Warne-Pardee and Pardee-Santa Clara 220 kV lines to create the Pastoria-Warne-Santa Clara 220 kV line. Modify the Big Creek/Pastoria CRAS to account for the new transmission line topology. | SCE | QC13 | RNU | SCD | Plan/Analyze | Pending | N/A | 44522 | [11 empty] | New | TBD | 1415
New: CAISO to provide ID (Pardee 220 kV SCD Mitigation: 80kA Upgrade) | Pardee 220 kV SCD Mitigation | Upgrade Pardee 220 Switchrack to 80 kA | SCE | QC14 | RNU | SCD | Initiation | Pending | N/A | 45321 | [11 empty] | New | 2033-05-15 | 2375
New: CAISO to provide ID (Vincent 500 kV SCD Mitigation) | Vincent 500 kV SCD Mitigation | De-loop Antelope-Vincent No.1 and Lugo-Vincent No.2 500 kV lines | SCE | QC14 | RNU | SCD | Initiation | Pending | N/A | 45321 | [11 empty] | New | 2027-01-29 | 6800 | The 6,800MW value is based on projects with an active LGIA. Projects that are parked with active Letter Agreements and projects in negotiation are not counted toward this value which would increase the overall MW in queue to approximately 9,525MW.

## SDGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Previous In-Service Jan 2022 TDF | Previous In-Service Apr 2022 TDF | Previous In-Service Jul 2022 TDF | Previous In-Service Oct 2022 TDF | Previous In-Service Jan 2023 TDF | Previous In-Service Apr 2023 TDF | Previous In-Service Jul 2023 TDF | Previous In-Service Oct 2023 TDF | Previous In-Service Jan 2024 TDF | Previous In-Service July 2024 TDF | Previous In-Service Jan 2025 TDF | Previous In-Service July 2025 TDF | Current In-Service Jan 2026 TDF (Current) | Notes
SDGE-EXISTING-RNU-01 | Imperial Valley Existing/Modified RAS' | Imperial Valley Existing/Modified RAS' | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-7.1 | Existing Miguel BK 80 / 81 | Existing Miguel BK 80 / 81 | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-02 | Existing Otay Mesa RASs | Existing Otay Mesa RASs | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-04 | Existing ECO/BUE anti-islanding scheme for radial generators | Existing ECO/BUE anti-islanding scheme for radial generators | SDGE |  | PNU |  | Operational
SDGE-C11-PHII-RNU-02 | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | SDGE | C11 Phase II | PNU | Reliability | Operational |  | N/A | N/A | 2024-06-22 | 2024-06-22 | 2024-06-22 | 2024-06-22 | 2024-07-22 | 2024-06-22 | 2024-07-22 | 2024-06-22 | 2024-06-22 | In-Service | In-Service | In-Service |  |  | Placed in service on 6/18/22
SDGE-C08-PHII-RNU-03.1 | TL680 OLS | Overload Scheme to protect TL680C. Previously named as Modify TL684 RAS. | SDGE | C8 Phase II | GRNU | Deliverability | Operational |  | N/A | 1905-07-15 | 2024-06-23 | 2024-06-23 | 2024-06-23 | 2024-06-23 | 2024-06-23 | 2024-06-23 | 2024-04-23 | In-Service | In-Service | In-Service | In-Service | In-Service |  |  | Placed in service on 3/30/23
SDGE-C07-PHI-RNU-01 | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | SDGE | C7 Phase I | PNU | Reliability | Operational |  | N/A | 1905-07-15 | 2024-06-23 | 2024-06-23 | 2024-06-23 | 2024-06-23 |  | 2024-06-23 | 2024-06-23 | 2024-08-23 | 2024-08-23 | 2024-08-23 | 2024-08-23 | 2024-08-23 |  |  | Placed in service 8/20/23
SDGE-C08-PHII-RNU-04 | Participate in the proposed RAS to protect TL23003 & TL23011 Encina to San Luis Rey 230 kV lines (Proposed grouping RAS to protect Encina/Pen/San Luis Rey 230kV Lines) | Proposed RAS to Protect TL23003 Encina - San Luis Rey 230 kV line | SDGE | C8 Phase II | PNU | [6 empty] | 2024-06-23 | 2024-06-23 | 2024-06-23
SDGE-PRE-AMEND-RNU-01.2 | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | SDGE |  | CANU-GR | [6 empty] | 2024-06-23 | 2024-06-23 | 2024-06-23
SDGE-C14-PHII-RNU-81 | update relay settings for Q1532 - ECO 138 kV #1 line | update relay settings for Q1532 - ECO 138 kV #1 line | SDGE | C14 Phase II | GRNU | Deliverability | Design | 2025-04-25 | N/A | 2024 | 2027-05-17 | [9 empty] | 2028-05-01 | 2026-04-15 | 2026-03-18 | Removed | This Network Upgrade was removed in the 2024 Reassessment Report

## GLW-VEA
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Previous In-Service Jan 2022 TDF | Previous In-Service Apr 2022 TDF | Previous In-Service Jul 2022 TDF | Previous In-Service Oct 2022 TDF | Previous In-Service Jan 2023 TDF | Previous In-Service Apr 2023 TDF | Previous In-Service Jul 2023 TDF | Previous In-Service Oct 2023 TDF | Previous In-Service Jan 2024 TDF | Previous In-Service July 2024 TDF | Previous In-Service Jan 2025 TDF | Previous In-Service July 2025 TDF | Current In-Service Jan 2026 TDF (Current) | Agregate MW in Queue with Executed LGIA | Notes
VEA-C6P2-EOP-R5 | VEA Vista RAS | VEA Vista RAS: Install a new RAS to protect Jackass Flats - Mercury Switch 138 kV line under contingency conditions | VEA | C6 Phase II | RNU | Thermal | Cancelled | N/A | N/A | N/A | N/A | 2022-09-30 | 2022-11-22 | [7 empty] | N/A | N/A | Completed | Completed |  | Project was replaced by upgrading the Jackass Flats - Mercury Switch 138kV line. This project is completed.
VEA-C8P2-VEA-R2 | Innovation RAS | Install a new Innovation RAS | GLW | C8 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 | Complete | Complete | Complete | Complete | Completed | Completed | 1547 | Project completed.
VEA-C9P2-EOP-R3 | Innovation RAS (VEA-GLW portion) | New Innovation RAS (include Desert View RAS from QC8) to trip generation under N-1 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 | Complete | Complete | Complete | Complete | Completed | Completed | 1547 | Project completed.
VEA-C9P2-EOP-R4 | Sloan Canyon RAS (fka Bob RAS - VEA-GLW portion) | New Sloan Canyon RAS to trip generation under N-1 and N-2 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 | Complete | Complete | Complete | Complete | Completed | Completed | 1547 | Project completed.
GLW-2021-EOP-L1 | Trout Canyon - Sloan Canyon 230kV line upgrade | Trout Canyon - Sloan Canyon 230kV line upgrade | GLW | 2021 Reassessment | LDNU |  |  |  |  | N/A | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | N/A | 2027-12-31 | 2027-12-31 | 2026-12-31 | 2026-12-31 | 2027-12-31 | 2027-12-31 | N/A | The Trout Canyon – Sloan Canyon 230kV Line Upgrade is part of the GLW/VEA Area Project which was approved through the 2021-2022 TPP and revised in the 2022-2023 TPP to 500kV DCTL. GLW is prioritizing the TC-SC 500kV segment, project in final stages of BLM permitting process.