## PGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Trigger Year | Current Expected Construction Start | Expected CPUC Permit Application | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service Jul 2022 TDF | Expected In-Service Oct 2022 TDF | Expected In-Service Jan 2023 TDF | Expected In-Service Apr 2023 TDF | Expected In-Service Jul 2023 TDF | Expected In-Service Oct 2023 TDF | Expected In-Service Jan 2024 TDF (Current) | Agregate MW in Queue with Executed LGIA | Notes
C13P1-GPN06 | Birds Landing 230 kV CBs 422, 222, 412, 212 Overload Mitigation | Upgrade Birds Landing Sw Sta 230 kV bays 1 and 2 to 3000 A equipment and replacing 6 circuit breakers and associated switches/relays | PG&E | C13 | (blank) | (blank) | Removed | [12 empty] | 0 | Removed
C13P2-FPT04 | Jackson Switching Station (CHSR Site 10) | (blank) | PG&E | C13 | (blank) | (blank) | Removed | [12 empty] | 0 | Removed
C13P2-FPT05 | CHSR Site 8 | (blank) | PG&E | C13 | (blank) | (blank) | Removed | [12 empty] | 0 | Removed
C9P2-F17 | Panoche 115 kV circuit breakers 152 overstress | Replace Panoche 115 kV circuit breaker 152 and associated switches/relays | PG&E | C9 | Reliability | SCD overstress | Removed | [12 empty] | 0 | Removed
C12P2-PNU-02 | Gates 230 kV circuit breakers 352, 362 and 372 overstress mitigation (Cap Banks) | Replace Gates 230 kV circuit breakers 352, 362 and 372 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Service | 2022 | 2022-10-24 |  | 2023-04-30 | 2023-03-31 | 2023-03-31 | 2023-04-06 | 2023-04-06 | 2023-05-23 | 2023-07-14 | 2023-07-12 | 2023-07-12 | 2992.67 | In-Service
C9P2-F13-F15 | Gates 230kV Bus Section E and CB 312, 322, 2102, 2202 overload mitigation (BAAH) | Gates Substation 230 kV circuit breakers 312, 322, 2102, 2202 overload – convert bus section E to BAAH and move Panoche-Gates #1 and #2 230 kV lines and Q1117/Q1120/Q1139/Q1242/Q1243 into bus section E | PG&E | C9 | Reliability | Bus Flow | In-Service | 2019 | 44414 |  | 45016 | 44999 | 45077 | 44999 | 45069 | 45077 | 45033 | 45033 | 45033 | 1993.95 | In-Service
C12P1-NPN02 | Lodi Substation 60 kV circuit breakers 12 and 22 overstress | (blank) | PG&E | C12 | Reliability | SCD overstress | In-Service | 2011 | 2020-08-04 |  | 2022-03-28 | 2022-12-29 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 0 | In-Service
22rsmt-3 | Metcalf 230 kV Substation Circuit Breaker #No 292 Upgrade | Upgrade Metcalf Circuit Breaker #292 due to overstress issues | PG&E | (blank) | Capacity | (blank) | In-Service | 2022 |  |  |  | 45658 | 45992 | 2022-09-27 | 2022-09-27 | 2022-09-27 | 2022-09-27 | 2022-09-27 |  | 1395 | In-Service
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | PG&E | C13 | Reliability | SCD overstress | In-Service | 2018 | 2022-10-10 |  | 45808 | 44832 | 44896 | 2022-12-07 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2195 | In-Service
20rsmt-3 | Midway 230 kV Bus Section E overload mitigation | Replace limiting conductor and/or fittings on Bus Section E to achieve 3372 A min. rating | PG&E | RA-20 | Reliability | Bus Flow | In-Service | 2021 |  |  | 2022-09-30 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 |  | 409.7 | In-Service
C11P2-FP01 | Midway 500 kV circuit breakers 732, 802, 832 and 842 overstress | Replace Midway 500 kV circuit breakers 732, 802, 832 and 842 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Service | 2021 | 2022-12-31 |  | 2022-09-30 | 2025-12-31 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 |  | 2100.1 | In-Service
C11P2-FC01 | Midway 500kV CB's 722 Overstress | Midway Sub: Replace 500kV CB's 722, SW's and Relays | PG&E | C11 | Reliability | SCD overstress | In-Service | 2021 | 2022-09-30 |  | 2025-12-31 | 2025-12-31 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 |  | 2100.1 | In-Service
C12P2-GRNU3 | Midway Substation 500 kV CB 712 overstress | Replace Midway Substation 500 kV CB 712 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Service | 2021 | 2022-12-31 |  | 2025-12-31 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 |  | 1800 | In-Service
C12P2-KC01 | Midway Substation 500kV CB 722 Overload mitigation | Replace Midway 500 kV CB 722 to achieve 3600 A emergency rating | PG&E | C12 | Reliability | Bus Flow | In-Service | 2021 | 2022-12-31 |  | 2025-12-31 | 2025-12-31 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 |  | 3231.05 | In-Service
21rsmt-4 | Monta Vista 115 kV circuit breaker 1322 overstress | Replace Monta Vista 115 kV circuit breaker 1322 | PG&E | RA-21 | Reliability | SCD overstress | In-Service | 2021 | 2021-10-01 |  | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 |  | 1200 | In-Service
C8P2-6 | Re-conductor Los Banos-Q779 SS #1 230 kV Line | Re-conductor 4.5 mi Los Banos-Padre Flat SS #1 230 kV Line with 1113 ACSS and upgrade equipment to 1900 A. | PG&E | C8 | Deliverability | Re-conductor | In-Service | 2017 | 2022-10-24 |  | 2023-03-01 | 2023-02-28 | 2023-02-28 | 2022-12-14 | 2022-12-24 | 2022-12-24 | 2022-12-24 | 2022-12-24 | 2022-12-24 | 632 | In-Service
C8P1-35 | Re-conductor Los Banos-Quinto SS 230 kV Line | Re-conductor 6.11 mi Quinto Sw Sta-Los Banos 230 kV Line with super bundled 795 ACSS | PG&E | C8 | Deliverability | Re-conductor | In-Service | 2017 | 2022-03-03 |  | 2022-05-31 | 2023-05-16 | 2023-05-16 | 2023-05-16 | 2023-04-28 | 2023-05-10 | 2023-05-08 | 2023-05-08 | 2023-05-08 | 1110.62 | In-Service
C9P2-N09 | Re-conductor Stockton A-Weber #3 60 kV Line (Stockton A-Hazelton Jct) | Re-conductor 0.9 mi of Stockton A-Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC. | PG&E | C9 | Deliverability | Re-conductor | In-Service | 2018 | 2022-01-14 |  | 2022-03-31 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 25 | In-Service
20rsmt-7a | Tesla 500 kV circuit breaker 632 overstress | Replace Tesla 500 kV circuit breaker 632 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Service | 2021 | 2021-12-03 |  | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 |  | 850 | In-Service
C13P2-GGR01 | Tesla 500 kV circuit breakers 622 overstress | Replace Tesla 500 kV circuit breaker 622 with 63 kA interrupting capability. Only went to 50 kA | PG&E | C13 | Reliability | SCD overstress | In-Service | 2021 | [7 empty] | 2021-12-20 | 2021-12-20 | 2021-12-20 |  | 400 | In-Service
C11P2-NC01 | Tesla Substation 230 kV bus section D and circuit breakers 372, 382 and 842 overstress (reactors) TESLA: 230KV BUS REACTORS D - E | Increase Tesla Substation 230 kV series bus reactors between bus section C and D and D and E | PG&E | C11 | Reliability | SCD overstress | In-Service | 2019 | 2022-04-19 | N/A | 2023-10-31 | 2023-04-05 | 2023-03-28 | 2023-05-01 | 2023-06-13 | 2023-07-27 | 2023-06-14 | 2023-06-14 | 2023-06-14 | 2501.5 | In-Service
19rsmt-3 | Schindler 70kV Bus Normal & Outage Overload | Upgrade Schindler 70 kV Bus to 1113 kcmil AAC | PG&E | RA-19 | Reliability | Bus Flow | Not Triggered | [12 empty] | 0 | Q4-2023: Not triggered
C11P2-NC01 | Tesla Substation 230 kV bus section D and circuit breakers 372, 382 and 842 overstress (reactors) TESLA: 230KV BUS REACTORS C - D | Increase Tesla Substation 230 kV series bus reactors between bus section C and D and D and E | PG&E | C11 | Reliability | SCD overstress | In-Flight | 2019 | 2023-06-15 | N/A | 2023-10-31 | 2023-10-27 | 2023-09-28 | 2023-11-29 | 2023-12-19 | 2024-03-29 | 2024-03-29 | 2024-03-29 | 2024-04-18 | 2501.5 | Q1-2024: schedule/construction sequencing date adjustments.
C13P1-FPT02 | Warnerville-Bellota 230 kV line reconductoring | The project proposes to reinforce 45 circuit miles of the 230 kV transmission lines between Bellota, Cottle, and Warnerville substations with 1113 kcmil steel-supported aluminum conductors with emergency capability of 1890 Amps. The project includes the installation of a new Optical Ground Wire (OPGW) that will replace the existing aging third-party owned OPGW. The project will upgrade the Bellota, Cottle, and Warnerville terminals and upgrade the line fault protection to current safety standards. The project includes replacing a manual bypass switch and installing an additional shield wire. Key construction elements are as follows: • Replace 148 steel electric transmission lattice towers with 148 new tubular steel poles (TSP’s) • Replace 1 manual bypass switch • Replace 22.5 miles of the Bellota-Warnerville 230 kV circuit • Replace 19.9 miles of the Bellota-Cottle 230 kV circuit • Replace 2.5 miles of the Cottle-Melones 230 kV circuit • Replace 0.1 mile of the Warnerville-Wilson 230 kV circuit • Replace 22.5 miles of OPGW with new OPGW • Install 22.5 miles of shield wire • Upgrade transmission line terminals at Bellota, Cottle, and Warnerville substations | PG&E | (blank) | Capacity | Re-conductor | In-Flight | 2013 | 2022-06-01 | NOC: AL 6047-E | 2024-12-27 | 2024-04-30 | 2024-04-30 | 2024-04-30 | 2024-04-30 | 2024-04-30 | 2024-04-30 | 2024-05-31 | 2024-04-30 | 0 | Q1-2024: schedule/construction sequencing date adjustments.
C8P2-3 | QC8RAS-08 RAS (Deliverability Triggered RNU) | QC8RAS-08 RAS to trip Generation offline for outage AND overload of either Gates 500/230 kV Transformer Bank 11 or 12 | PG&E | C8 | Deliverability | RAS (Deliverability) | In-Flight | 2017 |  |  | 2023-01-12 | 2023-01-12 | 2023-12-31 | 2024-05-03 | 2024-05-03 | 2024-05-03 | 2024-05-03 | 2024-05-03 | 2024-05-03 | 2870.57 | Q1-2024: Project is currently getting the telecom radio and fiber line connections completed. Testing planned for April. The Gates 500kV bank 12 ISD is planned for Q2 2024.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 1 - incl CB282) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2021-07-09 |  | 2026-02-28 | 2023-12-05 | 2023-12-05 | 2025-12-05 | 2025-12-05 | 2025-12-05 | 2025-12-05 | 2025-03-01 | 2024-11-08 | 200 | Q1-2024: Phase 1 activity
C12P1-NPT01 | Gold Hill Substation 115 kV circuit breakers 142 and 172 overstress | Replace Gold Hill Substation 115 kV circuit breakers 142 and 172 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2021 | 2024-06-06 |  | 2023-09-30 | 2024-01-04 | 2023-11-13 | 2025-07-02 | 2025-08-28 | 2025-01-28 | 2025-01-01 | 2025-01-01 | 2024-11-21 | 49.9 | Q1-2024: Long Lead Material Received. Proceeding to construction contracts for Release to Civil Construction in March for CB142. Construction Start in April for CB172.
C12P1-NPT03 | Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 overstress | Replace Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2020 | 2021-06-01 |  | 2024-12-31 | 2024-12-31 | 2023-11-10 | 2024-05-01 | 2024-12-31 | 2024-09-30 | 2024-09-30 | 2024-12-31 | 2024-12-30 | 49.9 | Q1-2024: In progress: on site construction of new Transformers, 115kV GIS System, and 230kV GIS System.
C11P2-ND03 | North Dublin-Cayetano 230 kV Line | Reconductor North Dublin-Cayetano 230 kV Line 2.63 miles OH Line & 2.82 UG cable with new UG cable 797 MVA/2000 A | PG&E | C11 | Deliverability | Re-conductor | In-Flight | 2021 | 2024-09-17 | 45313 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-03-25 | 2025-03-25 | 2025-02-10 | 2025-03-24 | 2025-03-25 | 2025-01-20 | 90.8 | Q1-2024: Upcoming procurement of material (6 month lead times) and EPC contract execution are in progress. Main drivers to ISD will be clearance availability and CPUC permitting.
C8P2-15 | Cottonwood Substation 230 kV Circuit Breaker 522 and 542 Overstress | Cottonwood Substation 230 kV CB Overstress: Replace CB 522 & 542 (rated @ 34.5KA, overstress close-in fault is 35,179A or 2%, 679A). | PG&E | C8 | Reliability | SCD overstress | In-Flight | 2018 | 45504 |  | 2023-07-28 | 2023-08-15 | 2023-08-15 | 2024-09-30 | 2024-09-30 | 2024-09-04 | 2025-12-31 | 2025-12-01 | 2025-02-17 | 700 | Q1-2024: The Circuit Breakers are expected in Q2 2024
21rsmt-SCD-23 | El Cerrito G 115kV CB 112, 142, 132 Overstress | Replace Overstressed Circuit Breakers | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2011 | 45303 |  |  | 2024-07-18 | 2024-07-17 | 2025-11-14 | 2025-12-26 | 2025-12-26 | 2025-12-26 | 2025-05-01 | 2025-05-01 | 0 | Q1-2024: CB 112 and CB 142 have been replaced under emergency orders. CB 132 is overstressed and will be replaced by Q2 2025. Long lead materials have been ordered. Underground Transmission cable and switch expected Q1 2024.
C8P1-34 | Re-conductor Padre Flat SS-Panoche #1 230 kV Line | Re-conductor 32.59 mi Q779/Padre Flat SS-Panoche #1 230 kV Line with 795 ACSS | PG&E | C8 | Deliverability | Re-conductor | In-Flight | 2017 | 2023-09-21 | 44967 | 2024-05-31 | 2024-05-21 | 2024-05-20 | 2024-05-20 | 2024-05-10 | 2024-05-10 | 2024-05-10 | 2025-05-13 | 2025-05-13 | 600 | Q1-2024: Phase 1 of construction is in progress and expected to be completed on time in Q2 2024. Phase 2 is expected to start on time in Q4 2024 and be completed by Q2 2025.
C11P2-NP02 | Contra Costa 230kV Bus Sections D, E and F and circuit breaker 820 overload. Replaced by Line relocation project | Contra Costa PP: Reconductor Bus Sections D, E and F. Replace circuit breaker 820. | PG&E | C11 | Reliability | Bus Flow | Replaced | 2021 | 2024-12-30 |  | 2025-12-31 | 2025-12-31 | 2025-07-07 | 2025-05-02 | 2025-05-30 | 2025-05-23 | 2025-05-22 | 2025-05-23 | 2025-05-23 | 490.8 | Q1-2024: Scoping is complete. Long lead material scheduled to arrive in August 2024. Working toward Engineering/IFC completion, Construction Contract Execution, and Clearance coordination with other projects
C11P2-NP01 | Contra Costa 230kV SW's 601, 603 overload. Replaced by Line relocation project | Contra Costa PP: Replace 230kV SW's 601 & 603 and jumpers. | PG&E | C11 | Reliability | Bus Flow | Replaced | 2021 | 2024-12-30 |  | 2025-12-31 | 2025-12-31 | 2025-07-07 | 2025-05-02 | 2025-05-30 | 2025-05-23 | 2025-05-22 | 2025-05-23 | 2025-05-23 | 0 | Q1-2024: Scoping is complete. Long lead material scheduled to arrive in August 2024. Working toward Engineering/IFC completion, Construction Contract Execution, and Clearance coordination with other projects
C11P2-NP02, C11P2-NP01 | Contra Costa PP 230 kV Line Terminals Reconfiguration Project | Swap the Lone Tree line and Birds Landing Sw Sta. line between Sec 2D and Sec 2E and Move the Wind Master (Delta) line to section 2E. Replaces the need for: Contra Costa 230kV Bus Sections D, E and F and circuit breaker 820 overload Contra Costa 230kV SW's 601, 603 overload | PG&E | C11 | Capacity | Bus Flow | In-Flight | 2022 | 2024-05-23 | N/A | 2025-12-31 | 2025-12-31 | 2025-07-07 | 2025-02-04 | 2025-05-30 | 2025-05-23 | 2025-05-22 | 2025-05-23 | 2025-05-23 | 691 | Q1-2024: No date changes at this time.
20rsmt-7b | Tesla 500 kV circuit breakers 542 and 642 overstress | Replace Tesla 500 kV circuit breakers 542 and 642 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 2024-01-26 |  | 2024-07-31 | 2023-09-20 | 2024-04-12 | 2024-07-05 | 2024-07-12 | 2024-09-24 | 2024-11-20 | 2024-05-03 | 2025-06-30 | 2680 | Q1-2024: On 1/17/2024, a supplier informed that the circuit breakers are delayed until March 2024. Due to clearances, the project has deferring construction start to Q4 2024 with a projected in-service date of Q2 2025.
20rsmt-6 | 20RSMTRAS-02 (Reliability) to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | 20RSMTRAS-02 RAS to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | PG&E | RA-20 | Reliability | RAS (Reliability) | In-Flight | 2020 | 2025-01-13 |  | 2023-12-31 | 2023-12-29 | 2023-12-29 | 2023-10-31 | 2023-12-31 | 2024-11-14 | 2024-11-14 | 2025-05-08 | 2025-07-03 | 100 | Q1-2024: Project depends on Midway 230kV Bus D BAAH conversion and its related MPAC install. The Dependent Generator opted to install the necessary equipment into the existing 115/230kV building. To complete the RAS, the project will move the necessary equipment from the old building to the new 230kV MPAC, when it's ready and available.
C9P1-F12 | Re-conductor Borden-Gregg #2 230 kV Line | Re-conductor 6.25 mi Borden-Gregg #2 230 kV Line with 1113 ACSS | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2017 | 2025-08-08 | 45348 | 2025-05-31 | 2025-05-07 | 2025-05-07 | 2025-05-07 | 2025-05-07 | 2026-01-16 | 2026-01-16 | 2026-01-16 | 2026-01-16 | 632 | Q1-2024: 30% re-design package received Jan 2024. Final scope is expected March 2024.
C11P2-ND01 | Re-conductor Fulton-Hopland 60 kV Line (Fitch Mountain Tap-Geysers Jct) | Re-conductor Fulton-Hopland 60 kV Line (Fitch Mountain Tap 009/005A-Geysers Jct 016/004) ~7 mi total length with 715 AAC | PG&E | C11 | Deliverability | Re-conductor | In-Flight | 2018 | 2025-10-13 | 2024-10-25 | 2026-03-31 | 2027-12-31 | 2027-12-31 | 2025-11-03 | 2026-02-13 | 2026-05-25 | 2026-06-05 | 2026-04-02 | 2026-03-23 | 230 | Q1-2024: The project has determined there is more structural scope than expected. Long lead materials expected Q2 2025. Permits expected Q2 2025.
C9P2-N02 | Re-conductor Fulton-Hopland 60 kV Line (Geysers Jct-Cloverdale Jct-Hopland) | Re-conductor 24.21 mi Fulton-Hopland 60 kV Line (Geysers Jct 016/003A-Cloverdale Jct 026/002-Hopland) with 715 AAC and upgrade any limiting equipment | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2019 | 2025-10-13 | 2024-10-25 | 2027-05-31 | 2027-03-31 | 2027-12-31 | 2025-11-03 | 2026-02-13 | 2026-05-25 | 2026-06-05 | 2026-04-02 | 2026-03-23 | 230 | Q1-2024: The project has determined there is more structural scope than expected. Long lead materials expected Q2 2025. Permits expected Q2 2025.
Impact to C14 | Tesla MPAC | New 230kV MPAC building relocates 230kV equipment from existing Control Building | PG&E | n/a | Reliability | MPAC | In-Flight | 2018 | 2025-08-06 |  |  | n/a | n/a | 2024-10-09 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2026-03-24 | 0 | Q1-2024: Project has experienced several delays and is likely delayed until Q3 2027. No present impact to Generation projects.
C11P2-GP01 | Moraga-Castro Valley 230 kV Line Capacity Increase Project | The project scope of work involves upgrading the limiting substation equipment (jumper conductors and wave traps) on the Moraga-Castro Valley and Castro Valley-Newark 230 kV lines to utilize their full conductor ratings. | PG&E | C11 | Capacity | (blank) | In-Flight | 2011 | 2024-07-05 | TBD | 2023-09-22 | 2023-11-06 | 2024-03-07 | 2024-03-20 | 2024-06-20 | 2024-10-25 | 2024-10-16 | 2026-03-25 | 2026-03-25 | 90.8 | Q1-2024: No date changes at this time.
20rsmt-5 | Tesla 500 kV circuit breaker 612 overstress | Replace Tesla Substation 500 kV CB 612 and associated switches/relays | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 2024-10-30 |  | 2024-03-01 | 2024-05-28 | 2024-07-05 | 2024-08-08 | 2024-08-15 | 2024-10-28 | 2025-06-30 | 2025-02-18 | 2026-03-30 | 850 | Q1-2024: On 1/17/2024, a supplier informed that the circuit breakers are delayed until March 2024. Due to clearances, the project has deferring construction start to Q4 2025 with a projected in-service date of Q1 2026.
C12P2-GRNU2 | Gates Substation 230 kV Bus Overstress (Reactors on Bus E and F) | Install series bus reactors between Gates Substation 230 kV bus sections E and F | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2022 | 2024-08-29 |  | 2025-12-01 | 2025-12-01 | 2025-12-31 | 2025-03-31 | 2025-03-31 | 2025-03-31 | 2024-05-31 |  | 2026-04-30 | 2300 | Q1-2024: In-Service delayed to Q2 2026 due to 42 week lead time on reactors. Civil work started in 2023. Construction resumes Q3 2024 to Q1 2025 on BUS 1 . Work Resumes in Q3 2025 to Q1 2026 on BUS 2.
C8P2-1 | Re-conductor Borden-Gregg #1 230 kV Line | Re-conductor 6.25 mi Borden-Gregg #1 230 kV Line with 1113 ACSS and upgrade equipment to 2000 A minimum (this is the existing Borden-Gregg 230 kV Line) | PG&E | C8 | Deliverability | Re-conductor | In-Flight | 2017 | 2026-01-30 | 45348 | 2026-01-05 | 2026-01-05 | 2026-01-05 | 46027 | 2026-01-05 | 2026-05-07 | 2026-05-07 | 2026-05-07 | 2026-05-07 | 632 | Q1-2024: 30% re-design package received Jan 2024. Final scope is expected March 2024.
C9P1-F11 | Re-conductor Dos Amigos PP-Panoche #3 230 kV Line | Re-conductor 23.63 mi Dos Amigos PP-Panoche #3 230 kV Line with 795 ACSS | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2017 | 2025-09-15 |  | 2025-05-14 | 2025-04-30 | 2025-04-30 | 2025-04-30 | 2025-04-30 | 2025-04-30 | 2025-05-01 | 2026-05-01 | 2026-05-15 | 632 | Q1-2024: Project on schedule for Q2 2026 ISD. Conductor planned for delivery in Q3 2024. Tower steel planned for Q4 2024. Substation switches planned for delivery Q2 2024.
C11P2-NR01 | Cottonwood Substation 230 kV circuit breakers 222, 232, 242 overstress | Replace Cottonwood Substation 230 kV circuit breakers 222, 232, 242 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Flight | 2022 | 2025-06-03 |  | 2024-02-28 | 2024-04-02 | 2024-05-24 | 2025-08-28 | 2025-08-28 | 2025-03-07 | 2025-05-22 | 2027-01-25 | 2026-06-18 | 500 | Q1-2024: Scoping is complete. Long lead material scheduled to arrive in September 2025
21rsmt-1 | Henrietta Substation 70kV CBs 12 and 72 Overstress | Henrietta Sub: Replace 70kV CB 12 & 72 and switches. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2025-07-14 |  | 2025-12-31 | 2026-06-16 | 2025-02-26 | 2026-09-14 | 2026-10-07 | 2026-10-07 | 2026-10-07 | 2026-10-07 | 2026-10-07 | 0 | Q1-2024: Previous scope has to be confirmed with current condition within the substation. Design and Engineering to follow.
C12P1-GCR01 | Moraga 115 kV circuit breakers 582, 612, 622, 642 and 712 overstress | Replace Moraga 115 kV circuit breakers 582, 612, 622, 642 and 712 | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2022 | 2025-03-06 |  | 2026-10-01 | 2027-01-01 | 2028-11-23 | 2029-10-10 | 2028-11-23 | 2028-11-23 | 2028-11-23 | 2028-11-23 | 2026-12-03 | 220 | Q1-2024: CB 582 in-service Jan 2023. CB 612 and 622 ISD being replaced under emergency. Planned ISD Feb 2024. The remaining two breakers CB 642 and CB 712 design is complete and materials onsite.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 3 - incl CB262) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2026-01-01 |  | 2026-02-28 | 2024-10-16 | 2024-10-16 | 2026-12-07 | 2026-12-07 | 2026-12-07 | 2026-12-07 | 2026-12-01 | 2026-12-04 | 200 | Q1-2024: Phase 3 activity
20rsmt-4 | Metcalf 115kV breakers Overstress (almost all breakers), install bus reactors on 230kV banks due to existing space constraints on the 115kV Bus | Install 4-3 ohm reactors at low side of Metcalf 115 kV 230kV Transformers | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 2026-05-29 |  | 2025-02-28 | 2025-08-22 | 2025-09-03 | 2025-11-04 | 2026-01-29 | 2026-02-05 | 2026-07-10 | 2027-04-09 | 2027-03-04 | 1145 | Q1-2024: Delivery date for bus reactors is Q3 2025.
C12P2-LDNU1 | Ripon-Manteca 115 kV Line Reconductor | Reconductor Ripon-Manteca 115 kV line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total) | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2026-04-06 | 2025-02-03 | 2027-12-31 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2028-09-11 | 2027-04-19 | 2027-05-10 | 2027-05-10 | 99 | Q1-2024: This project is part of a multi-phased process to rebuild/reconductor in the Ripon-Manteca area. Long lead materials expected in Q1 2026. Permit completion is expected in Q1 2026. Project is soliciting bids for the design contract
C12P1-NPT04 | Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 overstress | Replace Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | Initiating | 2021 | 2026-02-19 |  | 2024-03-31 | 2024-06-27 | 2024-12-02 | 2025-03-06 | 2025-05-20 | 2025-08-14 | 2025-10-16 | 2025-10-16 | 2027-06-09 | 1840.8 | Q1-2024: Q1-2024: Project is in the process of requesting circuit breakers. If the Project cannot locate non-long lead options, the Project will become subject to significant 230kV Circuit Breaker lead times with supplier estimates of 4-1/2 years. The Project is working on improving the stated ISD.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 4 - incl CB182) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2027-11-01 |  | 2026-02-28 | 2023-02-01 | 2023-04-11 | 2024-11-12 | 2024-11-12 | 2024-11-12 | 2024-11-12 | 2028-02-01 | 2027-12-13 | 200 | Q1-2024: Phase 4 activity
C12P1-GPT01 | Ames Distribution 115 kV circuit breaker 132 overstress | Replace Ames Distribution 115 kV circuit breaker 132 | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2019 | 2026-02-11 |  | 2024-03-31 | 2024-06-14 | 2024-08-22 | 2026-03-10 | 2026-03-10 | 2026-03-10 | 2026-03-10 | 2028-03-24 | 2028-03-24 | 450 | Q1-2024: Project Team has resumed planning. There is a change in resources for engineering. Once final, scoping will resume.
C12P2-LDNU4 | Stanislaus-Melones SW STA-Riverbank Jct Sw Sta 115 kV Line Reconductor | Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/043 - scope taken over by the more comprehensive STAN-MELONES TAP LINES: REPL CU COND P3 project. | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2028-02-25 |  | 2027-12-31 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2028-09-11 | 2028-05-29 | 2028-06-08 | 2028-05-11 | 99 | Q1-2024: This project is part of a multi-phased process to rebuild/reconductor in the Stanislaus-Melones area. Long lead materials expected in Q3 2027. Permit completion is expected in Q3 2026.
C12P2-LDNU3 | Bellota-Riverbank-Melones Sw Sta 115 kV Line 115 kV Line Reconductor | Reconductor a total of 17 miles of Bellota-Riverbank-Melones SW STA 115 kV Line with 477 ACSS | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2027-09-10 | 45712 | 2027-12-31 | 2027-12-16 | 2027-12-31 | 2027-12-31 | 2027-12-31 | 2028-09-11 | 2028-04-12 | 2028-08-18 | 2028-08-18 | 99 | Q1-2024: This project is part of a multi-phased process to rebuild/reconductor in the Bellota-Riverbank area. Long lead materials expected in Q4 2025. Permit completion is expected in Q1 2027. Project is soliciting bids for the design contract
C12P2-LDNU2 | Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line Reconductor | Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV line 25.23 miles section of various conductors from 018/115-043/277 | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2026-07-21 | 2025-05-20 | 2027-12-31 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2028-09-11 | 2028-02-29 | 2028-09-05 | 2028-09-05 | 99 | Q1-2024: This project is part of a multi-phased process to rebuild/reconductor in the Stanislaus-Melones area. Long lead materials expected in Q2 2025. Permit completion is expected in Q2 2026. Project is soliciting bids for the design contract
22rsmt-4 | New 230 kV switching station to loop Dos Amigos – Panoche # 3 230 kV | Build a new 2 bay 230 kV BAAH switching station to loop in the Dos Amigos – Panoche # 3 230 kV Line requiring access road, land and land rights acquisition and permitting, remote end protection upgrades, and OPGW/fiber telecommunication work | PG&E | RA-22 | Deliverability | New Station | Initiating |  |  |  |  | n/a | n/a | 2028-12-31 | 2028-12-31 | 2028-12-31 | 2028-12-31 | 2028-12-01 | 2028-12-01 | 632 | Q1-2024: Project has entered into the planning stage and has been assigned a lead PM.
C8P2-10 | QC8RAS-02 SPS (Deliverability Triggered RNU) | QC8SPS-02 SPS to modify the existing Hatchet Ridge SPS to trip Q1106 200 MW wind and Hatchet Ridge 102 MW wind for thermal overloads on the Q1106 SS-Cottonwood, Carberry SS-Round Mountain or Pit #3-Carberry SS 230 kV Lines. | PG&E | C8 | Deliverability | RAS (Deliverability) | Deferred | 2017 | 2028-05-23 |  | 2023-07-28 | 2023-07-28 | 2023-07-28 | TBD | 2027-03-31 | 2028-12-07 | 2028-12-07 | 2028-12-07 | 2028-12-07 | 200 | Q1-2024: ISD is dependent on the triggering Queue project's self-built switching station. ISD will be reviewed and updated when the Queue project resumes active engagement
C12P2-LDNUs overlap. see forum team comment. | Manteca-Ripon-Riverbank-Melones Area 115 kV Line Reconductoring Project | Reconductor 2.4 miles between Manteca and Ripon Jct and 1.8 miles between Riverbank SW STA and Valley Home Tap | PG&E | (blank) | Capacity | (blank) | In-Flight | 2022 | 46861 | TBD |  | 46874 | 46143 | 46143 | 2026-05-01 | 2026-05-01 | 2026-05-01 | 2028-05-31 | 2029-02-02 | 0 | Q1-2024: Project ISD delayed due to schedule/construction sequencing date adjustments
Impact to C14 | Morro Bay MPAC | New 230kV MPAC building relocates 230kV equipment from existing Control Building | PG&E | n/a | Reliability | MPAC | Deferred | 2014 | 2027-10-29 |  |  | n/a | n/a | 2027-03-09 | 2027-05-06 | 2027-05-06 | 2028-05-30 | 2029-05-25 | 2029-05-25 | 0 | Q1-2024: Project remains deferred. Not Yet triggered by Generation. This project is part of sequenced upgrades related to Mesa Sub, Diablo Canyon SS, and Cal Flats SS. Long lead material expected Q3 2025. Final in-service date tied to multiple orders for the overall upgrades.
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 overstress | Replace Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2018 | 2025-09-15 |  | 2025-05-31 | 2025-05-29 | 2025-05-21 | 2026-02-17 | 2025-05-13 | 2026-02-26 | 2025-09-23 | 2027-05-01 | 2029-05-30 | 2195 | Q1-2024: Delivery date has been changed for 4 CBs. Original planned arrival Nov 2024, now March 2025. Delays the ISD of Dec 2026 to May 2027. Working through contracts for breaker orders. ISD at risk due to new lead times on 230kV breakers. 4-1/2 years
21rsmt-5 | Palo Alto 115 kV circuit breakers 412 and 442 overstress | Replace Palo Alto 115 kV circuit breakers 412 and 442 with 63 kA interrupting capability | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2027-04-19 |  | 45565 | 2025-03-27 | 2026-06-10 | 2027-11-08 | 2027-11-08 | 2027-11-08 | 2027-11-08 | 2029-03-29 | 2029-10-18 | 250 | Q1-2024: Project restarted with planned engineering completion in 2024. Project will plan to order materials during the scoping phase.
C13P1-KPN02 | Convert Midway Substation 230 kV Bus D to BAAH | Convert Midway Substation 230 kV to BAAH in order to install bus reactors & RAS | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2016 | 46456 |  |  |  |  | 45772 | 2025-04-25 | 2025-04-25 | 2025-05-08 | 2027-12-27 | 2030-02-28 | 0 | Q1-2024: Project is in the process of developing circuit breaker orders and is subject to significant 230kV Circuit Breaker lead times with supplier estimates of 3 years. Resuming project scheduled activities in March.
C13P1-KPN02 | Midway Substation 230 kV bus and 27 circuit breakers overstress | Install 2 x 16 ohm series bus reactors between Midway Substation 230 kV bus sections D and E (16 ohm parallel / 8 ohm net) | PG&E | C13 | Reliability | SCD overstress | Not Triggered | [12 empty] | 0 | Q1-2024: Being triggered in Q1 2024 by new Agreement. New ISD TBD pending Project Setup, Funding, and Preliminary Scheduling.

## SCE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Serivce July 2022 TDF | Expected In-Service Oct TDF 2022 | Expected In-Service January TDF 2023 | Expected In-Service April TDF 2023 | Expected In-Service July TDF 2023 | Expected In-Service Oct TDF 2023 | Expected In-Service Jan TDF 2024 | Agregate MW in Queue with Executed LGIA | Notes
SCE-C10P2-E-R3 | West of Colorado River CRAS Inland/Devers Extension - monitoring infrastructure | Infrastructure to convert the formally referred to as the New Devers RAS and the Inland RAS to centralized RAS platform | SCE | C10 Phase II | RNU | RAS/CRAS | Execution | 2021-01-01 | N/A | 43435 | 44470 | Aug-25 | 44986 | 44986 | 45078 | 45192 | 45192 | 2024-03-01 | 2024-03-01 | 4438 | No ISD change between Oct 2023 TDF and Jan 2024 TDF
SCE-C11P2-N-L1 | Pardee – Pastoria – Warne 220 kV T/L rating increase | Upgrade terminal equipment and fix ground clearance for Pardee – Pastoria- Warne 230kV line | SCE | C11 Phase II | LDNU | Capacity Increase | Design | TBD | N/A | 44013 | 44849 | 45170 | 45078 | 45078 | 45383 | 45078 | 2023-10-30 | 2024-03-29 | 2024-03-29 | 126 | Expected Construction Start TBD based on outage availability dates.
SCE-C9C10-N | Windhub AA Bank cRAS - monitoring infrastructure | Windhub AA Bank cRAS - monitoring infrastructure | SCE | 2021 Reassessment | GRNU | RAS/CRAS | Execution | 2023-01-01 | N/A | 44409 | 44866 | 44958 | 44958 | 44958 | 44986 | 45046 | 2023-12-31 | 2023-09-01 | 2024-12-31 | 1800 | ISD change due to high number of customers being added to the Tehachepi CRAS in Q2-2024 and to reduce potential cascading impacts to CRAS testing queue for 2024.
SCE-C9P2-N-R1 | Whirlwind AA Bank CRAS Monitoring Infrastructure | Implement Whirlwind AA Bank CRAS - monitoring infrastructure | SCE | 2018 Reassessment | GRNU | RAS/CRAS | Execution | 2023-08-01 | N/A | 44013 | 44866 | 44958 | 44958 | 44958 | 45078 | 45078 | 2024-03-30 | 2024-06-01 | 2024-12-31 | 1014.87 | ISD change due to high number of customers being added to the Tehachepi CRAS in Q2-2024 and to reduce potential cascading impacts to CRAS testing queue for 2024.
SCE-TCP2-EOP-R4 | Lugo - Victorville RAS | Trip generation for Eldorado area 500kV line outages. | SCE | TC Phase II | RNU | RAS/CRAS | Permitting | 2024-04-01 | N/A | 40787 | 44166 | 45047 | 45047 | 45047 | 45261 | 45261 | 2024-04-30 | 2024-06-30 | 2024-12-31 | 530 | Agency approval delays have pushed the construction start date to April 2024
SCE-C12P2-N-R3 | Moorpark CRAS: monitoring infrastructure | New Moorpark CRAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | Pending | N/A | 44378 | 45474 | 45474 | 45474 | 45474 | 45474 | Pending | 2025-10-15 | 2025-10-15 | 2025-10-15 | 635 | No ISD change between Oct 2023 TDF and Jan 2024 TDF
SCE-C12P2-N-R2 | Tehachapi CRAS: monitoring infrastructure addition | Add N-1 to RAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | 2025-01-01 | N/A | 44228 | 2024-09-01 | 2024-09-01 | 2024-09-01 | 2024-09-01 | 2025-04-01 | 2025-04-01 | 2025-11-01 | 2026-03-01 | 2026-03-01 | 2700 | No ISD change between Oct 2023 TDF and Jan 2024 TDF
SCE-C9P2-NOL-R1 | New North of Lugo RAS - Backbone Portion | New North of Lugo RAS combining HDPP RAS and Calcite RAS | SCE | C9 Phase II | RNU | RAS/CRAS | Design | 2025-06-01 | N/A | 43040 | 2024-06-01 | 2024-06-30 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2026-06-01 | 2026-06-01 | 2026-06-01 | 650 | No ISD change between Oct 2023 TDF and Jan 2024 TDF
SCE-C11P2-EOP-R1 | Lugo - Victorville CRAS - monitoring infrastructure | Infrastructure to convert the Lugo - Victorville RAS to centralized RAS platform | SCE | C11 Phase II | GRNU | RAS/CRAS | Design | 2025-06-01 | N/A | 43770 | 2024-06-01 | Jun-25 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-30 | 2025-06-01 | 2026-06-30 | 950 | Project sequencing and outage constraints has slipped the construction start to 2025.
SCE-C72021-EOP | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | SCE | 2021 Reassessment | RNU | RAS/CRAS | Design | 2025-06-01 | N/A | 44409 | 2025-06-01 | 2025-06-30 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2026-06-30 | 550 | Project sequencing and outage constraints has slipped the construction start to 2025.
SCE-C11P2-E-R1 | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub | SCE | C11 Phase II | RNU | RAS/CRAS | Design | Pending | N/A | 43891 | 2026-10-01 | 2026-10-01 | 2026-10-01 | 2026-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 865 | No ISD change between Oct 2023 TDF and Jan 2024 TDF
PIN8483-RNU | South of Vincent CRAS | Add lines south of Vincent to the Tehachapi CRAS | SCE | C13 Phase II | RNU | RAS/CRAS | Design | 2026-01-12 | N/A | 2021-12-31 | 2026-04-30 |  |  | New | 2026-02-01 | 2026-02-01 | 2026-02-01 | 2027-12-15 | 2027-12-15 | 800 | No ISD change between Oct 2023 TDF and Jan 2024 TDF
PIN6902 | Calcite Substation | New four position 220 kV switchrack | SCE | Serial LGIP | GRNU | New Substation | Plan/Analyze | 2026-06-01 | 2025-04-01 | 44165 | 2024-01-31 |  |  | New | TBD | TBD | 2027-03-01 | 2027-03-01 | 2027-12-31 | 400 | Interconnection Customer's CEQA lead agency (County of San Bernardino) plans to recirculate the DEIR to properly and correctly cover and analyze proposed SCE Calcite Substation.
SCE-C10P2-E-R3 | WOCR CRAS Inland/Devers Extension Monitoring (QC10) at Alberhill Sub | WOCR CRAS Inland/Devers Extension Monitoring (QC10) at Alberhill Sub | SCE | C10 Phase II | RNU | RAS/CRAS | Design | Pending | N/A | 43435 | 2025-08-01 | 2025-08-01 | 2025-08-01 | 2027-04-01 | TBD | TBD | TBD | 2029-06-01 | 2029-06-01 | 4438 | No ISD change between Oct 2023 TDF and Jan 2024 TDF

## SDGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service July 2022 TDF | Expected In-Service October 2022 TDF | Expected In-Service January TDF 2023 | Expected In-Service Date April TDF 2023 | Expected In-Service July 2023 TDF | Expected In-Service Oct 2023 TDF | Current Estimated In-Service Jan 2024 TDF | Notes
SDGE-EXISTING-RNU-01 | Imperial Valley Existing/Modified RAS' | Imperial Valley Existing/Modified RAS' | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-7.1 | Existing Miguel BK 80 / 81 | Existing Miguel BK 80 / 81 | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-02 | Existing Otay Mesa RASs | Existing Otay Mesa RASs | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-04 | Existing ECO/BUE anti-islanding scheme for radial generators | Existing ECO/BUE anti-islanding scheme for radial generators | SDGE |  | PNU |  | Operational
SDGE-C11-PHII-RNU-02 | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | SDGE | C11 Phase II | PNU | Reliability | Operational |  | N/A | N/A | 2022-06-01 | 2022-06-01 | 2022-06-01 | 2022-06-18 | 2022-07-18 | 2022-06-18 | 2022-07-18 | 2022-06-18 | 2022-06-18 | In-Service | Placed in service on 6/18/22
SDGE-C08-PHII-RNU-03.1 | TL680 OLS | Overload Scheme to protect TL680C. Previously named as Modify TL684 RAS. | SDGE | C8 Phase II | GRNU | Deliverability | Operational |  | N/A | 2023-06-23 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-04-01 | In-Service | In-Service | In-Service | Placed in service on 3/30/23
SDGE-C07-PHI-RNU-01 | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | SDGE | C7 Phase I | PNU | Reliability | Operational |  | N/A | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 |  | 2023-06-01 | 2023-06-23 | 2023-08-23 | 2023-08-20 | 2023-08-20 | Placed in service 8/20/23
SDGE-C08-PHII-RNU-04 | Participate in the proposed RAS to protect TL23003 & TL23011 Encina to San Luis Rey 230 kV lines (Proposed grouping RAS to protect Encina/Pen/San Luis Rey 230kV Lines) | Proposed RAS to Protect TL23003 Encina - San Luis Rey 230 kV line | SDGE | C8 Phase II | PNU | [6 empty] | 2023-06-01 | 2023-06-01 | 2023-06-01
SDGE-PRE-AMEND-RNU-01.2 | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | SDGE |  | CANU-GR | [6 empty] | 2023-06-01 | 2023-06-01 | 2023-06-01

## GLW-VEA
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service July 2022 TDF | Expected In-Service Oct 2022 TDF | Expected In-Service Jan 2023 TDF | Expected In-Service April 2023 TDF | Expected In-Service July 2023 TDF | Expected In-Service Oct 2023 TDF | Expected In-Service Jan 2024 TDF | Agregate MW in Queue with Executed LGIA | Notes
VEA-C6P2-EOP-R5 | VEA Vista RAS | VEA Vista RAS: Install a new RAS to protect Jackass Flats - Mercury Switch 138 kV line under contingency conditions | VEA | C6 Phase II | RNU | Thermal | Cancelled | N/A | N/A | N/A | N/A | 2022-09-30 | 2022-11-22 | [8 empty] | Project was replaced by upgrading the Jackass Flats - Mercury Switch 138kV line. This project is completed.
VEA-C8P2-VEA-R2 | Innovation RAS | Install a new Innovation RAS | GLW | C8 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 | Complete | Complete | 1547 | Project completed.
VEA-C9P2-EOP-R3 | Innovation RAS (VEA-GLW portion) | New Innovation RAS (include Desert View RAS from QC8) to trip generation under N-1 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 | Complete | Complete | 1547 | Project completed.
VEA-C9P2-EOP-R4 | Sloan Canyon RAS (fka Bob RAS - VEA-GLW portion) | New Sloan Canyon RAS to trip generation under N-1 and N-2 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 | Complete | Complete | 1547 | Project completed.
GLW-2021-EOP-L1 | Trout Canyon - Sloan Canyon 230kV line upgrade | Trout Canyon - Sloan Canyon 230kV line upgrade | GLW | 2021 Reassessment | LDNU |  |  |  |  | N/A | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | N/A | 2027-12-31 | 2027-12-31 | N/A | The Trout Canyon – Sloan Canyon 230kV Line Upgrade is part of the GLW Upgrade Project which was approved through the 2021-2022 TPP and revised in the 2022-2023 TPP to 500kV DCTL.