## PGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Trigger Year | Current Expected Construction Start | Expected CPUC Permit Application | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service Jul 2022 TDF | Expected In-Service Oct 2022 TDF | Expected In-Service Jan 2023 TDF | Expected In-Service Apr 2023 TDF | Expected In-Service Jul 2023 TDF | Expected In-Service Oct 2023 TDF (Current) | Agregate MW in Queue with Executed LGIA | Notes
20rsmt-3 | Midway 230 kV Bus Section E overload mitigation | Replace limiting conductor and/or fittings on Bus Section E to achieve 3372 A min. rating | PG&E | RA-20 | Reliability | Bus Flow | In-Service | 2021 |  |  | 2022-09-30 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 2022-07-31 | 409.7 | In-Service
20rsmt-7a | Tesla 500 kV circuit breaker 632 overstress | Replace Tesla 500 kV circuit breaker 632 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Service | 2021 | 2021-12-03 |  | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 2021-12-03 | 850 | In-Service
21rsmt-4 | Monta Vista 115 kV circuit breaker 1322 overstress | Replace Monta Vista 115 kV circuit breaker 1322 | PG&E | RA-21 | Reliability | SCD overstress | In-Service | 2021 | 2021-10-01 |  | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 2021-10-31 | 1200 | In-Service
22rsmt-3 | Metcalf 230 kV Substation Circuit Breaker #No 292 Upgrade | Upgrade Metcalf Circuit Breaker #292 due to overstress issues | PG&E | (blank) | Capacity | (blank) | In-Service | 2022 |  |  |  | 45658 | 45992 | 2022-09-27 | 2022-09-27 | 2022-09-27 | 2022-09-27 | 2022-09-27 | 1395 | In-Service
C11P2-FC01 | Midway 500kV CB's 722 Overstress | Midway Sub: Replace 500kV CB's 722, SW's and Relays | PG&E | C11 | Reliability | SCD overstress | In-Service | 2021 | 2022-09-30 |  | 2025-12-31 | 2025-12-31 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2100.1 | In-Service
C11P2-FP01 | Midway 500 kV circuit breakers 732, 802, 832 and 842 overstress | Replace Midway 500 kV circuit breakers 732, 802, 832 and 842 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Service | 2021 | 2022-12-31 |  | 2022-09-30 | 2025-12-31 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2022-08-30 | 2100.1 | In-Service
C12P1-NPN02 | Lodi Substation 60 kV circuit breakers 12 and 22 overstress | (blank) | PG&E | C12 | Reliability | SCD overstress | In-Service | 2011 | 2020-08-04 |  | 2022-03-28 | 2022-12-29 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 2022-05-20 | 0 | In-Service
C12P2-GRNU3 | Midway Substation 500 kV CB 712 overstress | Replace Midway Substation 500 kV CB 712 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Service | 2021 | 2022-12-31 |  | 2025-12-31 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 2022-02-15 | 1800 | In-Service
C12P2-KC01 | Midway Substation 500kV CB 722 Overload mitigation | Replace Midway 500 kV CB 722 to achieve 3600 A emergency rating | PG&E | C12 | Reliability | Bus Flow | In-Service | 2021 | 2022-12-31 |  | 2025-12-31 | 2025-12-31 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 2022-09-30 | 3231.05 | In-Service
C12P2-PNU-02 | Gates 230 kV circuit breakers 352, 362 and 372 overstress mitigation (Cap Banks) | Replace Gates 230 kV circuit breakers 352, 362 and 372 with 63 kA interrupting capability | PG&E | C12 | Reliability | SCD overstress | In-Service | 2022 | 2022-10-24 |  | 2023-04-30 | 2023-03-31 | 2023-03-31 | 2023-04-06 | 2023-04-06 | 2023-05-23 | 2023-07-14 | 2023-07-12 | 2992.67 | In-Service
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | Metcalf Substation 230 kV capacitor circuit breakers Interim Solution | PG&E | C13 | Reliability | SCD overstress | In-Service | 2018 | 44844 |  | 45808 | 44832 | 44896 | 44902 | 44866 | 44866 | 44866 | 44866 | 2195 | In-Service
C13P2-GGR01 | Tesla 500 kV circuit breakers 622 overstress | Replace Tesla 500 kV circuit breaker 622 with 63 kA interrupting capability. Only went to 50 kA | PG&E | C13 | Reliability | SCD overstress | In-Service | 2021 | [7 empty] | 2021-12-20 | 2021-12-20 | 2021-12-20 | 400 | In-Service
C8P1-35 | Re-conductor Los Banos-Quinto SS 230 kV Line | Re-conductor 6.11 mi Quinto Sw Sta-Los Banos 230 kV Line with super bundled 795 ACSS | PG&E | C8 | Deliverability | Re-conductor | In-Service | 2017 | 2022-03-03 |  | 2022-05-31 | 2023-05-16 | 2023-05-16 | 2023-05-16 | 2023-04-28 | 2023-05-10 | 2023-05-08 | 2023-05-08 | 1110.62 | In-Service
C8P2-6 | Re-conductor Los Banos-Q779 SS #1 230 kV Line | Re-conductor 4.5 mi Los Banos-Padre Flat SS #1 230 kV Line with 1113 ACSS and upgrade equipment to 1900 A. | PG&E | C8 | Deliverability | Re-conductor | In-Service | 2017 | 2022-10-24 |  | 2023-03-01 | 2023-02-28 | 2023-02-28 | 2022-12-14 | 2022-12-24 | 2022-12-24 | 2022-12-24 | 2022-12-24 | 632 | In-Service
C9P2-F13-F15 | Gates 230kV Bus Section E and CB 312, 322, 2102, 2202 overload mitigation (BAAH) | Gates Substation 230 kV circuit breakers 312, 322, 2102, 2202 overload – convert bus section E to BAAH and move Panoche-Gates #1 and #2 230 kV lines and Q1117/Q1120/Q1139/Q1242/Q1243 into bus section E | PG&E | C9 | Reliability | Bus Flow | In-Service | 2019 | 44414 |  | 45016 | 44999 | 45077 | 44999 | 45069 | 45077 | 45033 | 45033 | 1993.95 | In-Service
C9P2-N09 | Re-conductor Stockton A-Weber #3 60 kV Line (Stockton A-Hazelton Jct) | Re-conductor 0.9 mi of Stockton A-Weber #3 60 kV Line from Stockton A to Hazelton Jct Pole 000/026 with 715 AAC. | PG&E | C9 | Deliverability | Re-conductor | In-Service | 2018 | 2022-01-14 |  | 44651 | 44620 | 44620 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 2022-02-28 | 25 | In-Service
C13P1-GPN06 | Birds Landing 230 kV CBs 422, 222, 412, 212 Overload Mitigation | Upgrade Birds Landing Sw Sta 230 kV bays 1 and 2 to 3000 A equipment and replacing 6 circuit breakers and associated switches/relays | PG&E | C13 | (blank) | (blank) | Removed | [11 empty] | 0 | Removed
C13P2-FPT04 | Jackson Switching Station (CHSR Site 10) | (blank) | PG&E | C13 | (blank) | (blank) | Removed | [11 empty] | 0 | Removed
C13P2-FPT05 | CHSR Site 8 | (blank) | PG&E | C13 | (blank) | (blank) | Removed | [11 empty] | 0 | Removed
C9P2-F17 | Panoche 115 kV circuit breakers 152 overstress | Replace Panoche 115 kV circuit breaker 152 and associated switches/relays | PG&E | C9 | Reliability | SCD overstress | Removed | [11 empty] | 0 | Removed
(blank) | Morro Bay MPAC | New 230kV MPAC building relocates 230kV equipment from existing Control Building | PG&E | n/a | Reliability | MPAC | In-Flight | 2014 | 2027-10-29 |  |  | n/a | n/a | 2027-03-09 | 2027-05-06 | 2027-05-06 | 2028-05-30 | 2029-05-25 | 0 | Q4-2023: Reprioritization. There are no current dependent Generation projects triggering this work. In-service date is estimated subject to being triggered by a new generation project.
?? | Tesla MPAC | New 230kV MPAC building relocates 230kV equipment from existing Control Building | PG&E | n/a | Reliability | MPAC | In-Flight | 2018 | 45812 |  |  | n/a | n/a | 45574 | 46022 | 46022 | 46022 | 46022 | 0 | Q4-2023: Reprioritization. Impacted Interconnections to be planned to be installed in the existing control building. Future cluster projects connecting to Tesla Sub to require this upgrade.
19rsmt-3 | Schindler 70kV Bus Normal & Outage Overload | Upgrade Schindler 70 kV Bus to 1113 kcmil AAC | PG&E | RA-19 | Reliability | Bus Flow | Not Triggered | [11 empty] | 0 | Q4-2023: Not triggered
20rsmt-4 | Metcalf 115kV breakers Overstress (almost all breakers) | Install 4-3 ohm reactors at low side of Metcalf 115 kV 230kV Transformers | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 2026-03-13 |  | 2025-02-28 | 2025-08-22 | 2025-09-03 | 2025-11-04 | 2026-01-29 | 2026-02-05 | 2026-07-10 | 2027-05-01 | 1145 | Q4-2023: Delivery date has been changed for 4 CBs that we have on order for Metcalf. Original planned: Nov 2024, now March 2025. Delays the ISD of Dec 2026 to May 2027
20rsmt-5 | Tesla 500 kV circuit breaker 612 overstress | Replace Tesla Substation 500 kV CB 612 and associated switches/relays | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 2024-10-01 |  | 2024-03-01 | 2024-05-28 | 2024-07-05 | 2024-08-08 | 2024-08-15 | 2024-10-28 | 2025-06-30 | 2025-02-17 | 850 | Q4-2023: Portions of this work cannot complete until work on CB542 and CB642 due to operational constrains. Requires a significant 500kV clearance at the same time. A shoofly is being considered to mitigate clearing the bank. In-Service subject to change as clearances are finalized.
20rsmt-6 | 20RSMTRAS-02 (Reliability) to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | 20RSMTRAS-02 RAS to open Bitterwater Sw Sta-Wheeler Ridge #2 230 kV Line for loss of Midway-Bitterwater 230 kV line and overload on the Midway-Wheeler Ridge #1 230 kV line. | PG&E | RA-20 | Reliability | RAS (Reliability) | In-Flight | 2020 | 2024-10-11 |  | 2023-12-31 | 2023-12-29 | 2023-12-29 | 2023-10-31 | 2023-12-31 | 2024-11-14 | 2024-11-14 | 2025-04-08 | 100 | Q4-2023: Planned materials due to be received October 2023. This project has a planned release to construction in August 2024. This project deferred work due to Long Lead Material Constraints and an Interim solution by the triggering project.
20rsmt-7b | Tesla 500 kV circuit breakers 542 and 642 overstress | Replace Tesla 500 kV circuit breakers 542 and 642 with 63 kA interrupting capability | PG&E | RA-20 | Reliability | SCD overstress | In-Flight | 2020 | 2024-01-05 |  | 2024-07-31 | 2023-09-20 | 2024-04-12 | 2024-07-05 | 2024-07-12 | 2024-09-24 | 2024-11-20 | 2024-05-07 | 2680 | Q4-2023: Construction sequencing complete. Release to construction Oct 2023 subject to change pending receipt of long lead materials. In-Service subject to change as clearances are finalized.
21rsmt-1 | Henrietta Substation 70kV CBs 12 and 72 Overstress | Henrietta Sub: Replace 70kV CB 12 & 72 and switches. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2025-07-14 |  | 2025-12-31 | 2026-06-16 | 2025-02-26 | 2026-09-14 | 2026-10-07 | 2026-10-07 | 2026-10-07 | 2026-10-07 | 0 | Q4-2023: Reprioritization. There are no current dependent Generation projects triggering this work. In-service date is estimated subject to being triggered by a new generation project. In-service date is also currently under review and is subject to change. In the first TDF of 2024, the earliest achievable In-service date will be updated.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 1 - incl CB282) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2021-07-09 |  | 2026-02-28 | 2023-12-05 | 2023-12-05 | 2025-12-05 | 2025-12-05 | 2025-12-05 | 2025-12-05 | 2025-03-01 | 200 | Q4-2023: Reprioritization. Project has been removed as a dependency on active generation projects. Project is resuming activities in Jan 2024.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 3 - incl CB262) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2026-01-01 |  | 2026-02-28 | 2024-10-16 | 2024-10-16 | 2026-12-07 | 2026-12-07 | 2026-12-07 | 2026-12-07 | 2026-12-01 | 200 | Q4-2023: Reprioritization. Project has been removed as a dependency on active generation projects. Project is resuming activities in Jan 2024.
21rsmt-3 | Kern PP Substation 115 kV CBs 182, 262 and 282 overstress (BAAH Conversion Phase 4) | Kern PP Sub: Existing PG&E 115 kV BAAH conversion project will cover this replacement. | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2027-11-01 |  | 2026-02-28 | 2023-02-01 | 2023-04-11 | 2024-11-12 | 2024-11-12 | 2024-11-12 | 2024-11-12 | 2028-02-01 | 200 | Q4-2023: Reprioritization. Project has been removed as a dependency on active generation projects. Project is resuming activities in Jan 2024.
21rsmt-5 | Palo Alto 115 kV circuit breakers 412 and 442 overstress | Replace Palo Alto 115 kV circuit breakers 412 and 442 with 63 kA interrupting capability | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2021 | 2026-09-28 |  | 45565 | 2025-03-27 | 2026-06-10 | 2027-11-08 | 2027-11-08 | 2027-11-08 | 2027-11-08 | 2029-03-29 | 250 | Q4-2023: Reprioritization. This project is in engineering with issue for construction coming in Q1 2024. In-service date is subject to long lead material and construction/sequence dependencies.
21rsmt-SCD-23 | El Cerrito G 115kV CB 112, 142, 132 Overstress | Replace Overstressed Circuit Breakers | PG&E | RA-21 | Reliability | SCD overstress | In-Flight | 2011 | 45303 |  |  | 2024-07-18 | 2024-07-17 | 2025-11-14 | 2025-12-26 | 2025-12-26 | 2025-12-26 | 2025-05-01 | 0 | Q4-2023: 2024 Reprioritization. There are no current dependent Generation projects triggering this work
22rsmt-4 | New 230 kV switching station to loop Dos Amigos – Panoche # 3 230 kV | Build a new 2 bay 230 kV BAAH switching station to loop in the Dos Amigos – Panoche # 3 230 kV Line requiring access road, land and land rights acquisition and permitting, remote end protection upgrades, and OPGW/fiber telecommunication work | PG&E | RA-22 | Deliverability | New Station | Initiating |  |  |  |  | n/a | n/a | 2028-12-31 | 2028-12-31 | 2028-12-31 | 2028-12-31 | 2028-12-01 | 632 | Q4-2023: Project Authorization and funding are approved and project is proceeding into scoping and engineering activities starting in Fall 2023.
C11P2-ND01 | Re-conductor Fulton-Hopland 60 kV Line (Fitch Mountain Tap-Geysers Jct) | Re-conductor Fulton-Hopland 60 kV Line (Fitch Mountain Tap 009/005A-Geysers Jct 016/004) ~7 mi total length with 715 AAC | PG&E | C11 | Deliverability | Re-conductor | In-Flight | 2018 | 2025-10-29 | 2024-09-30 | 2026-03-31 | 2027-12-31 | 2027-12-31 | 2025-11-03 | 2026-02-13 | 2026-05-25 | 2026-06-05 | 2026-04-28 | 230 | Q4-2023: Schedule adjustments due to land acquisitions, permitting, and construction sequencing. Dates subject to change until permitting and land acquisitions are completed. NOC permit is required to meet current ISD. If a PTC is required, the OPDAT will need to push out.
C11P2-ND03 | North Dublin-Cayetano 230 kV Line | Reconductor North Dublin-Cayetano 230 kV Line 2.63 miles OH Line & 2.82 UG cable with new UG cable 797 MVA/2000 A | PG&E | C11 | Deliverability | Re-conductor | In-Flight | 2021 | 2024-12-23 | 45231 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-03-25 | 2025-03-25 | 2025-02-10 | 2025-03-24 | 2025-03-25 | 90.8 | Q4-2023: Clearance constraints is the most significant risk to delivering the ISD. The project team is aware of multiple projects which may ask for overlapping conflicting clearances in late 2024/early 2025.
C11P2-NP01 | Contra Costa 230kV SW's 601, 603 overload | Contra Costa PP: Replace 230kV SW's 601 & 603 and jumpers. | PG&E | C11 | Reliability | Bus Flow | Replaced by T.0008048 Line Relo Project | 2021 | 2024-12-30 |  | 2025-12-31 | 2025-12-31 | 2025-07-07 | 2025-05-02 | 2025-05-30 | 2025-05-23 | 2025-05-22 | 2025-05-23 | 0 | Q4-2023: See C11P2-NP02, C11P2-NP01 Line Reconfiguration notes
C11P2-NP02 | Contra Costa 230kV Bus Sections D, E and F and circuit breaker 820 overload | Contra Costa PP: Reconductor Bus Sections D, E and F. Replace circuit breaker 820. | PG&E | C11 | Reliability | Bus Flow | Replaced by T.0008048 Line Relo Project | 2021 | 2024-12-30 |  | 2025-12-31 | 2025-12-31 | 2025-07-07 | 2025-05-02 | 2025-05-30 | 2025-05-23 | 2025-05-22 | 2025-05-23 | 490.8 | Q4-2023: See C11P2-NP02, C11P2-NP01 Line Reconfiguration notes
C11P2-NR01 | Cottonwood Substation 230 kV circuit breakers 222, 232, 242 overstress | Replace Cottonwood Substation 230 kV circuit breakers 222, 232, 242 and associated switches/relays | PG&E | C11 | Reliability | SCD overstress | In-Flight | 2022 | 2026-03-05 |  | 2024-02-28 | 2024-04-02 | 2024-05-24 | 2025-08-28 | 2025-08-28 | 2025-03-07 | 2025-05-22 | 2025-05-22 | 500 | Q4-2023: Reprioritization. This project had been reprioritized but will be realigned with other Cottonwood breaker replacement work. It is understood that the project to replace the CBs will utlize the existing 230kV relays until the 230kV MPAC project is complete. The ISD is under review and is subject to change as project is set to re-start in 2024 long lead material receipt date is determined. Long lead materials have not yet been ordered. The ISD will be updated in the first TDF of 2024.
C12P1-GCR01 | Moraga 115 kV circuit breakers 582, 612, 622, 642 and 712 overstress | Replace Moraga 115 kV circuit breakers 582, 612, 622, 642 and 712 | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2022 | 2025-03-06 |  | 2026-10-01 | 2027-01-01 | 2028-11-23 | 2029-10-10 | 2028-11-23 | 2028-11-23 | 2028-11-23 | 2028-11-23 | 220 | Q4-2023: Reprioritization. A triggering Interconnection project has signed requiring this project however that project has gone into suspension. The in-service date is currently under review and subject to change. In the first TDF of 2024, the earliest achievable In-service date will be updated.
C12P1-GPT01 | Ames Distribution 115 kV circuit breaker 132 overstress | Replace Ames Distribution 115 kV circuit breaker 132 | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2019 | 2026-02-11 |  | 2024-03-31 | 2024-06-14 | 2024-08-22 | 2026-03-10 | 2026-03-10 | 2026-03-10 | 2026-03-10 | 2028-03-10 | 450 | Q4-2023: Reprioritization. Project is set to resume in 2024. In the first TDF of 2024, the earliest achievable In-service date will be updated. Current estimated ISD is March 2028; however, in-service date is currently under review as the project sequencing take place after the issue for construction documents are made available and long lead material arrival date is determined.
C12P1-NPT01 | Gold Hill Substation 115 kV circuit breakers 142 and 172 overstress | Replace Gold Hill Substation 115 kV circuit breakers 142 and 172 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2021 | 2024-03-13 |  | 2023-09-30 | 2024-01-04 | 2023-11-13 | 2025-07-02 | 2025-08-28 | 2025-01-28 | 2025-01-01 | 2025-01-01 | 49.9 | Q4-2023: Reprioritization. Deferred until dependent generation project emerges from suspension. In-service date is currently under review and is subject to change. In the first TDF of 2024, the earliest achievable In-service date will be updated.
C12P1-NPT03 | Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 overstress | Replace Rio Oso Substation 115 kV circuit breakers 412, 422, 482, 522 and 542 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2020 | 2021-06-01 |  | 2024-12-31 | 2024-12-31 | 2023-11-10 | 2024-05-01 | 2024-12-31 | 2024-09-30 | 2024-09-30 | 2024-12-31 | 49.9 | Q4-2023: Project was listed as reprioirtized however, this project is underway in construction with a planned In-service in Q4 2024 for the new MPAC and 230kV GIS. Each breaker is installed in sequence. In-service is subject to changes due to weather, construction resources, and operational constraints.
C12P1-NPT04 | Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 overstress | Replace Vaca Dixon Substation 230 kV circuit breakers 442, 452 and 462 and associated switches/relays | PG&E | C12 | Reliability | SCD overstress | Initiating | 2021 | 2025-11-05 |  | 2024-03-31 | 2024-06-27 | 2024-12-02 | 2025-03-06 | 2025-05-20 | 2025-08-14 | 2025-10-16 | 2025-10-16 | 1840.8 | Q4-2023: Reprioritrization - previous note was inacurate as funding was not available to perform scoping in 2023. Funding resumes in Jan 2024. Long lead material times drive the in-service date as will construction sequencing for clearing each breaker one at a time. Construction start planned Feb 2027 subject material lead times. The in-service date is currently under review and subject to change. In the first TDF of 2024, the earliest achievable in-service date will be updated.
C12P2-GRNU2 | Gates Substation 230 kV Bus Overstress | Install series bus reactors between Gates Substation 230 kV bus sections E and F | PG&E | C12 | Reliability | SCD overstress | In-Flight | 2022 | 2024-10-01 |  | 2025-12-01 | 2025-12-01 | 2025-12-31 | 2025-03-31 | 2025-03-31 | 2025-03-31 | 2024-05-31 | 2026-04-30 | 2300 | Q4-2023: In-Service delayed to April 2026 due to 42 week lead time on bushing capacitors. Starting foundation work in 2023. Construction resumes October of 2024 on BUS 1 scope until April of 2025. In October of 2025 work continues on BUS 2 until April of 2026.
C12P2-LDNU1 | Ripon-Manteca 115 kV Line Reconductor | Reconductor Ripon-Manteca 115 kV line 1.51 mi section of 2/0 CU and 0.92 mi 4/0 ACSR (2.43 mi total) | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2026-04-06 | 2025-02-03 | 2027-12-31 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2028-09-11 | 2027-04-19 | 2027-05-10 | 99 | Q4-2023: No date changes at this time. Dates subject to change until permitting and land acquisitions are completed.
C12P2-LDNU2 | Stanislaus-Melones Sw Sta-Manteca #1 115 kV Line Reconductor | Reconductor Stanislaus-Melones Sw Sta-Manteca #1 115 kV line 25.23 miles section of various conductors from 018/115-043/277 | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2026-07-21 | 2025-05-20 | 2027-12-31 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2028-09-11 | 2028-02-29 | 2028-09-05 | 99 | Q4-2023: No date changes at this time. Dates subject to change until permitting and land acquisitions are completed.
C12P2-LDNU3 | Bellota-Riverbank-Melones Sw Sta 115 kV Line 115 kV Line Reconductor | Reconductor a total of 17 miles of Bellota-Riverbank-Melones SW STA 115 kV Line with 477 ACSS | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2027-09-10 | 2025-02-24 | 2027-12-31 | 2027-12-16 | 2027-12-31 | 2027-12-31 | 2027-12-31 | 2028-09-11 | 2028-04-12 | 2028-08-18 | 99 | Q4-2023: No date changes at this time. Dates subject to change until permitting and land acquisitions are completed.
C12P2-LDNU4 | Stanislaus-Melones SW STA-Riverbank Jct Sw Sta 115 kV Line Reconductor | Reconductor Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV Line 7.53 miles section of various conductors from 000/001-007/043 - scope taken over by the more comprehensive STAN-MELONES TAP LINES: REPL CU COND P3 project. | PG&E | C12 | Deliverability | Re-conductor | In-Flight | 2021 | 2028-03-24 |  | 2027-12-31 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2027-12-16 | 2028-09-11 | 2028-05-29 | 2028-09-07 | 99 | Q4-2023: Schedule adjustments due to land acquisitions, permitting, and construction sequencing. Dates subject to change until permitting and land acquisitions are completed.
C13P1-GPN04 | Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 overstress | Replace Metcalf Substation 230 kV capacitor circuit breakers 654, 664, 674 and 684 | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2018 | 2025-08-04 |  | 2025-05-31 | 2025-05-29 | 2025-05-21 | 2026-02-17 | 2025-05-13 | 2026-02-26 | 2025-09-23 | 2027-05-01 | 2195 | Q4-2023: Delivery date has been changed for 4 CBs that we have on order for Metcalf. Original planned: Nov 2024, now March 2025. Delays the ISD of Dec 2026 to May 2027
C13P1-KPN02 | Midway Substation 230 kV bus and 27 circuit breakers overstress | Install 2 x 16 ohm series bus reactors between Midway Substation 230 kV bus sections D and E (16 ohm parallel / 8 ohm net) | PG&E | C13 | Reliability | SCD overstress | Not Triggered | [11 empty] | 0 | Q4-2023: Not triggered
C13P1-KPN02 | Convert Midway Substation 230 kV to BAAH | Convert Midway Substation 230 kV to BAAH in order to install bus reactors & RAS | PG&E | C13 | Reliability | SCD overstress | In-Flight | 2016 | 45475 |  |  |  |  | 2025-04-25 | 2025-04-25 | 2025-04-25 | 2025-05-08 | 2027-12-10 | 0 | Q4-2023: Reprioritization. Project due to resume activities in 2024 with an anticipated in-service date in Q4 2027; however, the date is subject to change as its currently under review. In the first TDF of 2024, the earliest achievable in-service date will be updated.
C8P1-34 | Re-conductor Padre Flat SS-Panoche #1 230 kV Line | Re-conductor 32.59 mi Q779/Padre Flat SS-Panoche #1 230 kV Line with 795 ACSS | PG&E | C8 | Deliverability | Re-conductor | In-Flight | 2017 | 2023-09-21 | 44967 | 2024-05-31 | 2024-05-21 | 2024-05-20 | 2024-05-20 | 2024-05-10 | 2024-05-10 | 2024-05-10 | 2025-05-13 | 600 | Q4-2023: Construction start Fall 2023. Partial work delayed until late 2024 due to land acquisitions.
C8P2-1 | Re-conductor Borden-Gregg #1 230 kV Line | Re-conductor 6.25 mi Borden-Gregg #1 230 kV Line with 1113 ACSS and upgrade equipment to 2000 A minimum (this is the existing Borden-Gregg 230 kV Line) | PG&E | C8 | Deliverability | Re-conductor | In-Flight | 2017 | 2026-01-30 | 45258 | 2026-01-05 | 2026-01-05 | 2026-01-05 | 46027 | 2026-01-05 | 2026-05-07 | 2026-05-07 | 2026-05-07 | 632 | Q4-2023: No date changes at this time. Dates subject to change until permitting and land acquisitions are completed.
C8P2-10 | QC8RAS-02 SPS (Deliverability Triggered RNU) | QC8SPS-02 SPS to modify the existing Hatchet Ridge SPS to trip Q1106 200 MW wind and Hatchet Ridge 102 MW wind for thermal overloads on the Q1106 SS-Cottonwood, Carberry SS-Round Mountain or Pit #3-Carberry SS 230 kV Lines. | PG&E | C8 | Deliverability | RAS (Deliverability) | Deferred | 2017 | 2028-05-23 |  | 2023-07-28 | 2023-07-28 | 2023-07-28 | TBD | 2027-03-31 | 2028-12-07 | 2028-12-07 | 2028-12-07 | 200 | Q3-2023: In-service date shown aligns with overall new Switching Station construction. Triggering Interconnection Project has suspended for 1-year
C8P2-15 | Cottonwood Substation 230 kV Circuit Breaker 522 and 542 Overstress | Cottonwood Substation 230 kV CB Overstress: Replace CB 522 & 542 (rated @ 34.5KA, overstress close-in fault is 35,179A or 2%, 679A). | PG&E | C8 | Reliability | SCD overstress | In-Flight | 2018 | 45474 |  | 2023-07-28 | 2023-08-15 | 2023-08-15 | 2024-09-30 | 2024-09-30 | 2024-09-04 | 2025-12-31 | 2025-12-01 | 700 | Q4-2023: Reprioritization. This project had been reprioritized but will be realigned with other Cottonwood breaker replacement work.
C8P2-3 | QC8RAS-08 RAS (Deliverability Triggered RNU) | QC8RAS-08 RAS to trip Generation offline for outage AND overload of either Gates 500/230 kV Transformer Bank 11 or 12 | PG&E | C8 | Deliverability | RAS (Deliverability) | In-Flight | 2017 |  |  | 2023-01-12 | 2023-01-12 | 2023-12-31 | 2024-05-03 | 2024-05-03 | 2024-05-03 | 2024-05-03 | 2024-05-03 | 2870.57 | Q4-2023: No date changes at this time.
C9P1-F11 | Re-conductor Dos Amigos PP-Panoche #3 230 kV Line | Re-conductor 23.63 mi Dos Amigos PP-Panoche #3 230 kV Line with 795 ACSS | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2017 | 2025-03-18 |  | 2025-05-14 | 2025-04-30 | 2025-04-30 | 2025-04-30 | 2025-04-30 | 2025-04-30 | 2025-05-01 | 2025-10-23 | 632 | Q4-2023: Construction starting Fall 2023. Portions of this project delayed to Fall 2024 due to land acquisitions. In-service subject to change due to land acquisition outcomes.
C9P1-F12 | Re-conductor Borden-Gregg #2 230 kV Line | Re-conductor 6.25 mi Borden-Gregg #2 230 kV Line with 1113 ACSS | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2017 | 2025-08-08 | 45258 | 2025-05-31 | 2025-05-07 | 2025-05-07 | 2025-05-07 | 2025-05-07 | 2026-01-16 | 2026-01-16 | 2026-01-16 | 632 | Q4-2023: No date changes at this time. Dates subject to change until permitting and land acquisitions are completed.
C9P2-N02 | Re-conductor Fulton-Hopland 60 kV Line (Geysers Jct-Cloverdale Jct-Hopland) | Re-conductor 24.21 mi Fulton-Hopland 60 kV Line (Geysers Jct 016/003A-Cloverdale Jct 026/002-Hopland) with 715 AAC and upgrade any limiting equipment | PG&E | C9 | Deliverability | Re-conductor | In-Flight | 2019 | 2025-10-29 | 45565 | 2027-05-31 | 2027-03-31 | 2027-12-31 | 2025-11-03 | 2026-02-13 | 2026-05-25 | 2026-06-05 | 2026-04-28 | 230 | Q4-2023: Schedule adjustments due to land acquisitions, permitting, and construction sequencing. Dates subject to change until permitting and land acquisitions are completed. NOC permit is required to meet current ISD. If a PTC is required, the OPDAT will need to push out.

## SCE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Serivce July 2022 TDF | Expected In-Service Oct TDF 2022 | Expected In-Service January TDF 2023 | Expected In-Service April TDF 2023 | Expected In-Service July TDF 2023 | Expected In-Service Oct TDF 2023 | Agregate MW in Queue with Executed LGIA | Notes
PIN6902 | Calcite Substation | New four position 220 kV switchrack | SCE | Serial LGIP | GRNU | New Substation | Plan/Analyze | 46023 | Pending | 44165 | 2024-01-31 |  |  | New | TBD | TBD | 2027-03-01 | 2027-03-01 | 400 | At the request of the IC, CAISO approved suspension of the associated project. The project became active again beginning of May 2023 with a tentaive in-service date of Q2 2027. In April 2023, there was a kickoff meeting regarding another IC that has requested interconnection of its project into the proposed Calcite Substation with an estimated in-service date of Q4 2026.
PIN8483-RNU | South of Vincent CRAS | Add lines south of Vincent to the Tehachapi CRAS | SCE | C13 Phase II | RNU | RAS/CRAS | Design | 2026-01-12 | N/A | 2021-12-31 | 2026-04-30 |  |  | New | 2026-02-01 | 2026-02-01 | 2026-02-01 | 2027-12-15 | 650 | MMA In-Service Date changed from 4/15/26 to 1/15/27. Expected Material delivery date pushed out the project completion date.
SCE-C10P2-E-R3 | West of Colorado River CRAS Inland/Devers Extension - monitoring infrastructure | Infrastructure to convert the formally referred to as the New Devers RAS and the Inland RAS to centralized RAS platform | SCE | C10 Phase II | RNU | RAS/CRAS | Execution | 2021-01-01 | N/A | 43435 | 44470 | Aug-25 | 44986 | 44986 | 45078 | 45192 | 45192 | 2024-03-01 | 4438 | Delay due to CRAS Test resources
SCE-C10P2-E-R3 | WOCR CRAS Inland/Devers Extension Monitoring (QC10) at Alberhill Sub | WOCR CRAS Inland/Devers Extension Monitoring (QC10) at Alberhill Sub | SCE | C10 Phase II | RNU | RAS/CRAS | Design | Pending | N/A | 43435 | 2025-08-01 | 2025-08-01 | 2025-08-01 | 2027-04-01 | TBD | TBD | TBD | 2029-06-01 | 4438 | Delay due to Alberhill Project licensing
SCE-C11P2-EOP-R1 | Lugo - Victorville CRAS - monitoring infrastructure | Infrastructure to convert the Lugo - Victorville RAS to centralized RAS platform | SCE | C11 Phase II | GRNU | RAS/CRAS | Design | 2024-06-01 | N/A | 43770 | 2024-06-01 | Jun-25 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-30 | 2025-06-01 | 950 | There is no change in the in-service date as of 9/1/2023. However, the construction start date has been updated
SCE-C11P2-E-R1 | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub | WOCR CRAS Inland/Devers Extension Additional Monitoring (QC11) at Wildlife Sub | SCE | C11 Phase II | RNU | RAS/CRAS | Design | Pending | N/A | 43891 | 2026-10-01 | 2026-10-01 | 2026-10-01 | 2026-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 2027-10-01 | 800 | There is no change in the ISD between the July and October TDFs
SCE-C11P2-N-L1 | Pardee – Pastoria – Warne 220 kV T/L rating increase | Upgrade terminal equipment and fix ground clearance for Pardee – Pastoria- Warne 230kV line | SCE | C11 Phase II | LDNU | Capacity Increase | Design | 2023-10-01 | N/A | 44013 | 44849 | 45170 | 45078 | 45078 | 45383 | 45078 | 2023-10-30 | 2024-03-29 | 109.7285 | ISD changed to March 2024 to accommodate 220kV gen-tie scope of work change (from overhead to underground construction) to avoid existing overhead line congestion.
SCE-C12P2-N-R2 | Tehachapi CRAS: monitoring infrastructure addition | Add N-1 to RAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | 2025-01-01 | N/A | 44228 | 2024-09-01 | 2024-09-01 | 2024-09-01 | 2024-09-01 | 2025-04-01 | 2025-04-01 | 2025-11-01 | 2026-03-01 | 2550 | Project delays due to POCO location and major equipment procurement
SCE-C12P2-N-R3 | Moorpark CRAS: monitoring infrastructure | New Moorpark CRAS | SCE | C12 Phase II | GRNU | RAS/CRAS | Design | Pending | N/A | 44378 | 45474 | 45474 | 45474 | 45474 | 45474 | Pending | 2025-10-15 | 2025-10-15 | 635 | Trigger year based on GIA. Project delayed to October 2025 due to delays in associated project.
SCE-C72021-EOP | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | Participate and modify the planned Lugo-Victorville CRAS - SCE portion | SCE | 2021 Reassessment | RNU | RAS/CRAS | Design | 2024-06-01 | N/A | 44409 | 2025-06-01 | 2025-06-30 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 800 | Project construction start is delayed to June 2025 due to delay in Lugo-Victorville RAS project.
SCE-C9C10-N | Windhub AA Bank cRAS - monitoring infrastructure | Windhub AA Bank cRAS - monitoring infrastructure | SCE | 2021 Reassessment | GRNU | RAS/CRAS | Execution | 2023-01-01 | N/A | 44409 | 44866 | 44958 | 44958 | 44958 | 44986 | 45046 | 2023-12-31 | 2023-09-01 | 1800 | Project has been completed
SCE-C9P2-NOL-R1 | New North of Lugo RAS - Backbone Portion | New North of Lugo RAS combining HDPP RAS and Calcite RAS | SCE | C9 Phase II | RNU | RAS/CRAS | Design | 2025-06-01 | N/A | 43040 | 2024-06-01 | 2024-06-30 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2025-06-01 | 2026-06-01 | 2026-06-01 | 450 | There is no change in the ISD between the July and October TDFs
SCE-C9P2-N-R1 | Whirlwind AA Bank CRAS Monitoring Infrastructure | Implement Whirlwind AA Bank CRAS - monitoring infrastructure | SCE | 2018 Reassessment | GRNU | RAS/CRAS | Execution | 2023-08-01 | N/A | 44013 | 44866 | 44958 | 44958 | 44958 | 45078 | 45078 | 2024-03-30 | 2024-06-01 | 1014.87 | Delay to June 2024 due to resources / reprioritization
SCE-TCP2-EOP-R4 | Lugo - Victorville RAS | Trip generation for Eldorado area 500kV line outages. | SCE | TC Phase II | RNU | RAS/CRAS | Permitting | 45292 | N/A | 40787 | 44166 | 45047 | 45047 | 45047 | 45261 | 45261 | 2024-04-30 | 2024-06-30 | 530 | Delay due to pending approvals from State (CDFW's Notice of Determination) and Federal (BLM Notice to Proceed) agencies.

## SDGaE
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service July 2022 TDF | Expected In-Service October 2022 TDF | Expected In-Service January TDF 2023 | Expected In-Service Date April TDF 2023 | Expected In-Service July 2023 TDF | Current Estimated In-Service Oct 2023 TDF | Notes
SDGE-EXISTING-RNU-01 | Imperial Valley Existing/Modified RAS' | Imperial Valley Existing/Modified RAS' | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-7.1 | Existing Miguel BK 80 / 81 | Existing Miguel BK 80 / 81 | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-02 | Existing Otay Mesa RASs | Existing Otay Mesa RASs | SDGE |  | PNU |  | Operational
SDGE-EXISTING-RNU-04 | Existing ECO/BUE anti-islanding scheme for radial generators | Existing ECO/BUE anti-islanding scheme for radial generators | SDGE |  | PNU |  | Operational
SDGE-C11-PHII-RNU-02 | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | Participate in the proposed RAS to protect TL13810A/TL13810B/TL13810C Friars - Penasquitos - Doublett Tap 138kV Lines (formerly known as Participate in the proposed RAS to protect TL13827 Mission – Friars 138kV line) | SDGE | C11 Phase II | PNU | Reliability | Operational |  | N/A | N/A | 2022-06-01 | 2022-06-01 | 2022-06-01 | 2022-06-18 | 2022-07-18 | 2022-06-18 | 2022-07-18 | 2022-06-18 |  | Placed in service on 6/18/22
SDGE-C08-PHII-RNU-03.1 | TL680 OLS | Overload Scheme to protect TL680C. Previously named as Modify TL684 RAS. | SDGE | C8 Phase II | GRNU | Deliverability | Operational |  | N/A | 2023-06-23 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-04-01 | In-Service |  | Placed in service on 3/30/23
SDGE-C07-PHI-RNU-01 | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | Participate in the proposed RAS to protect TL23006/TL23010/TL23002 San Luis Rey – San Onofre 230kV lines | SDGE | C7 Phase I | PNU | Reliability | Operational |  | N/A | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 |  | 2023-06-01 | 2023-06-23 | 2023-08-23 | 2023-08-20 | Placed in service 8/20/23
SDGE-C08-PHII-RNU-04 | Participate in the proposed RAS to protect TL23003 & TL23011 Encina to San Luis Rey 230 kV lines (Proposed grouping RAS to protect Encina/Pen/San Luis Rey 230kV Lines) | Proposed RAS to Protect TL23003 Encina - San Luis Rey 230 kV line | SDGE | C8 Phase II | PNU | [6 empty] | 2023-06-01 | 2023-06-01 | 2023-06-01
SDGE-PRE-AMEND-RNU-01.2 | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | Proposed RAS to Protect TL23011B Encina Tap - Encina 230 kV line | SDGE |  | CANU-GR | [6 empty] | 2023-06-01 | 2023-06-01 | 2023-06-01

## GLW-VEA
ID | Network Upgrades | Description | PTO | Study | Type of Upgrade | Category | Status | Current Expected Const Consturction Start | Expected CPUC Permit Application | Trigger Year | Original Estimated In-service Date | Expected In-Service Jan 2022 TDF | Expected In-Service Apr 2022 TDF | Expected In-Service July 2022 TDF | Expected In-Service Oct 2022 TDF | Expected In-Service Jan 2023 TDF | Expected In-Service April 2023 TDF | Expected In-Service July 2023 TDF | Expected In-Service Oct 2023 TDF | Agregate MW in Queue with Executed LGIA | Notes
VEA-C6P2-EOP-R5 | VEA Vista RAS | VEA Vista RAS: Install a new RAS to protect Jackass Flats - Mercury Switch 138 kV line under contingency conditions | VEA | C6 Phase II | RNU | Thermal | Cancelled | N/A | N/A | N/A | N/A | 2022-09-30 | 2022-11-22 | [7 empty] | Project was replaced by upgrading the Jackass Flats - Mercury Switch 138kV line. This project is completed.
VEA-C8P2-VEA-R2 | Innovation RAS | Install a new Innovation RAS | GLW | C8 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 |  | 1547 | Project completed.
VEA-C9P2-EOP-R3 | Innovation RAS (VEA-GLW portion) | New Innovation RAS (include Desert View RAS from QC8) to trip generation under N-1 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 |  | 1547 | Project completed.
VEA-C9P2-EOP-R4 | Sloan Canyon RAS (fka Bob RAS - VEA-GLW portion) | New Sloan Canyon RAS to trip generation under N-1 and N-2 | GLW | C9 Phase II | RNU |  |  |  |  | N/A | 2022-09-30 | 2022-09-30 | 2022-11-22 | 2022-11-22 | 2022-11-22 | 2023-07-01 | 2023-07-01 | 2023-05-23 |  | 1547 | Project completed.
GLW-2021-EOP-L1 | Trout Canyon - Sloan Canyon 230kV line upgrade | Trout Canyon - Sloan Canyon 230kV line upgrade | GLW | 2021 Reassessment | LDNU |  |  |  |  | N/A | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | 2025-12-31 | N/A | 2027-12-31 | N/A | The Trout Canyon – Sloan Canyon 230kV Line Upgrade is part of the GLW Upgrade Project which was approved through the 2021-2022 TPP and revised in the 2022-2023 TPP.