## Data Specification
|  |  | RC Operating Procedure Attachment | Procedure No. | RC0120B
|  |  |  | Version No. | 4.6
|  |  |  | Effective Date | 2025-07-01
RC West IRO-010 Data Specification for Adjacent RCs |  |  |  |  | Distribution Restriction: None
Section | Category | RC West Request Number | Responsible Party | Data Item | Data Transfer Method | Data Update Frequency | Effective Date | Data Validation Method | Related NERC Standards (including but not limited to) | CAISO Guidance Document | Last Revision Date
1 | Real-time Network Measurement Data | RC - 1.1 | Adjacent Reliability Coordinator | Real-time status points for all BES equipment and other non-BES equipment that impact the BES | ICCP | By exception | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.2 | Adjacent Reliability Coordinator | Real-time MW measurements, or ampere if MW not available, for all BES equipment and other non-BES equipment that impact the BES | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.3 | Adjacent Reliability Coordinator | Real-time Mvar measurements for all BES equipment and other non-BES equipment that impact the BES | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.4 | Adjacent Reliability Coordinator | Voltage measurements for all busses associated with BES equipment and other busses associated with non-BES equipment that impact the BES | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.5 | Adjacent Reliability Coordinator | Designated WECC Transfer Path data 1) Actual MW 2) Scheduled MW, Total Transfer Capability (TTC) | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.6 | Adjacent Reliability Coordinator | LTC tap position measurements for LTCs with high side voltage > 100 kV | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.7 | Adjacent Reliability Coordinator | Phase shifter phase tap position | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.8 | Adjacent Reliability Coordinator | MW/Mvar measurements for measured loads. These loads may be equivalent representations of your distribution system. | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.9 | Adjacent Reliability Coordinator | RAS Arming Status for all schemes that have an impact to the BES. An armed RAS implies that it is 1) In service and 2) Ready to perform an action (trip a unit for example) if a specific condition occurs on the power system. | ICCP (preferred, if available) | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.10 | Adjacent Reliability Coordinator | RAS in-service status for all schemes that have an impact to the BES | ICCP (preferred, if available), GMS, or phone notification to the Reliability Coordinator System Operator upon status change | ICCP – 10 sec / Phone Notification – As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.11 | Adjacent Reliability Coordinator | RAS associated analog arming values (e.g. Amp, MW, Mvar). | ICCP (preferred, if available) | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.12 | Adjacent Reliability Coordinator | Status of Non-RAS devices that perform automatic post-contingency actions based on certain parameters such as under voltage or overloaded facilities. This may include, but is not limited to, certain generator run-back schemes, under-voltage facility tripping schemes and current Protection System status when functionality is affected . This is not a request for under-voltage or under-frequency load shedding information. | ICCP (preferred, if available), GMS, or phone notification to the Reliability Coordinator System Operator upon status change | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.13 | Adjacent Reliability Coordinator | Dynamic line and transformer ratings that vary with real-time system or ambient conditions, as applicable to FERC 881 | ICCP or alternate secure site as agreed to amongst RCs | At least hourly or on demand as ratings changes | 7/1/2025 | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.14 | Adjacent Reliability Coordinator | Any TOP-provided stability limitation that the RC, in collaboration with the TOP, determines to require submission in Real-time. | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.15 | Adjacent Reliability Coordinator | IROL - limit calculation, monitored value and margin calculation (if available) | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
1 | Real-time Network Measurement Data | RC - 1.16 | Adjacent Reliability Coordinator | Real-time status points for RC identified PMU installations on the WISP network consisting of measurement and communication equipment, if applicable | PMU | 30 samples per second | 2020-06-26 | Not applicable | IRO-002-7 D.A.7.2. |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.1 | Adjacent Reliability Coordinator | Instantaneous BA Area Load | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.2 | Adjacent Reliability Coordinator | BA Net Actual Interchange (as used in ACE calculation) | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.3 | Adjacent Reliability Coordinator | BA Net Scheduled Interchange (as used in ACE calculation) | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.4 | Adjacent Reliability Coordinator | BA Instantaneous ACE that is used for NERC reporting requirements | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.5 | Adjacent Reliability Coordinator | BAAL high and low limits instantaneous | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.6 | Adjacent Reliability Coordinator | System frequency at multiple locations within the BA as requested by the RC | PMU (preferred, if available) or ICCP | PMU - 30 samples per second or if via ICCP - 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.7 | Adjacent Reliability Coordinator | BA Scheduled frequency | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.8 | Adjacent Reliability Coordinator | BA Area (BAA) Contingency Reserve obligation (as defined in the NERC Glossary and WECC Regional Standards) or, if the BAA is part of a Reserve Sharing Group (RSG), the BAA's allocated obligation as defined by the RSG. 1) Total Required, 2) Total Actual Available, 3) Spinning Required, 4) Spinning Actual Available | ICCP |  | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.9 | Adjacent Reliability Coordinator | BA Area Actual Generation Total | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.10 | Adjacent Reliability Coordinator | Actual Most Severe Single Contingency (MSSC) of your Balancing Authority. This value should not be a static PMax of the largest generator, rather the actual MW output. This is NOT a request for the RSG MSSC. | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.11 | Adjacent Reliability Coordinator | Real-time status points (UCON status point designating unit is or is not connected to the network) for BES connected and BES impacting units 10 MW or greater, or those units with automatic voltage control or black start capability | ICCP | By exception | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.12 | Adjacent Reliability Coordinator | All BES connected and BES impacting generators with SCADA, 10 MW or greater - real-time net MW output | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.13 | Adjacent Reliability Coordinator | All BES connected and BES impacting generators with SCADA, 10 MW or greater - real-time net Mvar output | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.14 | Adjacent Reliability Coordinator | Dynamic Schedule real-time dynamic signal used in ACE calculation for each dynamic schedule. This is not the anticipated energy on the tag, rather a real-time calculation of MWs associated with the dynamic schedule. | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.15 | Adjacent Reliability Coordinator | Pseudo tie real-time dynamic signal. This is a real-time calculation of MWs associated with each pseudo tie used in ACE calculation. Note: This is not an alternate method for inclusion in congestion management procedures pursuant to INT-004-3.1. | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.16 | Adjacent Reliability Coordinator | Balancing Authority total wind MW output. This is a single value - summation of all wind generation currently online. This value should represent wind generation at the BES level. | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.17 | Adjacent Reliability Coordinator | Balancing Authority total solar MW output. This is a single value - summation of all solar generation currently online. This value should represent solar generation at the BES level. | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.18 | Adjacent Reliability Coordinator | ATEC component of ACE | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.19 | Adjacent Reliability Coordinator | BA frequency bias if a dynamic bias is used | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.20 | Adjacent Reliability Coordinator | Meter error component of ACE | ICCP | 10 sec | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.22 | Adjacent Reliability Coordinator | Balancing Authority total storage MW output. This is a single value - summation of all storage production and consumption online. This value should represent storage at the BES level. | ICCP | 10 sec | 2021-01-01 | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.23 | Adjacent Reliability Coordinator | Balancing Authority total storage State of Charge. This is a single value - summation of the current MWh available within all storage. This value should represent storage at the BES level. | ICCP | 10 sec | 2021-01-01 | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.24 | Adjacent Reliability Coordinator | Balancing Authority gross storage charging MW. This is a single value - summation of all storage consumption online. This value should represent storage at the BES level. | ICCP | 10 sec | 2024-01-01 | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.25 | Adjacent Reliability Coordinator | All BES connected and BES impacting storage generators with SCADA - real-time State of Charge | ICCP | 10 sec | 2024-08-01 | Not applicable |  |  | 2025-07-01
2 | Real-time Balancing Authority Data | RC - 2.26 | Adjacent Reliability Coordinator | All BES connected and BES impacting hybrid (more than one resource type) generators with SCADA - real-time MW and State of Charge for each component of the hybrid resource, if applicable | ICCP | 10 sec | 2024-08-01 | Not applicable |  |  | 2025-07-01
3 | Forecast Data | RC - 3.3 | Adjacent Reliability Coordinator | Hourly BAA load forecast. Required each day for the current day through the next four calendar days, not to exceed 7 days. | ALFS | Daily submission by 9:45 AM Pacific Prevailing Time | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | CMRI > Load Forecast |  | Technical Specifications for ALFS, Technical Specifications for EIDE | 2025-07-01
3 | Forecast Data | RC - 3.4 | Adjacent Reliability Coordinator | Hourly BAA load forecast. Required each hour for the next 4 hours. | ALFS | 10 minutes prior to each hour | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | CMRI > Load Forecast |  | Technical Specifications for ALFS, Technical Specifications for EIDE | 2025-07-01
3 | Forecast Data | RC - 3.5 | Adjacent Reliability Coordinator | Hourly Resource Dispatch for all BAA generation that qualifies per the BES definition and any non-BES generation (As determined the RC) that are necessary to support the accuracy of Operational Planning Analyses and to determine SOL exceedance on BES Facilities. Required each day for the current day through the next four calendar days, not to exceed 7 days. | RC-BSAP/ BSAP | Daily submission by 10 AM Pacific Prevailing Time | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | CMRI > Forecasted Generation |  | Technical Specifications for RC-BSAP, Technical Specifications for EIDE | 2025-07-01
3 | Forecast Data | RC - 3.6 | Adjacent Reliability Coordinator | Hourly Resource Dispatch MW for all BAA generation that qualifies per the BES definition and any non-BES generation (as determined by the BA and RC) that is necessary to support the accuracy of Operational Planning Analyses and to determine SOL exceedance on BES Facilities. Required each hour for the next four hours. | RC-BSAP/ BSAP | 10 minutes prior to each hour | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | CMRI > Forecasted Generation |  | Technical Specifications for RC-BSAP, Technical Specifications for EIDE | 2025-07-01
4 | Documentation and Procedures | RC - 4.1 | Adjacent Reliability Coordinator | Emergency Operations Plans | Secure site as agreed to amongst RCs or email to procedurecontrol@caiso.com | Anytime the plan is updated | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Neighboring RC Operating Procedures library |  |  | 2025-07-01
4 | Documentation and Procedures | RC - 4.2 | Adjacent Reliability Coordinator | Restoration Plans | Secure site as agreed to amongst RCs or email to procedurecontrol@caiso.com | Annually and/or anytime the plan is updated | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Neighboring RC Operating Procedures library |  |  | 2025-07-01
4 | Documentation and Procedures | RC - 4.3 | Adjacent Reliability Coordinator | Under voltage and under frequency load shed Plans | Secure site as agreed to amongst RCs or email to procedurecontrol@caiso.com | Anytime the plan is updated | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Neighboring RC Operating Procedures library |  |  | 2025-07-01
4 | Documentation and Procedures | RC - 4.4 | Adjacent Reliability Coordinator | Path procedures (for WECC Paths that impact SOL/IROL, neighboring RCs) | Secure site as agreed to amongst RCs or email to procedurecontrol@caiso.com | Anytime the plan is updated | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Neighboring RC Operating Procedures library |  |  | 2025-07-01
4 | Documentation and Procedures | RC - 4.5 | Adjacent Reliability Coordinator | Geomagnetic Disturbance Operating Procedures | Secure site as agreed to amongst RCs or email to procedurecontrol@caiso.com | Anytime the plan is updated | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Neighboring RC Operating Procedures library |  |  | 2025-07-01
4 | Documentation and Procedures | RC - 4.6 | Adjacent Reliability Coordinator | Area specific Operating Plans, Procedures or Processes for mitigating SOLs, IROLs or other stability limitations | Secure site as agreed to amongst RCs or email to procedurecontrol@caiso.com | Anytime the plan is updated | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Neighboring RC Operating Procedures library |  |  | 2025-07-01
4 | Documentation and Procedures | RC - 4.8 | Adjacent Reliability Coordinator | System voltage limits and stability limitations | Secure site as agreed to amongst RCs or email to procedurecontrol@caiso.com | Anytime the plan is updated | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Neighboring RC Operating Procedures library | FAC-014-3 R1, R4 | Templates available on RC Portal > SOL Methodology library | 2025-07-01
4 | Documentation and Procedures | RC - 4.9 | Adjacent Reliability Coordinator | Other Plans, Procedures, Protocols or Process documents as requested by the RC, including fire/weather mitigation and/or regulatory limitations that could cause inability to follow Operating Instructions. | Secure site as agreed to amongst RCs or email to procedurecontrol@caiso.com | Anytime the plan is updated | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Neighboring RC Operating Procedures library |  |  | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.1 | Adjacent Reliability Coordinator | For Outages identified prior to Real-time/ Same-day study window - forced generation and transmission outages, 30 minutes or more in duration, on Facilities/equipment identified in the In-Scope Outage Categories section of the CAISO Outage Coordination Process | webOMS API | As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | GMS confirmation of Nightly Outage Review |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.2 | Adjacent Reliability Coordinator | For Outages identified prior to Real-time/ Same-day study window - any planned individual generating unit, or based on plant configuration, derate of > 50 MW reduction of available capacity (30 minutes or more in duration) shall be submitted per the instructions of the webOMS Manual and per the Short-Range Study Window Process Outage Submission Timeline | webOMS API | In accordance with the Short-Range Submittal Timeline specified in the CAISO Outage Coordination Process | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | GMS confirmation of Nightly Outage Review |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.3 | Adjacent Reliability Coordinator | For Outages identified prior to Real-time/ Same-day study window - any generating unit, or based on plant configuration, derate of > 50 MW reduction of available capacity (other than planned derates, and 30 minutes or more in duration), shall be submitted per the instructions of the webOMS Manual | webOMS API | As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | GMS confirmation of Nightly Outage Review |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.4 | Adjacent Reliability Coordinator | For Outages identified prior to Real-time/ Same-day study window - any Forced generating unit, or based on plant configuration, derate of > 50 MW reduction of available capacity (30 minutes or more in duration) | webOMS API | As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | GMS confirmation of Nightly Outage Review |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.5 | Adjacent Reliability Coordinator | For Outages identified prior to Real-time/ Same-day study window - planned Automatic Voltage Regulator (AVR) or Power System Stabilizer (PSS) outage (30 minutes or more in duration) on an identified BES facility | webOMS API | In accordance with the Short-Range Submittal Timeline specified in the CAISO Outage Coordination Process | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | GMS confirmation of Nightly Outage Review |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.6 | Adjacent Reliability Coordinator | For Outages identified prior to Real-time/ Same-day study window - Automatic Voltage Regulator (AVR) or Power System Stabilizer (PSS) outage (other than planned outages, and 30 minutes or more in duration) on an identified BES facility | webOMS API | As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | GMS confirmation of Nightly Outage Review |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.7 | Adjacent Reliability Coordinator | For Outages identified prior to Real-time/ Same-day study window - Total Transfer Capability (TTC) values for WECC Paths that impact SOL, IROLs, neighboring RCs adjusted to account for planned outages and operating conditions. See path listing in RC0120 - Guidelines for IRO-010 RC Data Specification and Collection. | webOMS | Timing in alignment with RCs outage coordination | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.8 | Adjacent Reliability Coordinator | For Outages identified prior to Real-time/ Same-day study window - Total Transfer Capability (TTC) values for WECC Paths that impact SOL, IROLs, neighboring RCs adjusted to account for unplanned outages or operating conditions. See path listing in RC0120 - Guidelines for IRO-010 RC Data Specification and Collection. | webOMS | As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.9 | Adjacent Reliability Coordinator | Notification to RC Operators of Total Transfer Capability (TTC) adjustments for WECC Paths identified due to a Forced outage or change in operating conditions. See path listing in RC0120 - Guidelines for IRO-010 RC Data Specification and Collection. | GMS or other agreed to format | As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.10 | Adjacent Reliability Coordinator | For Outages identified prior to Real-time/ Same-day study window - planned outages of telemetering and control equipment of 30 minutes or more in duration, with potential impacts to SE results, SOLs, IROLs, RAS visibility, or could lead to loss of visibility for an area, or communication channels impacting system protection that may result in EMS alarms | webOMS API | As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | GMS confirmation of Nightly Outage Review |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.11 | Adjacent Reliability Coordinator | For Outages identified prior to Real-time/ Same-day study window - unplanned telemetering and control equipment outages of 30 minutes or more in duration, with potential impacts to SE results, SOLs, IROLs, RAS visibility, or could lead to loss of visibility for an area, or communication channels impacting system protection that may result in EMS alarms | webOMS (via user interface or API); include Grid Messaging System (GMS) if impacts adjacent entities | As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | GMS confirmation of Nightly Outage Review |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.13 | Adjacent Reliability Coordinator | Operational Planning Analysis and Operating Plan(s) for next-day operations | Secure site as agreed to amongst RCs | When Operational Planning Analysis is completed or when Operating's Plans have been identified in addition to any updates | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Entity Studies library |  | CAISO Operational Planning Analysis document | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.16 | Adjacent Reliability Coordinator | For Outages identified prior to OPA and Real-time timeframes - any forced and planned Transmission outages on Facilities/equipment identified in the In-Scope Outage Categories section of the CAISO Outage Coordination Process | webOMS API | As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | GMS confirmation of Nightly Outage Review |  | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.17 | Adjacent Reliability Coordinator | For Outages in real-time - any forced or urgent generation unit derate of 50 MW or greater reduction of available capacity, 30 minutes or more in duration | webOMS, even if submitted after the fact (via user interface or API) | As soon as practicable | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable | IRO-017-1 | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
5 | Scheduled and Unscheduled Outage Information | RC - 5.18 | Adjacent Reliability Coordinator | For Outages in real-time - any forced or urgent generation unit connected to BES, 30 minutes or more in duration | webOMS, even if submitted after the fact (via user interface or API) | As soon as practicable; with as much advanced notice as possible. | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable | IRO-017-1 | CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
6 | Power System Modeling Information | RC - 6.1 | Adjacent Reliability Coordinator | Network topology changes (additions, changes, removals) for generation, transmission, and load equipment and facilities plus ICCP SCADA mapping | RIMS or alternate secure site as agreed to amongst RCs; if modeling method may impact SE solution (i.e. double modeling), submit required switch positions via WebOMS until facility is placed into service | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Western Interconnection Model Library > Model File 1) CIM Model File 2) PSSE Model File 3) RC West One Lines and Model Data Zip File |  | RIMS User Guide, Modeling Submission Checklist; CAISO Outage Coordination Process; webOMS Manual, Interface Specification for OMS | 2025-07-01
6 | Power System Modeling Information | RC - 6.8.1 | Adjacent Reliability Coordinator | Generators: connectivity, gross and net MW maximum and reactive capability curves (if no curve available, Mvar minimum and maximum required); List of units normally on AVR- a list shall include voltage set point(s) with High and Low range representing voltage regulation criteria. | RIMS or alternate secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Western Interconnection Model Library > RC West and Neighboring Generator Resources file |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC - 6.10.1 | Adjacent Reliability Coordinator | Seasonal Facility Ratings and overload relay trip settings (including time-delay) on those Facilities (transformers and transmission lines) that are part of Bulk Electric System and their overload trip settings are below 125% of the highest Facility rating. | RIMS or alternate secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library; or if between model builds, then in accordance with CAISO Outage Coordination Process | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Western Interconnection Model Library > Model MVA Ratings used by Area file |  | RIMS User Guide, Modeling Submission Checklist; OMS technical specifications for adjusting normal and emergency operational ratings | 2025-07-01
6 | Power System Modeling Information | RC - 6.10.2 | Adjacent Reliability Coordinator | Dynamic Facility Ratings on those Facilities (transformers and transmission lines) that are part of Bulk Electric System, as applicable to FERC 881 | FERC 881 Dynamic MVA ICCP Template uploaded to RIMS or alternate secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2025-07-01 | RC Portal > Western Interconnection Model Library > FERC881_Dynamic_MVA_ICCP file |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC - 6.11 | Adjacent Reliability Coordinator | List of all transmission and generation ICCP object ID data available for the entity's area. Also include SCADA definition relating to each object ID. | Secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Real-Time ICCP Points library |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC - 6.12 | Adjacent Reliability Coordinator | Dated BES system one-line diagrams on request and RC requested Non-BES system one-line diagrams | Secure site as agreed to amongst RCs or email to SystemOperatingDia@caiso.com | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > TOP-003 Reference library |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC - 6.13 | Adjacent Reliability Coordinator | Longitude and latitude for each substation with voltage levels > 100 kV or with total plant generation >= 50 MW | RIMS or alternate secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Western Interconnection Model Library > Substation Coordinates file |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC - 6.14 | Adjacent Reliability Coordinator | Line routing for all lines 100 kV and above | RIMS or alternate secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Western Interconnection Model Library > Transmission Line Shapefiles file |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC - 6.15 | Adjacent Reliability Coordinator | List of shunt devices normally on AVR. These shunts are those that can automatically connect/disconnect at a specified voltage set point without operator intervention. The list shall include the voltage set point(s) and any time delays prior to automatic switching. | RIMS or alternate secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC - 6.16 | Adjacent Reliability Coordinator | List of all pseudo ties and jointly owned units operated by the BA. List of all dynamic schedules operated by the BA as requested by the RC. | RIMS or alternate secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Western Interconnection Model Library > Model File 1) CIM Model File 2) PSSE Model File 3) RC West One Lines and Model Data Zip File |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC - 6.17 | Adjacent Reliability Coordinator | List of all normally open circuit breakers, disconnects and switches that control the connectivity of transmission branch elements and Facilities; list shall include unique status for all applicable seasons. The list is applicable to BES Facilities/elements and non-BES Facilities/elements that impact the BES (see Note 1), and non-BES Facilities/elements specifically requested by the RC. Examples of applicable switching devices include those associated with: * Transmission lines * Transformers * Series Compensation * Station bus switches including auxiliary buses and bus tie switches Examples of non-applicable devices include: Shunt devices. | RIMS or alternate secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Western Interconnection Model Library > Model File 1) CIM Model File 2) PSSE Model File 3) RC West One Lines and Model Data Zip File |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC - 6.18 | Adjacent Reliability Coordinator | RAS scheme information for all schemes or at the discretion of RC West. This requires logic diagrams and documentation on the function of each RAS. | Secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > RAS Database |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC - 6.19 | Adjacent Reliability Coordinator | Description and modeling information for all non-RAS automatic post-contingency actions based on certain parameters such as under voltage or overloaded facilities. This may include, but is not limited to, certain generator run-back schemes or under voltage facility tripping schemes. | Secure site as agreed to amongst RCs | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | RC Portal > Neighboring RC Operating Procedures library |  | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC- 6.24 | Adjacent Reliability Coordinator | Contingency definition additions, modifications, and deletions identified from RC West IRO-002 study report | via RIMS or email | Annual | 2020-06-26 | RC Portal > Western Interconnection Model library > Active Contingency Definitions file and TCOR file | IRO-002-7 | RIMS User Guide, Modeling Submission Checklist | 2025-07-01
6 | Power System Modeling Information | RC- 6.25 | Adjacent Reliability Coordinator | Dynamic Model for Transient Security Assessment (TSA) in GE PSLF format, along with the corresponding power flow model(s), definitions files (contingency, interface, transfer, monitor files), and other user defined dynamics models for RAS schemes, protection relays, etc., which are being used in RC’s real-time TSA applications. Additionally, include units’ dynamic model data mapping between WECC planning case and EMS operations case. | Upload to RIMS | In accordance with Full Network Model Schedule posted RC Portal > Western Interconnection Model library | 2020-09-11 | RC Portal > Western Interconnection Model library > Dynamic Data dyd file | MOD-032-1 MOD-033-2 |  | 2025-07-01
7 | Other Operational Information | RC - 7.6 | Adjacent Reliability Coordinator | See RC0330 Coordination with Neighboring RCs procedure for full list of requirements. This procedure addresses real-time events which require notification to the CAISO RC operator by phone, the Grid Messaging System (GMS) and/or Reliability Coordinator Information System (RCIS). | GMS, RCIS, phone | See RC0330 | 11/1 exchange with AESO, BCHA, 12/3 exchange with SPP | Not applicable |  |  | 2025-07-01

## Exceptions
|  | RC Operating Procedure Attachment | Procedure No. | RC0120B
|  |  | Version No. | 4.6
|  |  | Effective Date | 2025-07-01
RC West IRO-010 Data Specification for Adjacent RCs |  |  | Distribution Restriction: None
Operationally Affected Parties
Shared with the Public and Adjacent RCs.
Category | Request Number | Entity | Exclusion and Agreement Rationale
All | All | SPP | GRID provides BA services and information on behalf of HGMA.
Real-time Network Measurement Data | All | SPP | TEPC, EPE, and WALC will provide directly to CAISO.
Real-time Balancing Authority Data | All | SPP | TEPC, EPE, and WALC will provide directly to CAISO.
Real-time Balancing Authority Data | RC - 2.19 | SPP | If collected within SPP footprint, SPP will send to RC West but at this time, there are no instances of this.
Real-time Balancing Authority Data | RC-2.22, RC-2.23 | BCRC | No resources of this group.
Real-time Balancing Authority Data | RC-2.23 | AESO | Discussed through RC-RC subgroup, not able to provide at this time.
Forecast Data | RC-3.4, RC-3.6 | AESO | Data does not change from day ahead submissions.
Forecast Data | RC-3.4, RC-3.5, RC-3.6 | SPP | TEPC, EPE, and WALC will provide directly to CAISO.
Scheduled and Unscheduled Outage Information | All | SPP | TEPC, EPE, and WALC will provide directly to CAISO.
Scheduled and Unscheduled Outage Information | RC-5.2, RC-5.3, RC-5.4, RC-5.17 | BCRC | Coordinated due to technical limitations, with alternative means of identifying any applicable deratings in the BCRC OPA
Scheduled and Unscheduled Outage Information | RC-5.5, RC-5.6 | SPP | SPP is not including in their data specification.
Power System Modeling Information | RC-6.1, RC-6.8.1, RC-6.10, RC-6.11, RC-6.16, RC-6.17 | SPP | TEPC, EPE, and WALC will provide directly to CAISO.
Power System Modeling Information | RC-6.13, RC-6.14 | SPP | SPP is not including in their data specification. Discussed with Legal, and RC West to request data from individual SPP customers.
Power System Modeling Information | RC-6.25 | SPP | SPP provides updated data to WECC for CAISO to retrieve.

## Version History
| RC Operating Procedure Attachment | Procedure No. | RC0120B
|  | Version No. | 4.6
|  | Effective Date | 2025-07-01
RC West IRO-010 Data Specification for Adjacent RCs |  | Distribution Restriction: None
Operationally Affected Parties: Shared with the Public and Adjacent RCs.
References: NERC Requirements IRO-010-4; IRO-014-3
Version History
Version | Change Description | Effective Date
1 | Created for initial transition period with Peak RC. | 2019-07-01
2 | Added tab for AESO, BCRC and SPP. | 2019-11-01
3 | Section 1 - Clarified request RC-1.16. Section 4 – Replaced RC-6.21 with RC-4.8 and included templates reference. Section 5 - Consolidated RC-5.14 into RC-5.13 and added any updates to be provided; Removed PEAK references. Section 6 - Consolidated RC-6.2-6.7 and RC-6.9 into RC-6.1. Updated the CAISO guidance document for RC-6.1, RC-6.8.1, RC-6.10-6.19, RC-6.22. Clarified RC-6.12 to system one-line diagrams and on request basis. Removed state and city from RC-6.13. Updated data update frequency for RC-6.18 and RC-6.19. Combined RC-6.20 into RC-6.10. Added request RC-6.24 and RC-6.25. Errata Change: Annual Review. | 2020-06-26
3.1 | Updated effective date of request RC-1.16 to 6/26/2020 on line 22 of main tab. | 2020-09-24
4 | Annual Review: Section 2 - Added requests 2.22 and 2.23. Replaced instance of CAISO RC with RC West. Section 6 - Updated 6.1 data transfer method and CAISO guidance document to include webOMS for instances such as double modeling. Modified language in request 6.16. Added exceptions to data requests. Updated NERC Standard referenced in Data Specification tab. Changes coordinated with RC-RC IRO-010 coordination sub team. | 2021-04-01
4.1 | Section 2 - added data format and frequency for RC-2.10. Added exceptions to data requests in coordination with SPP RC. Changes coordinated with the RC-RC IRO-010 coordination sub team. Minor format and grammar updates. | 2022-02-10
4.2 | Annual Review: Added exceptions to data requests in coordination with TEPC. Clarified language in data request 6.24. | 2022-05-03
4.3 | Annual Review: Added RC-5.17 and RC-5.18 for items communicated in real-time via webOMS that were previously listed in RC0130. Added exceptions to data requests in coordination with EPE and WALC. | 2023-04-05
4.4 | Updated data requests RC-1.13, RC-6.10.1, and RC-6.10.2 in preparation of FERC Order 881 on dynamic ratings. Added request RC-2.24 based on feedback regarding battery storage ICCP data. 10/17/23 - Errata Change: Updated data requests RC-1.13 and RC-6.10.2 to mention " as applicable to FERC 881". | 2023-10-12
4.5 | Annual Review: Updated data requests 1.13 and exceptions based on discussions with SPP. Added data requests RC-2.25 and RC-2.26. Updated NERC Standards references. | 2024-04-01
4.6 | Added columns for Data Validation Method and Last Revision Date in main Data Specifications tab. Added References section in Version History tab to include NERC Requirements. | 2025-07-01