| Readiness Criterion Identifier | Readiness Category | Criteria | Measurable Elements | Threshold | Owner | Status | Evidence | Tariff Mapping |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Prospective WEIM Entity Full Network Model Integration | Generation, Interchange and Load comparison | Load, WEIM Internal Intertie and WEIM External Interties, and Generating Unit definition in the Full Network Model is consistent with the Load, WEIM Internal Intertie and WEIM External Interties, and Generating Unit definition in the exported prospective WEIM Entity network model file that it delivered to the CAISO. | Data matches within 10%, measured in MW capacity to start parallel operation, and within 5% before full activation. Any Discrepancies are accounted for in terms of imbalance adjustment | CAISO | Complete | CAISO team provided evidence which was validated and approved for both Market SIM and Parallel Ops | Tariff section 29.2(b)(7)(A)(i) |
| 2 | Prospective WEIM Entity Full Network Model Integration | Comparison of SCADA measurement | SCADA measurements used in prospective WEIM Entity EMS model match the measurements observed by the CAISO through the CAISO EMS model | Critical and used SCADA measurements match 90% to start parallel operation and 95% before full activation, measured in MW, outside of any exception in EMS model | CAISO | Complete | CAISO team provided evidence which was validated and approved for both Market SIM and Parallel Ops | Tariff section 29.2(b)(7)(A)(ii) |
| 3 | Prospective WEIM Entity Full Network Model Integration | State Estimator solution | CAISO state estimator solution is equivalent or superior to the prospective WEIM Entity state estimator solution for its Balancing Authority Area. | State Estimator solutions converge >90% of the time in two days before parallel operation and three days before full activation. Solution differences within 10% before parallel operation and 5% before full activation measured in MW or justified due to different external BAA modeling | CAISO | Complete | CAISO team provided evidence which was validated and approved for both Market SIM and Parallel Ops | Tariff section 29.2(b)(7)(A)(iii) |
| 4 | Prospective WEIM Entity Full Network Model Integration | Non-Conforming Load, Behind-the-Meter Generation, Pseudo Ties, and Dynamic Schedules | Physical representation of the prospective WEIM Entity’s network matches the Base Market Model that accounts for non-conforming load, behind-the-meter generation, pseudo-ties, and dynamic schedules, and third party transmission service provider and path operator information that supports WEIM Transfers and Real-Time Dispatch in the Energy Imbalance Market, as applicable | Prospective WEIM Entity major non-conforming loads > 5% of prospective WEIM Entity total actual load in MW are modeled separately from conforming load in market model | CAISO | Complete | CAISO team provided evidence which was validated and approved for both Market SIM and Parallel Ops | Tariff section 29.2(b)(7)(A)(iv) |
| 5 | Agreements | Execution of Necessary Agreements | The prospective WEIM Entity has executed all necessary agreements. | The prospective WEIM Entity will execute all agreements, as outlined in Section 5 of the WEIM BPM within the required timelines outlined in Section 5. | JOINT | Complete | Power Watch provided copies of all executed agreements. CAISO affirmed that all planned agreement tasks are complete. | Tariff section 29.2(b)(7)(K)(i) |
| 6 | Operations Training | Completion of mandatory training courses | Prospective WEIM Entity operators who will have responsibility for WEIM operations, transactions and settlements, will complete CAISO training modules. | Prospective WEIM Entity operators will Complete training and close-of-training assessment in the appropriate timeframes as outlined in “100 series”– an introduction to Energy Imbalance Market training “200 series”– the specific hourly and daily tasks and duties for normal operation training module; and “300 series”– the assessment of market results and response to contingencies and abnormal situations training module. | Power Watch | Complete | Power Watch provided transcripts of training and email confirmation of completion, CAISO provided evidence which was validated and approved | Tariff section 29.2(b)(7)(B) |
| 7 | Forecasting Capability | Load forecast capability | Definition of WEIM demand forecast boundaries based on the conforming and non-conforming load characteristics, as applicable. - Accuracy of the CAISO forecast of WEIM demand based on historical actual load data for the defined WEIM demand forecast boundaries. - Identification of weather station(s) locations used in forecasting, if applicable. | All Plant Information (PI) tags and historical data for defined load area(s), and non-conforming load, if applicable, compared with load forecasts provided from CAISO (if CAISO load forecast used). | CAISO | Complete | Since PWS load and forecast are zero (Non-load BA), this won’t be applicable for it. STF team provided screen shot evidence and verified this item is complete | Tariff sections 29.2(b)(7)(C)(i)-(iii) |
| 8a | Forecasting Capability | Variable Energy Resource (VER) forecast capability | Identification of the source of VER forecasts. (If a participating wind or solar unit requires a CAISO forecast, then BPM and Tariff requirements apply.) | Forecasting entity must demonstrate delivery of Unit MW forecast at 5 min intervals for at least three hours ahead. Forecasting entity must also provide base schedule by T-75, T-55 and T-40. WWEIM Entity provides to CAISO real-time MW production PI tags. | CAISO | Complete | STF team provided screen shot evidence and verified this item and all load tasks are complete | Tariff section 29.2(b)(7)(C)(iv) |
| 8b | Forecasting Capability | Hybrid Resources forecast capability | Identification of all Hybrid Resources, source of Hybrid Resource forecasts, and confirmation applicable tariff and BPM requirements are met. | Forecasting entity must demonstrate delivery of Unit MW forecast at 5 min intervals for at least three hours ahead. Forecasting entity must also provide base schedule by T-75, T-55 and T-40. For participating hybrid resources WEIM entity submits documents required by Appendix Q: Site information sheet, topo map, shapefile. WEIM entity provides real-time MW production PI tags for all Resources, and metrological measurements for participating hybrid resources required by Appendix Q. | CAISO | Complete | STF team provided screen shot evidence and verified this item and all load tasks are complete | Tariff section 29.2(b)(7)(C)(v) |
| 9 | Forecasting Capability | Flexible capacity requirements | CAISO has established flexible capacity requirements for the prospective WEIM Entity Balancing Authority Area and the combined WEIM Area including the prospective WEIM Entity | The CAISO has received and stored all historical data from the prospective WEIM Entity necessary and sufficient for the CAISO to perform the flexible ramp requirement. | CAISO | Complete | STF team provided screen shot evidence and verified this item and all load tasks are complete | Tariff section 29.2(b)(7)(K)(iv) |
| 10 | Balanced Schedules | Base schedule balancing capability | The prospective WEIM Entity Scheduling Coordinator demonstrates its ability to balance WEIM demand and WEIM supply for the prospective WEIM Entity’s Balancing Authority Area | 90% or greater of base schedules balance tests during monitored hours are within 10% average imbalance of load forecast over one day period before parallel operation, and 5% average over five full days before full activation. The CAISO will provide examples of MW thresholds for each prospective WEIM Entity to indicate a reasonable threshold as it applies to a given WEIM Entity and indicate the potential implications of a swing from 5% over to 5% under forecast in one hour to the next. | Power Watch | Complete | Market SIM: CAISO reviewed the screen shots evidence from PW and confirmed they met the readiness criteria. Parallel Ops: CAISO provided reports showing 90% or greater of base schedules balance tests during monitored hours are within 5% average over five full days before full activation. | Tariff section 29.2(b)(7)(D)(i) |
| 11 | Balanced Schedules | Flexible ramping sufficiency test capability | The prospective WEIM Entity \ Scheduling Coordinator demonstrates its ability to pass the flexible ramping sufficiency test. | Passes 90% of the time or greater over monitored hours of one day before parallel operation and five non-consecutive days before full activation. | Power Watch | Complete | Market SIM: CAISO reviewed the screen shots evidence from PW and confirmed they met the readiness criteria. Parallel Ops: CAISO provided reports showing 90% or greater of Flexible Ramping tests during monitored hours of five non-consecutive days before full activation. | Tariff section 29.2(b)(7)(D)(iii) |
| 12 | Balanced Schedules | Capacity test capability | The prospective WEIM Entity Scheduling Coordinator demonstrates its ability to pass capacity test | Passes 90% of the time or greater over monitored hours of one day before parallel operation and five non-consecutive days before full activation. The CAISO will explain the implications of any potential issues with the reliability of an WEIM Entity to meet its capacity requirements. | CAISO | Complete | Market SIM: CAISO reviewed the screen shots evidence from PW and confirmed they met the readiness criteria. Parallel Ops: PW sent evidence and CAISO provided reports showing 90% or greater of Capacity tests during monitored hours of five non-consecutive days before full activation. | Tariff section 29.2(b)(7)(D)(ii) |
| 13 | Operating Procedures | CAISO operating procedures (relevant to WEIM operations) | The prospective WEIM Entity signs CAISO non-disclosure agreement and receives appropriate CAISO “public” and “restricted” operating procedures | Operating procedures NDA signed by the prospective WEIM Entity. The prospective WEIM Entity receives CAISO operating procedures four months prior to the parallel operations date. | JOINT | Complete | Power Watch confirmed that they have been given access to all publicly available Operations documents available on CAISO website | Tariff section 29.2(b)(7)(K)(i) |
| 14 | Operating Procedures | Prospective WEIM Entity operating procedures | The prospective WEIM Entity operating procedures are defined, updated, and tested for the WEIM Entity Scheduling Coordinator | The prospective WEIM Entity operating procedures are updated tested and implemented prior to parallel operations date. | Power Watch | Complete | Power Watch submitted Operating Procedures and an email confirming the same, CAISO accepted as well | Tariff section 29.2(b)(7)(K)(ii) |
| 15 | System Readiness & Integration | Functional Testing | The prospective WEIM Entity and the CAISO will test the functional and system elements in accordance with functional and system testing documentation posted on the CAISO website | All tasks identified in the functional and system testing documentation are complete and will not have any issues deemed significant. Any exceptions will be explained or have an interim solution that is functionally equivalent. | Power Watch | Complete | CAISO reviewed the evidence provided; based on the attached test results, Power Watch has met readiness criteria. Documents are stored on the CAISO project SharePoint. | Tariff section 29.2(b)(7)(E)(i) |
| 16 | System Readiness & Integration | System Integration | The prospective WEIM Entity and CAISO will test system integration testing in accordance with the system integration testing documentation posted on the CAISO website | All tasks identified in the system integration testing documentation are complete and will not have any issues deemed significant. Any exceptions will be explained or have an interim solution that is functionally equivalent. | Power Watch | Complete | CAISO reviewed the evidence provided; based on the attached test results, Power Watch has met readiness criteria. Documents are stored on the CAISO project SharePoint. | Tariff section 29.2(b)(7)(E)(ii) |
| 17 | System Readiness & Integration | The prospective WEIM Entity system access complete | All prospective WEIM Entity employees who require system access to perform WEIM-related job functions identified and have necessary certificates. | All prospective WEIM Employees performing job functions for WEIM market are identified. All CAISO issued certificates are requested within the appropriate timeframes. All identified employees provided the necessary WEIM system access certificates. | Power Watch | Complete | PW verified by email that all access for Parallel Operations is in place and there is a plan in place to ensure all access for Production. CAISO confirmed all access is in place and there is a plan for ensuring access for production. | Tariff section 29.2(b)(7)(E)(iii) |
| 18 | System Readiness & Integration | ISO - prospective WEIM Entity interfaces | Data interfaces between prospective WEIM Entity’s systems and CAISO systems are tested | ISO and prospective WEIM Entity identify significant data interface issues. WEIM Entity and CAISO executives to approve exceptions. | JOINT | Complete | CAISO reviewed the evidence provided; based on the attached test results, Power Watch has met readiness criteria. Documents are stored on the CAISO project SharePoint. | Tariff section 29.2(b)(7)(E)(i) |
| 19 | Market Simulation | Day in the life simulation | The prospective WEIM Entity operators are able to meet the market timelines | The prospective WEIM Entity grid operations staff complete end-to-end daily market workflow with no critical defects. | JOINT | Complete | CAISO reviewed the evidence provided; based on the attached test results, Power Watch has met readiness criteria. Documents are stored on the CAISO project SharePoint. | Tariff section 29.2(b)(7)(I)(ii) |
| 20 | Market Simulation | Structured scenarios simulation | The prospective WEIM Entity operators execute and pass all structured scenarios provided by CAISO | All significant issues resolved or have an interim solution that is functionally equivalent. | JOINT | Complete | All tests passed, settlements validated by the entity and CAISO. Results reviewed and approved by CAISO. | Tariff section 29.2(b)(7)(I)(iii) |
| 21 | Market Simulation | Unstructured scenarios simulation | The prospective WEIM Entity operators execute and pass all unstructured scenarios provided by prospective WEIM Entity | All significant issues resolved or have an interim solution that is functionally equivalent. | JOINT | Complete | Not Applicable, no Unstructured scenarios needed | Tariff section 29.2(b)(7)(I)(iv) |
| 22 | Market Simulation | Market results reports | Market results are appropriate based on inputs | The prospective WEIM Entity and CAISO executive project sponsors approve the market results reports during market simulation | Power Watch | Complete | Market Quality team provided an email confirming they validated this for PW | Tariff section 29.2(b)(7)(I)(v) |
| 23a | Market Simulation | Market quality review | Prices are validated based on input data | Market simulation prices and MWs schedules/dispatches are validated by CAISO market quality team for entry into parallel operations | CAISO | Complete | Market Quality team provided an email confirming they validated this for PW | Tariff section 29.2(b)(7)(I)(vi) |
| 23b | Parallel Operations | Market quality review | Prices are validated based on input data | Parallel operations prices and MWs schedules/dispatches are validated by the CAISO market quality team | CAISO | Complete | ISO Market Quality team provided the analysis report and had the entity review it. | Tariff section 29.2(b)(7)(I)(vi) |
| 24 | Market Simulation | The prospective WEIM Entity Identification | Validation of SCID’s and Resource ID’s | The CAISO has established and the prospective WEIM Entity has tested all necessary SCIDs and Resource IDs established for the prospective WEIM Entity’s Balancing Authority Area | JOINT | Complete | PW provided the Schedule 1 confirming no changes. ISO provided a list of all SCIDs and Resource IDs confirming they are consistent with Schedule 1, and included the current Roles Matrix with email confirmation. | Tariff section 29.2(b)(7)(I)(i) |
| 25 | Settlements | ISO Settlement Statements and Invoices published to the prospective WEIM Entity and WEIM Participating Resources | The CAISO Settlement statements and invoices match the operational data published to stakeholders or fed into settlement system and the resulting calculations correspond to the formulas defined in ISO’s tariff and BPMs | Monthly settlement statement and invoice with corresponding daily statements produced during market simulation and parallel operations are verifiably accurate against available data. | JOINT | Complete | PW confirmed they have receipt of initial and recalculation statements, CAISO Settlements verified accuracy of statements and invoices. | Tariff section 29.2(b)(7)(F)(i) |
| 26 | Settlements | The prospective WEIM Entity settlement statements and invoices reflect accurate allocations to the prospective WEIM Entity customers prior to financially binding operations. | Verification that settlement statements and invoices accurately reflects system and market data | The prospective WEIM Entity settlement statements and invoices that allocate charges and credits to its customers accurately reflect system and market data during parallel operations. | JOINT | Complete | PW confirmed accuracy of statements and invoices, CAISO Settlements verified accuracy of statements and invoices. | Tariff section 29.2(b)(7)(F)(ii) |
| 27 | Monitoring | Data monitoring | Sufficient and adequate data is available to the CAISO and the Department of Market Monitoring | All required market monitoring data is available during testing and during post go-live for the key metrics (any exceptions will be addressed). CAISO will provide a market report that will provide publicly available information to all market participants. | CAISO | Complete | CAISO Market Quality and DMM each confirm that they are able to see the data in Parallel Ops Stage environment to complete their analysis. | Tariff section 29.2(b)(7)(K)(v) |
| 28 | Parallel Operations Plan | Deployment plan | Parallel operations run consistently and in accordance with the timeframe set forth in the prospective WEIM Entity specific parallel operation plan | Parallel operations runs consistently within normal production CAISO Market disruption tolerances. | CAISO | Complete | CAISO VP confirms Parallel Operations ran consistently within normal tolerances | Tariff section 29.2(b)(7)(J) |
| 29 | Outage Management System | Transmission and generation outage submittal and retrieval | The prospective WEIM Entity will verify its ability to submit and retrieve outage information with the CAISO | The prospective WEIM Entity validate their ability to submit and retrieve transmission out-of-service outages, generation Pmax derates, generation Pmin rerates, and generation out-of-service outage tickets within the required timelines. | JOINT | Complete | Entity provided screen shot evidence which CAISO reviewed and verified | Tariff section 29.2(b)(7)(G) |
| 30 | Communications between the CAISO and the prospective WEIM Entity | Voice and/or electronic messaging | Implemented process and procedures used for voice and/or electronic messaging | The process and procedures are incorporated into the prospective WEIM Entities business processes before the start of market simulation. | Power Watch | Complete | CAISO confirms the test is complete for both phone calls and Everbridge messaging | Tariff section 29.2(b)(7)(H)(i) |
| 31 | Communications between the CAISO and the prospective WEIM Entity | Communication tools | Staff are trained on communication procedures and tools | The prospective WEIM Entity operations staff who will have responsibility for WEIM operations, transactions and settlements are trained on the relevant operating procedures and tools used for WEIM related communications before the start of parallel operations | Power Watch | Complete | CAISO confirms the test is complete for both phone calls and Everbridge messaging | Tariff section 29.2(b)(7)(H)(ii) |
| 32 | Communications between the CAISO and the prospective WEIM Entity | 3rd party transmission service provider | The third party transmission service provider information that supports WEIM Transfers and Real-Time Dispatch included in the Full Network Model is available during parallel operations | The CAISO provides third party transmission service provider and path operator information to the prospective WEIM Entity through parallel operations | Power Watch | Complete | Entity confirmed via email their 3rd party transmission service provider, CAISO sent email confirming the criteria | Tariff section 29.2(b)(7)(H)(iii) |
| 33 | WEIM Available Balancing Capacity | Identification of WEIM Available Balancing Capacity | Participating resources and non-participating resources for WEIM Available Balancing Capacity. | The prospective WEIM Entity has identified WEIM participating resources and non-participating resources that it intends to designate in the WEIM Resource Plan as WEIM Available Balancing Capacity | Power Watch | Complete | PW submitted confirmation of ABC capacity, CAISO has reviewed and verified. | Tariff section 29.2(b)(7)(K)(iii) |