## Cost Details
All costs are $x1,000
2017 Final VEA Generator Interconnection Unit Cost Guide |  |  |  | "Voltages" |  |  | 138 kV | 230 kV | Notes/Comments:
Revised as of: 02/10/2017
Equipment Categories |  |  |  | Units |  |  |  |  | VEA does not currently have 500 kV facilities on their system. 500 kV connections will be estimated on an as-needed basis.
New Substation Equipment
|  | Complete 3-CB ring bus Substation, equipped with one line position to |  |  |  |  | 5910 | 8805 | We are estimating the cost of a three breaker ring bus interconnection substation at 230 kV or 138 kV. The station typically is designed with the capability to be expanded to a multi-bay Breaker and a Half station. Transformer cost is not included.
terminate a single gen-tie with as many as (2) outgoing lines.
New Substation Equipment
|  | Transformer Banks: | [6 empty] | Unit cost of transformer banks
reflects cost of a 100 MVA
rated transformer for the given
|  |  | 230/138 kV | per unit |  |  | 2838 | 2838 | voltage. Includes disconnects and additonal
relaying.
(Add additional options)
|  | Line Positions to terminate gen-ties and Transformer Bank positions | [6 empty] | Position cost estimate includes cost
|  |  | Single Breaker (add third breaker to breaker and a half) | per unit |  |  | 653 | 1087 | of any related disconnect switches
|  |  | Breaker and a half (2CB) | per unit |  |  | 1283 | 2714 | and protection equipment located within
|  |  | Breaker and a half (3CB) | per unit |  |  | 2054 | 3591 | the position
|  |  | Double Breaker (2CB, double bus) | per unit |  |  | 1251 | 2640
|  | Double Operating Bus Sections - 2 new buses, spanning 2 positions |  | per unit |  |  | 1188 | 1322 | Typical configuration includes "pair" of N/S or E/W buses
|  | Double Operating Bus Sections - 2 new buses, spanning 4 positions |  | per unit |  |  | 2282 | 2694 | Typical configuration includes "pair" of N/S or E/W buses
|  | Sectionalizing Breaker |  | per unit
|  | Shunt Capacitors |  | per unit |  |  |  |  | If required these items will be estimated as a lump sum
| Miscellaneous Equipment (see comments) | [7 empty] | If required these items will be estimated as a lump sum.
|  | Bus Tie (1CB) |  | lump sum
|  | Shunt Reactors |  | lump sum
|  | Phase Shifter |  | lump sum
|  | Ground Bank |  | lump sum
|  | Series Capacitors |  | lump sum
|  | Static VAR Compensator (SVC) |  | lump sum
|  | Tertiary Reactors (1 reactor, 1 bay) |  | lump sum
| Gas Insulated Substation (in lieu of open air construction) |  |  | lump sum |  |  |  |  | Not typical, would be estimated as a Lump sum, if GIS required.
Replacement Substation Equipment
|  | Line drops (Tie Downs)- 3 phases |  | lump sum |  |  |  |  | Not typical to the VEA system.
|  | Circuit Breakers (including replacement of foundation) |  | per unit |  |  | 347 | 660
|  | Circuit Breakers (without TRV caps) |  | lump sum |  |  |  |  | Not typical to the VEA system.
|  | Transient recovery voltage capacitors (set of 3, separate from CBs) |  | lump sum
|  | Disconnect switches (incl. steel structures and foundations) |  | per unit |  |  | 137 | 156
|  | Line protection relays (other end of line) |  | per set |  |  | 326 | 326
|  | Wave Trap - 1 phase only |  | lump sum |  |  |  |  | Not typical to the VEA system.
|  | Wave Trap removal |  | lump sum
New Protection Equipment
|  | New SPS |  | lump sum |  |  |  |  | Will be estimated as needed.
|  | SPS Relays |  | lump sum
|  | Additional set of bushing current transformers (3) at existing CBs |  | lump sum
Information Technology (IT) Equipment
IT interface equipment - Control Rooms
|  |  | Communication rack placed in existing B station MEER bldg |  | per set |  |  |  | Will be estimated as needed.
|  |  | Comm. Rack with own environmental enclosure |  | per set
|  |  | Full Comm. package for AA or A stations |  | per set
|  |  | Prefab communications building |  | per unit
|  |  | 48V DC power supply for comm. equipment |  | per set
|  |  | 100' self-supporting comm. tower (3 legs) |  | per unit
|  |  | 120' self-supporting comm. tower (4 legs) |  | per unit
IT interface equipment - miscellaneous equipment
|  |  | Lightwave terminal |  | per unit
|  |  | Microwave terminal and dish antennas |  | per set
|  |  | Dehydrator for microwave antennas |  | per unit
|  |  | Channel bank |  | per unit
|  |  | Digital Access Cross Connect (DACS) |  | per unit
|  |  | Network synchronization equipment (BITS clock) |  | per unit
|  |  | Large router for network access to work bases |  | per unit
|  |  | Small router for equipment monitoring, "data beyond SCADA" |  | per unit
|  |  | T1 cross connect |  | per unit
|  |  | Fiber to Telco connection (high voltage protected) |  | per unit
|  |  | Satellite Terminal for "RTU only" locations |  | per unit
IT interface equipment - T/L
|  |  | Fiber optic cable on existing poles |  | per mile
|  |  | Fiber optic cable on new poles |  | per mile
New HV Transmission Line
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | per mile |  |  | 3125 | 3481 | Assumes no environmental, permitting or ROW acquisition.
|  | Single Circuit, Tubular Steel Pole |  | per mile |  |  | 1922 | 2140
| SubTransmission Line (Overhead Facilities) | [7 empty] | SubTransmission not typical to the VEA system.
SubTransmission Line (Underground Facilities)
Removal of HV Transmission Line (complete tear down)
|  | Double Circuit |  | per mile |  |  | 593 | 659 | Assumes removal of old poles.
|  | Single Circuit |  | per mile |  |  | 408 | 453
Reconductor/Upgrade Transmission Line
|  | Double Circuit, Strung on both sides, Tubular Steel Pole |  | per mile |  |  | 2397 | 2664 | Assumes removal of existing conductor and installation of new.
|  | Single Circuit, Tubular Steel Pole |  | per mile |  |  | 1426 | 1584
Metering
|  | Upgrade of existing RTUs |  | lump sum
Lump Sum costs below are in addition to per-unit or lump-sum costs listed above:
| Engineering costs |  |  | lump sum |  |  |  |  | Will be estimated as needed.
| Capitalized Licensing and Permitting Costs, including |  |  | lump sum
mitigation measures, FAA permits, etc.
Civil work: Site Preparation including site grading, ground grid,
| and walls/fencing/containment |  |  | lump sum
| General Facilities: station light & power, backup generator, |  |  | lump sum
station utilities (water, gas, etc. if manned substation)
| Substation Control (MEER) Buildings |  |  | lump sum
| Incremental cost for transmission line crossings (roads, |  |  | lump sum
streams, rail, highway, other T\L)
| Land cost for substations and T/L ROW |  |  | lump sum
| Incremental cost of soil/geotechnical mitigation measures |  |  | lump sum
| Incremental environmental monitoring and mitigations |  |  | lump sum
| Corporate Overheads (A&G, P&B, and AFUDC) |  |  | lump sum
| Income Tax Component of Contribution (ITCC) |  |  | lump sum

## BulkTrans Factors & Assumptions
Bulk Transmission (138 & 230 kV) Factors for use in developing cost estimates in Phase I Generator Interconnection Studies
As of January 2013
Simplified example on how to apply factors:
[10 empty] | $ millions | Apply Factor | Delta
| Hypothetical baseline cost per mile for Double Circuit 220 kV line (strung one side) using Lattice Towers: | [8 empty] | 2
Known characteristics of proposed transmission line ROW at Phase I study:
|  | Will be constructed in mountainous terrain | [7 empty] | 2 | 2.0 x 2.0 =4 | 2
No population density issues
|  | High wind-prone area (but not icy) | [7 empty] | 1.35 | 2.0 x 1.35 =2.7 | 0.7
|  |  | Total Delta (summation of applied factor) | [8 empty] | 2.7
|  |  | Estimated cost per mile | [8 empty] | 2
|  |  | Estimated cost per mile including applied factors ($ million/ mile) | [8 empty] | 4.7
|  | Factor Types: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | flat |  |  | hilly |  | mountain |  | forest
|  |  | Population density |  | rural |  | desert | suburban |  | urban/metro
|  |  | Weather study (increase in |  | 1/2" ice, or 20# wind |  |  | 1" ice, 6# wind |  | > 2" ice, 6# wind
structural steel amount and foundation volume)
|  | Factor Amounts: |  |  | Low Impact factors: |  |  | Medium Impact factors: |  | High Impact factors:
|  |  | Terrain |  | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  | 2.0X to 3.0X
|  |  | Population density |  |  | 1.00X to 1.10X |  |  | 1.33X |  | 1.67X
|  |  | Weather study |  |  | 1.35X |  |  | 1.45X |  | 1.60X
|  |  | Factor Type | Explanation of Factor issues and Factor multipliers
|  |  | Terrain | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
|  |  | Population density | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
|  |  | Weather study | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure types or an increased number of structures to reduce the span lengths.
Other assumptions underlying unit cost guide:
Assumption

## Escalation Rates & Factors
ESCALATION OVERVIEW :
Current VEA Unit Cost Guide as posted on the CAISO website is in 2017 Constant Dollars.
VEA’s cost estimating is done in 2017 constant dollars and then escalated over the years during which the project will be
constructed, arriving at project costs in 2017 Constant Dollars Escalated to OD Year.
DEFINITIONS :
Project Cost in 2017 Constant Dollars represents the cost of the Project if all costs were paid for in 2017.
Project Cost Escalated to OD Year represents the cost of the Project if all costs were paid for in the OD Year.
Mathematical formula: Constant Dollars Escalated to OD Year | [5 empty] | = Cost in Constant Dollars + Escalation to OD Year
= Cost in Constant Dollars x Escalation Factor
2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
Escalation Rate | 2.11% | 2.26% | 2.31% | 2.32% | 2.33% | 2.38% | 2.41% | 2.32% | 2.38% | 2.08% | 2.26%
Escalation Factors | 1 | 1.0226 | 1.0462 | 1.0705 | 1.0955 | 1.1215 | 1.1485 | 1.1752 | 1.2032 | 1.2282 | 1.256